## 2016.3.14
Residential
Variable | Label | 2016.3.14 | 2015.6.30 | Notes
desired_size | Desired array size | 4 | 10
inv_snl_inverter_name | Inverter name | SMA America: SB3800TL-US-22 (240V) 240V [CEC 2013] | SMA America: SB4000US 240V [CEC 2007] | 3.8 kW inverter listed as a residential option available now
module_name | Module Name | SunPower SPR-X21-335-BLK | SunPower SPR-210-BLK-U | 335 W module is listed as the smaller premier residential option available now
subarray1_nmodx | Number of modules along bottom of row 1 | 6 | 9
user_modules_per_string | Modules per string | 6 | 9
system_capacity | Nameplate capacity | 4.0225 | 3.8745
total_inverter_capacity | Total capacity | 3.8 | 4
total_modules | Number of modules | 12 | 18
annual energy |  | 7842 | 6857
LCOE (nom) |  | 7.83 | 8.23
NPV |  | 4588 | 4586
Commercial
Variable | Label | 2016.3.14 | 2015.6.30
inv_snl_inverter_name | Inverter name | SMA America: STP 60-US-10 (400 VAC) 400V [CEC 2015] | SMA America: ST36 (240) 240V [CEC 2010] | 60 kW inverter listed as a current option on SMA website. 480 V option's MPPT range is too restrictive to work with any Sunpower panels >2013, so used 400 V option
module_name | Module Name | SunPower SPR-E19-310-COM | SunPower SPR-210-BLK-U | 310 W commercial module found on "e-series commercial solar panels supplementary technical specifications" on sunpower's website
subarray1_nmodx | Number of modules along bottom of row 1 | 24 | 9
subarray1_nmody | Number of modules along side of row 1 | 1 | 2
subarray1_tilt | Tilt 1 | 30 | 33 | 30 degrees is optimal tilt for annual energy for this system in even 5 deg increments
inverter_num_units | Inverter | 3 | 5
system_capacity | Nameplate capacity | 200.977 | 199.752
total_dc_inverter_capacity | Total capacity | 183.3 | 187.269
total_modules | Number of modules | 648 | 928
modules_per_string | Modules per string | 12 | 8
annual energy |  | 378136 | 358873
LCOE (nom) |  | 6.52 | 6.83
NPV |  | 54935 | 40444
Utility
Variable | Label | 2016.3.14 | 2015.6.30
inv_snl_inverter_name | Inverter name | SMA America: SC750CP-US 342V [CEC 2012] | Advanced Energy: Solaron 333-3159000-1XX 480V [CEC 2009] | listed as a good utility scale option on SMA website. Didn't use any of 3 newest inverters b/c database says they have ABB transformer.
module_name | Module Name | SunPower SPR-E19-310-COM | SunPower SPR-305-WHT-U | same module as commercial system
subarray1_nmodx | Number of modules along bottom of row 1 | 48 | 9
subarray1_tilt | Tilt 1 | 30 | 33 | 30 degrees is optimal tilt for annual energy for this system in even 5 deg increments
inverter_num_units | Inverter | 24 | 55
modules_per_string | Modules per string | 12 | 8
strings_in_parallel | Strings in parallel | 5374 | 8191
total_modules | Number of modules | 64488 | 65528
total_dc_inverter_capacity | Total capacity | 18843.5 | 18849.9
system_capacity | Nameplate capacity | 20000.9 | 20000.8
annual energy |  | 37638720 | 37216204
LCOE (nom) |  | 10.36 | 10.48
NPV |  | 2727511 | 2727506