## Inverter-Full Data
Inverter List (Full Data)
Data has not changed since November 1, 2018
Inverter List Notes
Archive of the "Prior List of Eligible Inverters" Expired March 31, 2005. (Adobe PDF, 6 pages, 120 kilobytes).
* Equipment is in the process of being removed from the list of eligible equipment pursuant to Appendix A, Section B, of the Guidelines for California's Solar Electric Incentive Programs (Senate Bill 1) at:
Guidelines for California's Solar Electric Incentive Programs (Senate Bill 1)
(1) Any text in brackets at the end of the Model Number is not part of the Manufacturer's Model Number. Part of the text in brackets indicates the specified voltage option for that model number, if provided; models with multiple voltage options will have multiple row entries, with one for each eligible option.
(2) The listed Firmware Version is the version that was used during the inverter's UL 1741 Supplement SA testing and was certified on the listed Certificate Date; multiple firmware versions may be listed for a single certificate date if all are required to comply with Supplement SA. Multiple certificate dates with different firmware versions may be listed if new firmware versions were certified under Supplement SA and reported by the manufacturer. Additional firmware versions may be certified but not reported. Check with NRTL for the most current information.
(3) UI: Utility Interactive (non-smart) / SI-1: Smart Inverter Phase 1 (tested to UL 1741 SA8-13) / SI-1R: UL 1741 SA13 tested with reactive power priority (when operating at apparent power capacity, inverter will reduce active power as needed to ensure curve-required reactive power is provided)
Blue colored text indicates that the model number occurs multiple times on the list under different manufacturer names.
Manufacturer Name | Model Number1 | Utility Interactive | Smart Inverter Phase 1 | Smart Inverter Phase 1 with Tested Reactive Power Priority | Description | Maximum Continuous Output Power at Unity Power Factor | Nominal Voltage | Weighted Efficiency | UL 1741 Supplement SA Certification (SA8-SA13)2 |  | UL 1741 SA13 Volt-Var | Built-In Meter | Microinverter | Notes | Night Tare Loss | Power Rating, Continuous, 40 deg C | Night Tare Loss, 40 deg C | Voltage Minimum | Voltage Nominal | Voltage Maximum | Power Level | Power Level | Power Level | Power Level | Power Level | Power Level | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vmin, | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vnom | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Efficiency @Vmax | Sort Order | CEC Listing Date | Last Update
|  | UI3 | SI-13 | SI-1R3 |  | (kW) | (Vac) | (%) | Certificate Date [mo/day/yr] | Firmware Version(s) Tested | SI-1R Listing Date (mo/day/yr) |  |  |  | (W) | (kW) | (W) | (Vdc) | (Vdc) | (Vdc) | 10% (kW) | 20% (kW) | 30% (kW) | 50% (kW) | 75% (kW) | 100% (kW) | 10% Pwr Lvl (%) | 20% Pwr Lvl (%) | 30% Pwr Lvl (%) | 50% Pwr Lvl (%) | 75% Pwr Lvl (%) | 100% Pwr Lvl (%) | Wtd (%) | 10% Pwr Lvl (%) | 20% Pwr Lvl (%) | 30% Pwr Lvl (%) | 50% Pwr Lvl (%) | 75% Pwr Lvl (%) | 100% Pwr Lvl (%) | Wtd (%) | 10% Pwr Lvl (%) | 20% Pwr Lvl (%) | 30% Pwr Lvl (%) | 50% Pwr Lvl (%) | 75% Pwr Lvl (%) | 100% Pwr Lvl (%) | Wtd (%)
ABB | MICRO-0.25-I-OUTD-US-208 [208V] | Y | N | N | 250 W Utility Interactive Microinverter | 0.25 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | Multiple Listing of Power-One | 0.02 |  |  | 30 | 40 | 50 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 91.2 | 94.5 | 95.4 | 96 | 96.2 | 96.2 | 95.8 | 91.5 | 94.4 | 95.5 | 96.2 | 96.3 | 96.4 | 95.9 | 91.2 | 94.3 | 95.3 | 96.2 | 96.2 | 96.4 | 95.8 | ABB0.25MICRO-0.25-I-OUTD-US-208 [208V]
ABB | MICRO-0.25-I-OUTD-US-240 [240V] | Y | N | N | 250 W Utility Interactive Microinverter | 0.25 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | Multiple Listing of Power-One | 0.05 |  |  | 30 | 40 | 50 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 90.8 | 94.2 | 95.4 | 96 | 96.1 | 96.2 | 95.7 | 91.2 | 94.2 | 95.3 | 96.3 | 96.2 | 96.5 | 95.8 | 90.5 | 94 | 95.3 | 96.3 | 96.1 | 96.5 | 95.8 | ABB0.25MICRO-0.25-I-OUTD-US-240 [240V]
ABB | MICRO-0.3HV-I-OUTD-US-208 [208V] | Y | N | N | 300 W Utility Interactive Microinverter | 0.3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | Multiple Listing of Power-One | 0.06 |  |  | 30 | 45 | 60 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.3 | 92.8 | 95.2 | 95.8 | 96.1 | 96 | 95.6 | 95.8 | 92.3 | 95 | 95.8 | 96.2 | 96.3 | 96.3 | 96 | 91.9 | 94.9 | 95.7 | 96.2 | 96.2 | 96.2 | 95.9 | ABB0.3MICRO-0.3HV-I-OUTD-US-208 [208V]
ABB | MICRO-0.3HV-I-OUTD-US-240 [240V] | Y | N | N | 300 W Utility Interactive Microinverter | 0.3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | Multiple Listing of Power-One | 0.06 |  |  | 30 | 45 | 60 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.3 | 92.4 | 95 | 95.7 | 96 | 96 | 95.7 | 95.8 | 91.8 | 94.7 | 95.8 | 96.2 | 96.4 | 96.4 | 96 | 91.7 | 94.6 | 95.6 | 96.1 | 96.2 | 96.4 | 95.8 | ABB0.3MICRO-0.3HV-I-OUTD-US-240 [240V]
ABB | MICRO-0.3-I-OUTD-US-208 [208V] | Y | N | N | 300 W Utility Interactive Microinverter | 0.3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | Multiple Listing of Power-One | 0.02 |  |  | 30 | 40 | 50 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 92 | 95 | 95.8 | 96 | 96.2 | 96 | 95.9 | 92.2 | 94.9 | 95.8 | 96.3 | 96.4 | 96.4 | 96 | 91.7 | 94.8 | 95.6 | 96.2 | 96.3 | 96.4 | 96 | ABB0.3MICRO-0.3-I-OUTD-US-208 [208V]
ABB | MICRO-0.3-I-OUTD-US-240 [240V] | Y | N | N | 300 W Utility Interactive Microinverter | 0.3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | Multiple Listing of Power-One | 0.05 |  |  | 30 | 40 | 50 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 91.7 | 94.8 | 95.8 | 96 | 96.1 | 96 | 95.8 | 92 | 94.8 | 95.7 | 96.3 | 96.4 | 96.4 | 96 | 91.6 | 94.7 | 95.6 | 96.3 | 96.4 | 96.5 | 96 | ABB0.3MICRO-0.3-I-OUTD-US-240 [240V]
ABB | UNO-2.0-I-OUTD-S-US [208V] | Y | N | N | 2 kW, 208 Vac Utility Interactive Inverter. Model number may include -W | 2 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.4 | 2 | 0.4 | 100 | 330 | 416 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.4 | 94.2 | 95.5 | 95.9 | 95.6 | 95 | 95.4 | 88.3 | 94.1 | 95.3 | 96.1 | 96.1 | 96 | 95.6 | 85.6 | 92.5 | 94.3 | 95.6 | 95.8 | 95.8 | 95 | ABB2UNO-2.0-I-OUTD-S-US [208V]
ABB | UNO-2.0-I-OUTD-S-US [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter. Model number may include -W | 2 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.4 | 2 | 0.4 | 100 | 340 | 416 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89.2 | 94.5 | 95.4 | 96 | 96 | 95.5 | 95.5 | 88.3 | 94.1 | 95.5 | 96.4 | 96.5 | 96.5 | 95.9 | 85.5 | 92.8 | 94.6 | 95.9 | 96.2 | 96.3 | 95.4 | ABB2UNO-2.0-I-OUTD-S-US [240V]
ABB | UNO-2.0-I-OUTD-S-US [277V] | Y | N | N | 2 kW, 277 Vac Utility Interactive Inverter. Model number may include -W | 2 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.5 | 2 | 0.5 | 100 | 360 | 416 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.6 | 94.2 | 95.1 | 95.9 | 96 | 95.7 | 95.4 | 87.8 | 93.7 | 95.1 | 96.2 | 96.6 | 96.6 | 95.8 | 85.8 | 93 | 94.7 | 96.1 | 96.4 | 96.6 | 95.6 | ABB2UNO-2.0-I-OUTD-S-US [277V]
ABB | UNO-2.0-TL-OUTD-S-US [208V] | Y | N | N | 2.0 kW, 208 Vac Utility Interactive Inverter | 2 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327 | ABB2UNO-2.0-TL-OUTD-S-US [208V]
ABB | UNO-2.0-TL-OUTD-S-US [240V] | Y | N | N | 2.0 kW, 240 Vac Utility Interactive Inverter | 2 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.2 | 94.5 | 95.4 | 95.8 | 96 | 95.9 | 95.6 | 92.7 | 95.8 | 96.6 | 97.2 | 97.3 | 97.3 | 96.9 | 91.3 | 95.3 | 96.2 | 96.9 | 97.2 | 97.2 | 96.7 | ABB2UNO-2.0-TL-OUTD-S-US [240V]
ABB | UNO-2.0-TL-OUTD-S-US [277V] | Y | N | N | 2.0 kW, 277 Vac Utility Interactive Inverter | 2 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476 | ABB2UNO-2.0-TL-OUTD-S-US [277V]
ABB | UNO-2.0-TL-OUTD-S-US-A [208V] | Y | N | N | 2.0 kW, 208 Vac Utility Interactive Inverter with arc detector | 2 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327 | ABB2UNO-2.0-TL-OUTD-S-US-A [208V]
ABB | UNO-2.0-TL-OUTD-S-US-A [240V] | Y | N | N | 2.0 kW, 240 Vac Utility Interactive Inverter with arc detector | 2 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631 | ABB2UNO-2.0-TL-OUTD-S-US-A [240V]
ABB | UNO-2.0-TL-OUTD-S-US-A [277V] | Y | N | N | 2.0 kW, 277 Vac Utility Interactive Inverter with arc detector | 2 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476 | ABB2UNO-2.0-TL-OUTD-S-US-A [277V]
ABB | UNO-2.0-TL-OUTD-S-US-B-C-M [208V] | Y | N | N | 2.0 kW, 208 Vac Utility Interactive Inverter with revenue grade meter | 2 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327 | ABB2UNO-2.0-TL-OUTD-S-US-B-C-M [208V]
ABB | UNO-2.0-TL-OUTD-S-US-B-C-M [240V] | Y | N | N | 2.0 kW, 240 Vac Utility Interactive Inverter with revenue grade meter | 2 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631 | ABB2UNO-2.0-TL-OUTD-S-US-B-C-M [240V]
ABB | UNO-2.0-TL-OUTD-S-US-B-C-M [277V] | Y | N | N | 2.0 kW, 277 Vac Utility Interactive Inverter with revenue grade meter | 2 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476 | ABB2UNO-2.0-TL-OUTD-S-US-B-C-M [277V]
ABB | UNO-2.0-TL-OUTD-S-US-B-C-M-A [208V] | Y | N | N | 2.0 kW, 208 Vac Utility Interactive Inverter with arc detector, with revenue grade meter | 2 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327 | ABB2UNO-2.0-TL-OUTD-S-US-B-C-M-A [208V]
ABB | UNO-2.0-TL-OUTD-S-US-B-C-M-A [240V] | Y | N | N | 2.0 kW, 240 Vac Utility Interactive Inverter with arc detector, with revenue grade meter | 2 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631 | ABB2UNO-2.0-TL-OUTD-S-US-B-C-M-A [240V]
ABB | UNO-2.0-TL-OUTD-S-US-B-C-M-A [277V] | Y | N | N | 2.0 kW, 277 Vac Utility Interactive Inverter with arc detector, with revenue grade meter | 2 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476 | ABB2UNO-2.0-TL-OUTD-S-US-B-C-M-A [277V]
ABB | UNO-2.0-TL-OUTD-S-US-B-M [208V] | Y | N | N | 2.0 kW, 208 Vac Utility Interactive Inverter with revenue grade meter | 2 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327 | ABB2UNO-2.0-TL-OUTD-S-US-B-M [208V]
ABB | UNO-2.0-TL-OUTD-S-US-B-M [240V] | Y | N | N | 2.0 kW, 240 Vac Utility Interactive Inverter with revenue grade meter | 2 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631 | ABB2UNO-2.0-TL-OUTD-S-US-B-M [240V]
ABB | UNO-2.0-TL-OUTD-S-US-B-M [277V] | Y | N | N | 2.0 kW, 277 Vac Utility Interactive Inverter with revenue grade meter | 2 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476 | ABB2UNO-2.0-TL-OUTD-S-US-B-M [277V]
ABB | UNO-2.0-TL-OUTD-S-US-B-M-A [208V] | Y | N | N | 2.0 kW, 208 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 2 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327 | ABB2UNO-2.0-TL-OUTD-S-US-B-M-A [208V]
ABB | UNO-2.0-TL-OUTD-S-US-B-M-A [240V] | Y | N | N | 2.0 kW, 240 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 2 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631 | ABB2UNO-2.0-TL-OUTD-S-US-B-M-A [240V]
ABB | UNO-2.0-TL-OUTD-S-US-B-M-A [277V] | Y | N | N | 2.0 kW, 277 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 2 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476 | ABB2UNO-2.0-TL-OUTD-S-US-B-M-A [277V]
ABB | UNO-2.0-TL-OUTD-S-US-C-M [208V] | Y | N | N | 2.0 kW, 208 Vac Utility Interactive Inverter with revenue grade meter | 2 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327 | ABB2UNO-2.0-TL-OUTD-S-US-C-M [208V]
ABB | UNO-2.0-TL-OUTD-S-US-C-M [240V] | Y | N | N | 2.0 kW, 240 Vac Utility Interactive Inverter with revenue grade meter | 2 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631 | ABB2UNO-2.0-TL-OUTD-S-US-C-M [240V]
ABB | UNO-2.0-TL-OUTD-S-US-C-M [277V] | Y | N | N | 2.0 kW, 277 Vac Utility Interactive Inverter with revenue grade meter | 2 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476 | ABB2UNO-2.0-TL-OUTD-S-US-C-M [277V]
ABB | UNO-2.0-TL-OUTD-S-US-C-M-A [208V] | Y | N | N | 2.0 kW, 208 Vac Utility Interactive Inverter with revenue grade meter | 2 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327 | ABB2UNO-2.0-TL-OUTD-S-US-C-M-A [208V]
ABB | UNO-2.0-TL-OUTD-S-US-C-M-A [240V] | Y | N | N | 2.0 kW, 240 Vac Utility Interactive Inverter with revenue grade meter | 2 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631 | ABB2UNO-2.0-TL-OUTD-S-US-C-M-A [240V]
ABB | UNO-2.0-TL-OUTD-S-US-C-M-A [277V] | Y | N | N | 2.0 kW, 277 Vac Utility Interactive Inverter with revenue grade meter | 2 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476 | ABB2UNO-2.0-TL-OUTD-S-US-C-M-A [277V]
ABB | UNO-2.0-TL-OUTD-S-US-Z-A [208V] | Y | N | N | 2.0 kW, 208 Vac Utility Interactive Inverter with arc detector | 2 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327 | ABB2UNO-2.0-TL-OUTD-S-US-Z-A [208V]
ABB | UNO-2.0-TL-OUTD-S-US-Z-A [240V] | Y | N | N | 2.0 kW, 240 Vac Utility Interactive Inverter with arc detector | 2 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631 | ABB2UNO-2.0-TL-OUTD-S-US-Z-A [240V]
ABB | UNO-2.0-TL-OUTD-S-US-Z-A [277V] | Y | N | N | 2.0 kW, 277 Vac Utility Interactive Inverter with arc detector | 2 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476 | ABB2UNO-2.0-TL-OUTD-S-US-Z-A [277V]
ABB | UNO-2.0-TL-OUTD-S-US-Z-M-A [208V] | Y | N | N | 2.0 kW, 208 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 2 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 2 | 0.11 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.7068 | 94.899 | 95.5602 | 95.9572 | 95.9308 | 95.8079 | 95.6652 | 92.3515 | 95.6294 | 96.4468 | 96.9728 | 97.0562 | 97.0233 | 96.7044 | 91.0019 | 95.1782 | 96.0695 | 96.7303 | 96.8835 | 96.8764 | 96.4327 | ABB2UNO-2.0-TL-OUTD-S-US-Z-M-A [208V]
ABB | UNO-2.0-TL-OUTD-S-US-Z-M-A [240V] | Y | N | N | 2.0 kW, 240 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 2 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.1975 | 94.5303 | 95.4161 | 95.8429 | 95.9573 | 95.8859 | 95.603 | 92.6562 | 95.7866 | 96.5911 | 97.1714 | 97.3297 | 97.3297 | 96.9437 | 91.299 | 95.2613 | 96.1981 | 96.9232 | 97.1551 | 97.1651 | 96.6631 | ABB2UNO-2.0-TL-OUTD-S-US-Z-M-A [240V]
ABB | UNO-2.0-TL-OUTD-S-US-Z-M-A [277V] | Y | N | N | 2.0 kW, 277 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 2 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 2 | 0.15 | 180 | 400 | 480 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.2646 | 94.0996 | 95.0474 | 95.7968 | 95.97 | 95.9471 | 95.5 | 91.4691 | 95.1802 | 96.172 | 96.9329 | 97.1504 | 97.2299 | 96.6655 | 91.5415 | 95.4443 | 96.413 | 97.1915 | 97.4681 | 97.5166 | 96.9476 | ABB2UNO-2.0-TL-OUTD-S-US-Z-M-A [277V]
ABB | UNO-2.5-I-OUTD-S-US [208V] | Y | N | N | 2.5 kW, 208 Vac Utility Interactive Inverter. Model number may include -W | 2.5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.4 | 2.5 | 0.4 | 100 | 330 | 416 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 91.9 | 95.2 | 95.8 | 95.8 | 95.2 | 94.2 | 95.2 | 89.6 | 94.9 | 95.8 | 96.1 | 96 | 95.7 | 95.7 | 87.5 | 93.6 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | ABB2.5UNO-2.5-I-OUTD-S-US [208V]
ABB | UNO-2.5-I-OUTD-S-US [240V] | Y | N | N | 2.5 kW, 240 Vac Utility Interactive Inverter. Model number may include -W | 2.5 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.4 | 2.5 | 0.4 | 100 | 340 | 416 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 91 | 95.1 | 95.8 | 96.1 | 95.7 | 95 | 95.5 | 89.8 | 95 | 96 | 96.5 | 96.5 | 96.3 | 96.1 | 87.8 | 94 | 95.3 | 96.3 | 96.3 | 96.3 | 95.7 | ABB2.5UNO-2.5-I-OUTD-S-US [240V]
ABB | UNO-2.5-I-OUTD-S-US [277V] | Y | N | N | 2.5 kW, 277 Vac Utility Interactive Inverter. Model number may include -W | 2.5 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.5 | 2.5 | 0.5 | 100 | 360 | 416 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 89.7 | 94.7 | 95.6 | 96 | 95.9 | 95.3 | 95.5 | 89 | 94.6 | 95.7 | 96.4 | 96.6 | 96.6 | 96.1 | 87.9 | 94.1 | 95.4 | 96.4 | 96.6 | 96.6 | 95.9 | ABB2.5UNO-2.5-I-OUTD-S-US [277V]
ABB | PVI-3.0-OUTD-S-US [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | ABB3PVI-3.0-OUTD-S-US [208V]
ABB | PVI-3.0-OUTD-S-US [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | ABB3PVI-3.0-OUTD-S-US [240V]
ABB | PVI-3.0-OUTD-S-US [277V] | Y | N | N | 3 kW, 277 Vac Utility Interactive Inverter | 3 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | ABB3PVI-3.0-OUTD-S-US [277V]
ABB | PVI-3.0-OUTD-S-US-A [208V] | Y | Y | Y | 3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 3 | 208 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | ABB3PVI-3.0-OUTD-S-US-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-A [240V] | Y | Y | Y | 3 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 3 | 240 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | ABB3PVI-3.0-OUTD-S-US-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-A [277V] | Y | Y | Y | 3 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 3 | 277 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | ABB3PVI-3.0-OUTD-S-US-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | ABB3PVI-3.0-OUTD-S-US-Z [208V]
ABB | PVI-3.0-OUTD-S-US-Z [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | ABB3PVI-3.0-OUTD-S-US-Z [240V]
ABB | PVI-3.0-OUTD-S-US-Z [277V] | Y | N | N | 3 kW, 277 Vac Utility Interactive Inverter | 3 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | ABB3PVI-3.0-OUTD-S-US-Z [277V]
ABB | PVI-3.0-OUTD-S-US-Z-A [208V] | Y | Y | Y | 3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 3 | 208 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | ABB3PVI-3.0-OUTD-S-US-Z-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z-A [240V] | Y | Y | Y | 3 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 3 | 240 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | ABB3PVI-3.0-OUTD-S-US-Z-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z-A [277V] | Y | Y | Y | 3 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 3 | 277 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | ABB3PVI-3.0-OUTD-S-US-Z-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z-M-A [208V] | Y | Y | Y | 3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3 | 208 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.1 |  |  | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | ABB3PVI-3.0-OUTD-S-US-Z-M-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z-M-A [240V] | Y | Y | Y | 3 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3 | 240 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.1 |  |  | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | ABB3PVI-3.0-OUTD-S-US-Z-M-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-S-US-Z-M-A [277V] | Y | Y | Y | 3 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3 | 277 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.2 |  |  | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | ABB3PVI-3.0-OUTD-S-US-Z-M-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.0-OUTD-US [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | ABB3PVI-3.0-OUTD-US [208V]
ABB | PVI-3.0-OUTD-US [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter, model # may include -S- or -W | 3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | ABB3PVI-3.0-OUTD-US [240V]
ABB | PVI-3.0-OUTD-US [277V] | Y | N | N | 3 kW, 277 Vac Utility Interactive Inverter, model # may include -S- or -W | 3 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | ABB3PVI-3.0-OUTD-US [277V]
ABB | UNO-3.0-TL-OUTD-S-US [208V] | Y | N | N | 3.0 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567 | ABB3UNO-3.0-TL-OUTD-S-US [208V]
ABB | UNO-3.0-TL-OUTD-S-US [240V] | Y | N | N | 3.0 kW, 240 Vac Utility Interactive Inverter | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226 | ABB3UNO-3.0-TL-OUTD-S-US [240V]
ABB | UNO-3.0-TL-OUTD-S-US [277V] | Y | N | N | 3.0 kW, 277 Vac Utility Interactive Inverter | 3 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623 | ABB3UNO-3.0-TL-OUTD-S-US [277V]
ABB | UNO-3.0-TL-OUTD-S-US-A [208V] | Y | N | N | 3.0 kW, 208 Vac Utility Interactive Inverter with arc detector | 3 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567 | ABB3UNO-3.0-TL-OUTD-S-US-A [208V]
ABB | UNO-3.0-TL-OUTD-S-US-A [240V] | Y | N | N | 3.0 kW, 240 Vac Utility Interactive Inverter with arc detector | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226 | ABB3UNO-3.0-TL-OUTD-S-US-A [240V]
ABB | UNO-3.0-TL-OUTD-S-US-A [277V] | Y | N | N | 3.0 kW, 277 Vac Utility Interactive Inverter with arc detector | 3 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623 | ABB3UNO-3.0-TL-OUTD-S-US-A [277V]
ABB | UNO-3.0-TL-OUTD-S-US-B-C-M [208V] | Y | N | N | 3.0 kW, 208 Vac Utility Interactive Inverter with revenue grade meter | 3 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567 | ABB3UNO-3.0-TL-OUTD-S-US-B-C-M [208V]
ABB | UNO-3.0-TL-OUTD-S-US-B-C-M [240V] | Y | N | N | 3.0 kW, 240 Vac Utility Interactive Inverter with revenue grade meter | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226 | ABB3UNO-3.0-TL-OUTD-S-US-B-C-M [240V]
ABB | UNO-3.0-TL-OUTD-S-US-B-C-M [277V] | Y | N | N | 3.0 kW, 277 Vac Utility Interactive Inverter with revenue grade meter | 3 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623 | ABB3UNO-3.0-TL-OUTD-S-US-B-C-M [277V]
ABB | UNO-3.0-TL-OUTD-S-US-B-C-M-A [208V] | Y | N | N | 3.0 kW, 208 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567 | ABB3UNO-3.0-TL-OUTD-S-US-B-C-M-A [208V]
ABB | UNO-3.0-TL-OUTD-S-US-B-C-M-A [240V] | Y | N | N | 3.0 kW, 240 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226 | ABB3UNO-3.0-TL-OUTD-S-US-B-C-M-A [240V]
ABB | UNO-3.0-TL-OUTD-S-US-B-C-M-A [277V] | Y | N | N | 3.0 kW, 277 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623 | ABB3UNO-3.0-TL-OUTD-S-US-B-C-M-A [277V]
ABB | UNO-3.0-TL-OUTD-S-US-B-M [208V] | Y | N | N | 3.0 kW, 208 Vac Utility Interactive Inverter with revenue grade meter | 3 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567 | ABB3UNO-3.0-TL-OUTD-S-US-B-M [208V]
ABB | UNO-3.0-TL-OUTD-S-US-B-M [240V] | Y | N | N | 3.0 kW, 240 Vac Utility Interactive Inverter with revenue grade meter | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226 | ABB3UNO-3.0-TL-OUTD-S-US-B-M [240V]
ABB | UNO-3.0-TL-OUTD-S-US-B-M [277V] | Y | N | N | 3.0 kW, 277 Vac Utility Interactive Inverter with revenue grade meter | 3 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623 | ABB3UNO-3.0-TL-OUTD-S-US-B-M [277V]
ABB | UNO-3.0-TL-OUTD-S-US-B-M-A [208V] | Y | N | N | 3.0 kW, 208 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567 | ABB3UNO-3.0-TL-OUTD-S-US-B-M-A [208V]
ABB | UNO-3.0-TL-OUTD-S-US-B-M-A [240V] | Y | N | N | 3.0 kW, 240 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226 | ABB3UNO-3.0-TL-OUTD-S-US-B-M-A [240V]
ABB | UNO-3.0-TL-OUTD-S-US-B-M-A [277V] | Y | N | N | 3.0 kW, 277 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623 | ABB3UNO-3.0-TL-OUTD-S-US-B-M-A [277V]
ABB | UNO-3.0-TL-OUTD-S-US-C-M [208V] | Y | N | N | 3.0 kW, 208 Vac Utility Interactive Inverter with revenue grade meter | 3 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567 | ABB3UNO-3.0-TL-OUTD-S-US-C-M [208V]
ABB | UNO-3.0-TL-OUTD-S-US-C-M [240V] | Y | N | N | 3.0 kW 240 Vac Utility Interactive Inverter, with revenue grade meter | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226 | ABB3UNO-3.0-TL-OUTD-S-US-C-M [240V]
ABB | UNO-3.0-TL-OUTD-S-US-C-M [277V] | Y | N | N | 3.0 kW, 277 Vac Utility Interactive Inverter with revenue grade meter | 3 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623 | ABB3UNO-3.0-TL-OUTD-S-US-C-M [277V]
ABB | UNO-3.0-TL-OUTD-S-US-C-M-A [208V] | Y | N | N | 3.0 kW, 208 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567 | ABB3UNO-3.0-TL-OUTD-S-US-C-M-A [208V]
ABB | UNO-3.0-TL-OUTD-S-US-C-M-A [240V] | Y | N | N | 3.0 kW, 240 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226 | ABB3UNO-3.0-TL-OUTD-S-US-C-M-A [240V]
ABB | UNO-3.0-TL-OUTD-S-US-C-M-A [277V] | Y | N | N | 3.0 kW, 277 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623 | ABB3UNO-3.0-TL-OUTD-S-US-C-M-A [277V]
ABB | UNO-3.0-TL-OUTD-S-US-Z-A [208V] | Y | N | N | 3.0 kW, 208 Vac Utility Interactive Inverter with arc detector | 3 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567 | ABB3UNO-3.0-TL-OUTD-S-US-Z-A [208V]
ABB | UNO-3.0-TL-OUTD-S-US-Z-A [240V] | Y | N | N | 3.0 kW, 240 Vac Utility Interactive Inverter with arc detector | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226 | ABB3UNO-3.0-TL-OUTD-S-US-Z-A [240V]
ABB | UNO-3.0-TL-OUTD-S-US-Z-A [277V] | Y | N | N | 3.0 kW, 277 Vac Utility Interactive Inverter with arc detector | 3 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623 | ABB3UNO-3.0-TL-OUTD-S-US-Z-A [277V]
ABB | UNO-3.0-TL-OUTD-S-US-Z-M-A [208V] | Y | N | N | 3.0 kW, 208 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 | 3 | 0.11 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.5877 | 95.5788 | 95.9532 | 95.9149 | 95.7186 | 95.1981 | 95.6697 | 94.4062 | 96.4712 | 96.8978 | 97.0529 | 97.019 | 96.7605 | 96.8667 | 93.6377 | 96.0982 | 96.6144 | 96.8857 | 96.8551 | 96.6678 | 96.6567 | ABB3UNO-3.0-TL-OUTD-S-US-Z-M-A [208V]
ABB | UNO-3.0-TL-OUTD-S-US-Z-M-A [240V] | Y | N | N | 3.0 kW, 240 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 | 3 | 0.15 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.094 | 95.4386 | 95.8649 | 95.9573 | 95.8111 | 95.4222 | 95.7015 | 94.5916 | 96.6224 | 97.087 | 97.3297 | 97.3224 | 97.1876 | 97.1447 | 93.754 | 96.232 | 96.804 | 97.1551 | 97.1447 | 97.1026 | 96.9226 | ABB3UNO-3.0-TL-OUTD-S-US-Z-M-A [240V]
ABB | UNO-3.0-TL-OUTD-S-US-Z-M-A [277V] | Y | N | N | 3.0 kW, 277 Vac Utility Interactive Inverter with arc detector and revenue grade meter | 3 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 3 | 0.2 | 180 | 400 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.4542 | 95.1981 | 95.7797 | 95.9716 | 95.9228 | 95.6371 | 95.7266 | 93.7103 | 96.2189 | 96.8155 | 97.1633 | 97.2311 | 97.1831 | 96.9732 | 93.9658 | 96.4497 | 97.0595 | 97.4757 | 97.5241 | 97.5271 | 97.2623 | ABB3UNO-3.0-TL-OUTD-S-US-Z-M-A [277V]
ABB | UNO-DM-3.3-TL-PLUS-US-SB-RA [208V] | N | Y | Y | 3.3 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 3 | 208 | 96 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 0.9 | 3 | 0.9 | 200 | 340 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.3 | 95 | 95.4 | 95.8 | 95.7 | 95.3 | 95.5 | 93.2 | 95.6 | 96.1 | 96.4 | 96.4 | 96.2 | 96.2 | 91.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | ABB3UNO-DM-3.3-TL-PLUS-US-SB-RA [208V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.3-TL-PLUS-US-SE-RA [208V] | N | Y | Y | 3.3 kW, 208 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 3 | 208 | 96 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 0.9 | 3 | 0.9 | 200 | 340 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.3 | 95 | 95.4 | 95.8 | 95.7 | 95.3 | 95.5 | 93.2 | 95.6 | 96.1 | 96.4 | 96.4 | 96.2 | 96.2 | 91.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | ABB3UNO-DM-3.3-TL-PLUS-US-SE-RA [208V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.3-TL-PLUS-US-SZM-RA [208V] | N | Y | Y | 3.3 kW, 208 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 3 | 208 | 96 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 0.9 | 3 | 0.9 | 200 | 340 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.3 | 95 | 95.4 | 95.8 | 95.7 | 95.3 | 95.5 | 93.2 | 95.6 | 96.1 | 96.4 | 96.4 | 96.2 | 96.2 | 91.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | ABB3UNO-DM-3.3-TL-PLUS-US-SZM-RA [208V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.3-TL-PLUS-US-SZ-RA [208V] | N | Y | Y | 3.3 kW, 208 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply | 3 | 208 | 96 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 0.9 | 3 | 0.9 | 200 | 340 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.3 | 95 | 95.4 | 95.8 | 95.7 | 95.3 | 95.5 | 93.2 | 95.6 | 96.1 | 96.4 | 96.4 | 96.2 | 96.2 | 91.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | ABB3UNO-DM-3.3-TL-PLUS-US-SZ-RA [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-I-OUTD-x-US-y-Z [208V] | Y | N | N | 3.8 kW, 208 Vac Inverter, where x may include S and y = PG or NG | 3.3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 3.3 | 0.1 | 100 | 310 | 416 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 93.6 | 95.7 | 96.2 | 96.4 | 96.3 | 96 | 96.2 | 92.5 | 95.6 | 96.3 | 96.6 | 96.7 | 96.5 | 96.4 | 89.5 | 94 | 95.3 | 96.1 | 96.3 | 96.1 | 95.7 | ABB3.3PVI-3.8-I-OUTD-x-US-y-Z [208V]
ABB | UNO-DM-3.3-TL-PLUS-US-SB-RA [240V] | N | Y | Y | 3.3 kW, 240 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 3.3 | 240 | 96.5 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 0.9 | 3.3 | 0.9 | 200 | 355 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92.8 | 95.3 | 95.8 | 96.1 | 96.1 | 95.7 | 95.9 | 93.6 | 96 | 96.6 | 96.9 | 96.8 | 96.7 | 96.6 | 92.2 | 95.3 | 96 | 96.6 | 96.6 | 96.5 | 96.3 | ABB3.3UNO-DM-3.3-TL-PLUS-US-SB-RA [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.3-TL-PLUS-US-SE-RA [240V] | N | Y | Y | 3.3 kW, 240 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 3.3 | 240 | 96.5 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 0.9 | 3.3 | 0.9 | 200 | 355 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92.8 | 95.3 | 95.8 | 96.1 | 96.1 | 95.7 | 95.9 | 93.6 | 96 | 96.6 | 96.9 | 96.8 | 96.7 | 96.6 | 92.2 | 95.3 | 96 | 96.6 | 96.6 | 96.5 | 96.3 | ABB3.3UNO-DM-3.3-TL-PLUS-US-SE-RA [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.3-TL-PLUS-US-SZM-RA [240V] | N | Y | Y | 3.3 kW, 240 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 3.3 | 240 | 96.5 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 0.9 | 3.3 | 0.9 | 200 | 355 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92.8 | 95.3 | 95.8 | 96.1 | 96.1 | 95.7 | 95.9 | 93.6 | 96 | 96.6 | 96.9 | 96.8 | 96.7 | 96.6 | 92.2 | 95.3 | 96 | 96.6 | 96.6 | 96.5 | 96.3 | ABB3.3UNO-DM-3.3-TL-PLUS-US-SZM-RA [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.3-TL-PLUS-US-SZ-RA [240V] | N | Y | Y | 3.3 kW, 240 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply | 3.3 | 240 | 96.5 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 0.9 | 3.3 | 0.9 | 200 | 355 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92.8 | 95.3 | 95.8 | 96.1 | 96.1 | 95.7 | 95.9 | 93.6 | 96 | 96.6 | 96.9 | 96.8 | 96.7 | 96.6 | 92.2 | 95.3 | 96 | 96.6 | 96.6 | 96.5 | 96.3 | ABB3.3UNO-DM-3.3-TL-PLUS-US-SZ-RA [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.8-TL-PLUS-US-SB-RA [208V] | N | Y | Y | 3.8 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 3.3 | 208 | 96 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 0.9 | 3.3 | 0.9 | 200 | 340 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.7 | 95.4 | 95.7 | 95.5 | 95.2 | 95.3 | 92.9 | 95.7 | 96.2 | 96.6 | 96.6 | 96.5 | 96.4 | 90.5 | 94.5 | 95.7 | 96.2 | 96.1 | 96 | 95.8 | ABB3.3UNO-DM-3.8-TL-PLUS-US-SB-RA [208V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.8-TL-PLUS-US-SE-RA [208V] | N | Y | Y | 3.8 kW, 208 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 3.3 | 208 | 96 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 0.9 | 3.3 | 0.9 | 200 | 340 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.7 | 95.4 | 95.7 | 95.5 | 95.2 | 95.3 | 92.9 | 95.7 | 96.2 | 96.6 | 96.6 | 96.5 | 96.4 | 90.5 | 94.5 | 95.7 | 96.2 | 96.1 | 96 | 95.8 | ABB3.3UNO-DM-3.8-TL-PLUS-US-SE-RA [208V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.8-TL-PLUS-US-SZM-RA [208V] | N | Y | Y | 3.8 kW, 208 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 3.3 | 208 | 96 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 0.9 | 3.3 | 0.9 | 200 | 340 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.7 | 95.4 | 95.7 | 95.5 | 95.2 | 95.3 | 92.9 | 95.7 | 96.2 | 96.6 | 96.6 | 96.5 | 96.4 | 90.5 | 94.5 | 95.7 | 96.2 | 96.1 | 96 | 95.8 | ABB3.3UNO-DM-3.8-TL-PLUS-US-SZM-RA [208V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.8-TL-PLUS-US-SZ-RA [208V] | N | Y | Y | 3.8 kW, 208 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply | 3.3 | 208 | 96 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 0.9 | 3.3 | 0.9 | 200 | 340 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.7 | 95.4 | 95.7 | 95.5 | 95.2 | 95.3 | 92.9 | 95.7 | 96.2 | 96.6 | 96.6 | 96.5 | 96.4 | 90.5 | 94.5 | 95.7 | 96.2 | 96.1 | 96 | 95.8 | ABB3.3UNO-DM-3.8-TL-PLUS-US-SZ-RA [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US [208V] | Y | N | N | 3.6 kW, 208 Vac Utility Interactive Inverter | 3.6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | ABB3.6PVI-3.6-OUTD-S-US [208V]
ABB | PVI-3.6-OUTD-S-US [240V] | Y | N | N | 3.6 kW, 240 Vac Utility Interactive Inverter | 3.6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | ABB3.6PVI-3.6-OUTD-S-US [240V]
ABB | PVI-3.6-OUTD-S-US [277V] | Y | N | N | 3.6 kW, 277 Vac Utility Interactive Inverter | 3.6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | ABB3.6PVI-3.6-OUTD-S-US [277V]
ABB | PVI-3.6-OUTD-S-US-A [208V] | Y | Y | Y | 3.6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 3.6 | 208 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | ABB3.6PVI-3.6-OUTD-S-US-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-A [240V] | Y | Y | Y | 3.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 3.6 | 240 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | ABB3.6PVI-3.6-OUTD-S-US-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-A [277V] | Y | Y | Y | 3.6 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 3.6 | 277 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | ABB3.6PVI-3.6-OUTD-S-US-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z [208V] | Y | N | N | 3.6 kW, 208 Vac Utility Interactive Inverter | 3.6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | ABB3.6PVI-3.6-OUTD-S-US-Z [208V]
ABB | PVI-3.6-OUTD-S-US-Z [240V] | Y | N | N | 3.6 kW, 240 Vac Utility Interactive Inverter | 3.6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | ABB3.6PVI-3.6-OUTD-S-US-Z [240V]
ABB | PVI-3.6-OUTD-S-US-Z [277V] | Y | N | N | 3.6 kW, 277 Vac Utility Interactive Inverter | 3.6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | ABB3.6PVI-3.6-OUTD-S-US-Z [277V]
ABB | PVI-3.6-OUTD-S-US-Z-A [208V] | Y | Y | Y | 3.6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 3.6 | 208 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | ABB3.6PVI-3.6-OUTD-S-US-Z-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z-A [240V] | Y | Y | Y | 3.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 3.6 | 240 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | ABB3.6PVI-3.6-OUTD-S-US-Z-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z-A [277V] | Y | Y | Y | 3.6 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 3.6 | 277 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | ABB3.6PVI-3.6-OUTD-S-US-Z-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z-M-A [208V] | Y | Y | Y | 3.6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3.6 | 208 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.1 |  |  | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | ABB3.6PVI-3.6-OUTD-S-US-Z-M-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z-M-A [240V] | Y | Y | Y | 3.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3.6 | 240 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.2 |  |  | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | ABB3.6PVI-3.6-OUTD-S-US-Z-M-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-S-US-Z-M-A [277V] | Y | Y | Y | 3.6 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3.6 | 277 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.2 |  |  | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | ABB3.6PVI-3.6-OUTD-S-US-Z-M-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.6-OUTD-US [208V] | Y | N | N | 3.6 kW, 208 Vac Utility Interactive Inverter, model # may include -S- or -W | 3.6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | ABB3.6PVI-3.6-OUTD-US [208V]
ABB | PVI-3.6-OUTD-US [240V] | Y | N | N | 3.6 kW, 240 Vac Utility Interactive Inverter, model # may include -S- or -W | 3.6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | ABB3.6PVI-3.6-OUTD-US [240V]
ABB | PVI-3.6-OUTD-US [277V] | Y | N | N | 3.6 kW, 277 Vac Utility Interactive Inverter, model # may include -S- or -W | 3.6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | ABB3.6PVI-3.6-OUTD-US [277V]
ABB | PVI-3.8-I-OUTD-x-US-y-Z [240V] | Y | N | N | 3.8 kW, 240 Vac Inverter, where x may include S and y = PG or NG | 3.8 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 3.8 | 0.1 | 100 | 340 | 416 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93.7 | 95.8 | 96.2 | 96.5 | 96.4 | 96.1 | 96.3 | 92.8 | 95.9 | 96.6 | 96.9 | 96.8 | 96.8 | 96.6 | 90.7 | 94.8 | 95.9 | 96.5 | 96.5 | 96.5 | 96.1 | ABB3.8PVI-3.8-I-OUTD-x-US-y-Z [240V]
ABB | PVI-3.8-I-OUTD-x-US-y-Z [277V] | Y | N | N | 3.8 kW, 277 Vac Inverter, where x may include S and y = PG or NG | 3.8 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 3.8 | 0.1 | 100 | 362 | 416 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.9 | 95.4 | 96 | 96.3 | 96.4 | 96.1 | 96.1 | 92.3 | 95.6 | 96.4 | 96.9 | 96.9 | 96.9 | 96.6 | 91.3 | 95.2 | 96.2 | 96.8 | 96.8 | 96.9 | 96.4 | ABB3.8PVI-3.8-I-OUTD-x-US-y-Z [277V]
ABB | PVI-3.8-OUTD-S-US [208V] | Y | N | N | 3.3 kW, 208 Vac Utility Interactive Inverter with arc detector | 3.8 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | ABB3.8PVI-3.8-OUTD-S-US [208V]
ABB | PVI-3.8-OUTD-S-US [240V] | Y | N | N | 3.8 kW, 240 Vac Utility Interactive Inverter with arc detector | 3.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | ABB3.8PVI-3.8-OUTD-S-US [240V]
ABB | PVI-3.8-OUTD-S-US [277V] | Y | N | N | 3.8 kW, 277 Vac Utility Interactive Inverter with arc detector | 3.8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | ABB3.8PVI-3.8-OUTD-S-US [277V]
ABB | PVI-3.8-OUTD-S-US-A [208V] | Y | Y | Y | 3.3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 3.8 | 208 | 95.5 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | ABB3.8PVI-3.8-OUTD-S-US-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-A [240V] | Y | Y | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 3.8 | 240 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | ABB3.8PVI-3.8-OUTD-S-US-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-A [277V] | Y | Y | Y | 3.8 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 3.8 | 277 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | ABB3.8PVI-3.8-OUTD-S-US-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z [208V] | Y | N | N | 3.3 kW, 208 Vac Utility Interactive Inverter | 3.8 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | ABB3.8PVI-3.8-OUTD-S-US-Z [208V]
ABB | PVI-3.8-OUTD-S-US-Z [240V] | Y | N | N | 3.3 kW, 208 Vac Utility Interactive Inverter | 3.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | ABB3.8PVI-3.8-OUTD-S-US-Z [240V]
ABB | PVI-3.8-OUTD-S-US-Z [277V] | Y | N | N | 3.3 kW, 208 Vac Utility Interactive Inverter | 3.8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | ABB3.8PVI-3.8-OUTD-S-US-Z [277V]
ABB | PVI-3.8-OUTD-S-US-Z-A [208V] | Y | Y | Y | 3.3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 3.8 | 208 | 95.5 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | ABB3.8PVI-3.8-OUTD-S-US-Z-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z-A [240V] | Y | Y | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 3.8 | 240 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | ABB3.8PVI-3.8-OUTD-S-US-Z-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z-A [277V] | Y | Y | Y | 3.8 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 3.8 | 277 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | ABB3.8PVI-3.8-OUTD-S-US-Z-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z-M-A [208V] | Y | Y | Y | 3.3 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3.8 | 208 | 95.5 | [3/9/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | ABB3.8PVI-3.8-OUTD-S-US-Z-M-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z-M-A [240V] | Y | Y | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3.8 | 240 | 96 | [3/9/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | ABB3.8PVI-3.8-OUTD-S-US-Z-M-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-S-US-Z-M-A [277V] | Y | Y | Y | 3.8 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 3.8 | 277 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | ABB3.8PVI-3.8-OUTD-S-US-Z-M-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-3.8-OUTD-US [208V] | Y | N | N | 3.3 kW, 208 Vac Utility Interactive Inverter | 3.8 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | ABB3.8PVI-3.8-OUTD-US [208V]
ABB | PVI-3.8-OUTD-US [240V] | Y | N | N | 3.8 kW, 240 Vac Utility Interactive Inverter | 3.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | ABB3.8PVI-3.8-OUTD-US [240V]
ABB | PVI-3.8-OUTD-US [277V] | Y | N | N | 3.8 kW, 277 Vac Utility Interactive Inverter | 3.8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | ABB3.8PVI-3.8-OUTD-US [277V]
ABB | UNO-DM-3.8-TL-PLUS-US-SB-RA [240V] | Y | Y | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 3.8 | 240 | 96.5 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 1 | 3.8 | 1 | 200 | 355 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 95.7 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 96.7 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5 | 96.3 | ABB3.8UNO-DM-3.8-TL-PLUS-US-SB-RA [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.8-TL-PLUS-US-SE-RA [240V] | Y | Y | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 3.8 | 240 | 96.5 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 1 | 3.8 | 1 | 200 | 355 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 95.7 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 96.7 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5 | 96.3 | ABB3.8UNO-DM-3.8-TL-PLUS-US-SE-RA [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.8-TL-PLUS-US-SZM-RA [240V] | Y | Y | Y | 3.8 kW, 240 Vac Grid Support Interactive Utility Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 3.8 | 240 | 96.5 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1 | 3.8 | 1 | 200 | 355 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 95.7 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 96.7 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5 | 96.3 | ABB3.8UNO-DM-3.8-TL-PLUS-US-SZM-RA [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-3.8-TL-PLUS-US-SZ-RA [240V] | Y | Y | Y | 3.8 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and Rapid Shutdown power supply | 3.8 | 240 | 96.5 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1 | 3.8 | 1 | 200 | 355 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92 | 95 | 95.7 | 95.9 | 96 | 95.8 | 95.7 | 93.7 | 96 | 96.6 | 96.9 | 97 | 96.8 | 96.7 | 91.7 | 95.2 | 96 | 96.6 | 96.7 | 96.5 | 96.3 | ABB3.8UNO-DM-3.8-TL-PLUS-US-SZ-RA [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US [208V] | Y | N | N | 4.2 kW, 208 Vac Utility Interactive Inverter (with Zigbee -Z) | 4.2 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6 | ABB4.2PVI-4.2-OUTD-S-US [208V]
ABB | PVI-4.2-OUTD-S-US [240V] | Y | N | N | 4.2 kW, 240 Vac Utility Interactive Inverter (with Zigbee -Z) | 4.2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96 | ABB4.2PVI-4.2-OUTD-S-US [240V]
ABB | PVI-4.2-OUTD-S-US [277V] | Y | N | N | 4.2 kW, 277 Vac Utility Interactive Inverter (with Zigbee -Z) | 4.2 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | ABB4.2PVI-4.2-OUTD-S-US [277V]
ABB | PVI-4.2-OUTD-S-US-A [208V] | Y | Y | Y | 4.2 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 4.2 | 208 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6 | ABB4.2PVI-4.2-OUTD-S-US-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-A [240V] | Y | Y | Y | 4.2 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 4.2 | 240 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96 | ABB4.2PVI-4.2-OUTD-S-US-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-A [277V] | Y | Y | Y | 4.2 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 4.2 | 277 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | ABB4.2PVI-4.2-OUTD-S-US-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z [208V] | Y | N | N | 4.2 kW, 208 Vac Utility Interactive Inverter | 4.2 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6 | ABB4.2PVI-4.2-OUTD-S-US-Z [208V]
ABB | PVI-4.2-OUTD-S-US-Z [240V] | Y | N | N | 4.2 kW, 240 Vac Utility Interactive Inverter | 4.2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96 | ABB4.2PVI-4.2-OUTD-S-US-Z [240V]
ABB | PVI-4.2-OUTD-S-US-Z [277V] | Y | N | N | 4.2 kW, 277 Vac Utility Interactive Inverter | 4.2 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | ABB4.2PVI-4.2-OUTD-S-US-Z [277V]
ABB | PVI-4.2-OUTD-S-US-Z-A [208V] | Y | Y | Y | 4.2 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 4.2 | 208 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6 | ABB4.2PVI-4.2-OUTD-S-US-Z-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z-A [240V] | Y | Y | Y | 4.2 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 4.2 | 240 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96 | ABB4.2PVI-4.2-OUTD-S-US-Z-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z-A [277V] | Y | Y | Y | 4.2 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 4.2 | 277 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | ABB4.2PVI-4.2-OUTD-S-US-Z-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z-M-A [208V] | Y | Y | Y | 4.2 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 4.2 | 208 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.1 |  |  | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6 | ABB4.2PVI-4.2-OUTD-S-US-Z-M-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z-M-A [240V] | Y | Y | Y | 4.2 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 4.2 | 240 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.2 |  |  | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96 | ABB4.2PVI-4.2-OUTD-S-US-Z-M-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-S-US-Z-M-A [277V] | Y | Y | Y | 4.2 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 4.2 | 277 | 96 | [03/09/2017] | [A.4.0.B, B.4.2.2, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.2 |  |  | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | ABB4.2PVI-4.2-OUTD-S-US-Z-M-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-4.2-OUTD-US [208V] | Y | N | N | 4.2 kW, 208 Vac Utility Interactive Inverter. Model number may include -S- or -W | 4.2 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6 | ABB4.2PVI-4.2-OUTD-US [208V]
ABB | PVI-4.2-OUTD-US [240V] | Y | N | N | 4.2 kW, 240 Vac Utility Interactive Inverter. Model number may include -S- or -W | 4.2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96 | ABB4.2PVI-4.2-OUTD-US [240V]
ABB | PVI-4.2-OUTD-US [277V] | Y | N | N | 4.2 kW, 277 Vac Utility Interactive Inverter. Model number may include -S- or -W | 4.2 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | ABB4.2PVI-4.2-OUTD-US [277V]
ABB | UNO-DM-4.6-TL-PLUS-US-SB-RA [208V] | N | Y | Y | 4.6 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 4.2 | 208 | 96 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 0.9 | 4.2 | 0.9 | 200 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.6 | 95 | 95.7 | 95.6 | 95.2 | 95 | 95.2 | 94.1 | 96 | 96.4 | 96.6 | 96.5 | 96.1 | 96.4 | 92.3 | 95.2 | 96 | 96.2 | 96 | 95.8 | 95.8 | ABB4.2UNO-DM-4.6-TL-PLUS-US-SB-RA [208V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-4.6-TL-PLUS-US-SE-RA [208V] | N | Y | Y | 4.6 kW, 208 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 4.2 | 208 | 96 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 0.9 | 4.2 | 0.9 | 200 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.6 | 95 | 95.7 | 95.6 | 95.2 | 95 | 95.2 | 94.1 | 96 | 96.4 | 96.6 | 96.5 | 96.1 | 96.4 | 92.3 | 95.2 | 96 | 96.2 | 96 | 95.8 | 95.8 | ABB4.2UNO-DM-4.6-TL-PLUS-US-SE-RA [208V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-4.6-TL-PLUS-US-SZM-RA [208V] | N | Y | Y | 4.6 kW, 208 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 4.2 | 208 | 96 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 0.9 | 4.2 | 0.9 | 200 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.6 | 95 | 95.7 | 95.6 | 95.2 | 95 | 95.2 | 94.1 | 96 | 96.4 | 96.6 | 96.5 | 96.1 | 96.4 | 92.3 | 95.2 | 96 | 96.2 | 96 | 95.8 | 95.8 | ABB4.2UNO-DM-4.6-TL-PLUS-US-SZM-RA [208V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-4.6-TL-PLUS-US-SZ-RA [208V] | N | Y | Y | 4.6 kW, 208 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply | 4.2 | 208 | 96 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 0.9 | 4.2 | 0.9 | 200 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.6 | 95 | 95.7 | 95.6 | 95.2 | 95 | 95.2 | 94.1 | 96 | 96.4 | 96.6 | 96.5 | 96.1 | 96.4 | 92.3 | 95.2 | 96 | 96.2 | 96 | 95.8 | 95.8 | ABB4.2UNO-DM-4.6-TL-PLUS-US-SZ-RA [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-4.6-1-OUTD-x-US-y [208V] | Y | N | N | 4.6 kW, 208 Vac Inverter, where x may include S and y = PG or NG | 4.6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.1 | 4.6 | 0.1 | 100 | 310 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.6 | 96.1 | 96.2 | 96.4 | 95.9 | 95.1 | 96 | 94.1 | 96.3 | 96.6 | 96.7 | 96.5 | 96.2 | 96.4 | 91.8 | 95.1 | 95.9 | 96.3 | 96 | 95.9 | 95.8 | ABB4.6PVI-4.6-1-OUTD-x-US-y [208V]
ABB | PVI-4.6-1-OUTD-x-US-y [240V] | Y | N | N | 4.6 kW, 240 Vac Inverter, where x may include S and y = PG or NG | 4.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.1 | 4.6 | 0.1 | 100 | 340 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.1 | 96 | 96.2 | 96.5 | 96.2 | 95.6 | 96.1 | 93.8 | 96.3 | 96.7 | 96.9 | 96.8 | 96.6 | 96.6 | 92 | 95.4 | 96.2 | 96.6 | 96.5 | 96.5 | 96.2 | ABB4.6PVI-4.6-1-OUTD-x-US-y [240V]
ABB | PVI-4.6-1-OUTD-x-US-y [277V] | Y | N | N | 4.6 kW, 277 Vac Inverter, where x may include S and y = PG or NG | 4.6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.1 | 4.6 | 0.1 | 100 | 360 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.4 | 95.7 | 96.1 | 96.4 | 96.3 | 95.9 | 96.1 | 93.3 | 96.1 | 96.6 | 97 | 96.9 | 96.9 | 96.7 | 92.6 | 95.8 | 96.6 | 97 | 96.8 | 96.8 | 96.6 | ABB4.6PVI-4.6-1-OUTD-x-US-y [277V]
ABB | PVI-4.6-I-OUTD-x-US-y-Z [208V] | Y | N | N | 4.6 kW, 208 Vac Inverter, where x may include S and y = PG or NG | 4.6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 4.6 | 0.1 | 100 | 310 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.6 | 96.1 | 96.2 | 96.4 | 95.9 | 95.1 | 96 | 94.1 | 96.3 | 96.6 | 96.7 | 96.5 | 96.2 | 96.4 | 91.8 | 95.1 | 95.9 | 96.3 | 96 | 95.9 | 95.8 | ABB4.6PVI-4.6-I-OUTD-x-US-y-Z [208V]
ABB | PVI-4.6-I-OUTD-x-US-y-Z [240V] | Y | N | N | 4.6 kW, 240 Vac Inverter, where x may include S and y = PG or NG | 4.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 4.6 | 0.1 | 100 | 340 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.1 | 96 | 96.2 | 96.5 | 96.2 | 95.6 | 96.1 | 93.8 | 96.3 | 96.7 | 96.9 | 96.8 | 96.6 | 96.6 | 92 | 95.4 | 96.2 | 96.6 | 96.5 | 96.5 | 96.2 | ABB4.6PVI-4.6-I-OUTD-x-US-y-Z [240V]
ABB | PVI-4.6-I-OUTD-x-US-y-Z [277V] | Y | N | N | 4.6 kW, 277 Vac Inverter, where x may include S and y = PG or NG | 4.6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 4.6 | 0.1 | 100 | 360 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.4 | 95.7 | 96.1 | 96.4 | 96.3 | 95.9 | 96.1 | 93.3 | 96.1 | 96.6 | 97 | 96.9 | 96.9 | 96.7 | 92.6 | 95.8 | 96.6 | 97 | 96.8 | 96.8 | 96.6 | ABB4.6PVI-4.6-I-OUTD-x-US-y-Z [277V]
ABB | UNO-DM-4.6-TL-PLUS-US-SB-RA [240V] | Y | Y | Y | 4.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 4.6 | 240 | 96.5 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 1 | 4.6 | 1 | 200 | 355 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 95.8 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 96.8 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3 | 96.4 | ABB4.6UNO-DM-4.6-TL-PLUS-US-SB-RA [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-4.6-TL-PLUS-US-SE-RA [240V] | Y | Y | Y | 4.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 4.6 | 240 | 96.5 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 1 | 4.6 | 1 | 200 | 355 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 95.8 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 96.8 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3 | 96.4 | ABB4.6UNO-DM-4.6-TL-PLUS-US-SE-RA [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-4.6-TL-PLUS-US-SZM-RA [240V] | Y | Y | Y | 4.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 4.6 | 240 | 96.5 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 1 | 4.6 | 1 | 200 | 355 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 95.8 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 96.8 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3 | 96.4 | ABB4.6UNO-DM-4.6-TL-PLUS-US-SZM-RA [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-4.6-TL-PLUS-US-SZ-RA [240V] | Y | Y | Y | 4.6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector and Rapid Shutdown power supply | 4.6 | 240 | 96.5 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1 | 4.6 | 1 | 200 | 355 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.1 | 95.3 | 95.9 | 96 | 95.9 | 95.5 | 95.8 | 94.5 | 96.3 | 96.8 | 97 | 96.9 | 96.6 | 96.8 | 92.6 | 95.6 | 96.3 | 96.6 | 96.6 | 96.3 | 96.4 | ABB4.6UNO-DM-4.6-TL-PLUS-US-SZ-RA [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-5.0-TL-PLUS-US-SB-RA [208V] | N | Y | Y | 5.0 kW, 208 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 4.6 | 208 | 96.5 | [05/02/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 1 | 4.6 | 1 | 240 | 340 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93 | 95.4 | 96.2 | 96.4 | 96.3 | 96.1 | 96.1 | 93.6 | 95.9 | 96.5 | 96.8 | 96.8 | 96.6 | 96.6 | 90.8 | 94.9 | 95.8 | 96.4 | 96.4 | 96.3 | 96 | ABB4.6UNO-DM-5.0-TL-PLUS-US-SB-RA [208V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-5.0-TL-PLUS-US-SE-RA [208V] | N | Y | Y | 5.0 kW, 208 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 4.6 | 208 | 96.5 | [5/2/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 1 | 4.6 | 1 | 240 | 340 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93 | 95.4 | 96.2 | 96.4 | 96.3 | 96.1 | 96.1 | 93.6 | 95.9 | 96.5 | 96.8 | 96.8 | 96.6 | 96.6 | 90.8 | 94.9 | 95.8 | 96.4 | 96.4 | 96.3 | 96 | ABB4.6UNO-DM-5.0-TL-PLUS-US-SE-RA [208V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-5.0-TL-PLUS-US-SZM-RA [208V] | N | Y | Y | 5.0 kW, 208 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 4.6 | 208 | 96.5 | [5/2/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 1 | 4.6 | 1 | 240 | 340 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93 | 95.4 | 96.2 | 96.4 | 96.3 | 96.1 | 96.1 | 93.6 | 95.9 | 96.5 | 96.8 | 96.8 | 96.6 | 96.6 | 90.8 | 94.9 | 95.8 | 96.4 | 96.4 | 96.3 | 96 | ABB4.6UNO-DM-5.0-TL-PLUS-US-SZM-RA [208V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-5.0-TL-PLUS-US-SZ-RA [208V] | N | Y | Y | 5.0 kW, 208 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply | 4.6 | 208 | 96.5 | [5/2/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 1 | 4.6 | 1 | 240 | 340 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93 | 95.4 | 96.2 | 96.4 | 96.3 | 96.1 | 96.1 | 93.6 | 95.9 | 96.5 | 96.8 | 96.8 | 96.6 | 96.6 | 90.8 | 94.9 | 95.8 | 96.4 | 96.4 | 96.3 | 96 | ABB4.6UNO-DM-5.0-TL-PLUS-US-SZ-RA [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-S-US-Z [208V] | Y | N | N | 5 kW, 208 Vac Utility Interactive Inverter with meter and with arc detector | 5 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | ABB5PVI-5000-OUTD-S-US-Z [208V]
ABB | PVI-5000-OUTD-S-US-Z [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter with meter and with arc detector | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | ABB5PVI-5000-OUTD-S-US-Z [240V]
ABB | PVI-5000-OUTD-S-US-Z [277V] | Y | N | N | 5 kW, 277 Vac Utility Interactive Inverter with meter and with arc detector | 5 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | ABB5PVI-5000-OUTD-S-US-Z [277V]
ABB | PVI-5000-OUTD-S-US-Z-A [208V] | Y | N | N | 5 kW, 208 Vac Utility Interactive Inverter with meter and with arc detector | 5 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | ABB5PVI-5000-OUTD-S-US-Z-A [208V]
ABB | PVI-5000-OUTD-S-US-Z-A [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter with meter and with arc detector | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | ABB5PVI-5000-OUTD-S-US-Z-A [240V]
ABB | PVI-5000-OUTD-S-US-Z-A [277V] | Y | N | N | 5 kW, 277 Vac Utility Interactive Inverter with meter and with arc detector | 5 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | ABB5PVI-5000-OUTD-S-US-Z-A [277V]
ABB | PVI-5000-OUTD-US [208V] | Y | N | N | 5 kW, 208 Vac Utility Interactive Inverter | 5 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | ABB5PVI-5000-OUTD-US [208V]
ABB | PVI-5000-OUTD-US [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | ABB5PVI-5000-OUTD-US [240V]
ABB | PVI-5000-OUTD-US [277V] | Y | N | N | 5 kW, 277 Vac Utility Interactive Inverter | 5 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | ABB5PVI-5000-OUTD-US [277V]
ABB | PVI-5000-OUTD-US-A [208V] | Y | Y | Y | 5 kW, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 5 | 208 | 96 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | ABB5PVI-5000-OUTD-US-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-A [240V] | Y | Y | Y | 5 kW, 240 Vac Grid Support Utility Interactive Inverter with arc detector | 5 | 240 | 96.5 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | ABB5PVI-5000-OUTD-US-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-A [277V] | Y | Y | Y | 5 kW, 277 Vac Grid Support Utility Interactive Inverter with arc detector | 5 | 277 | 96.5 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | ABB5PVI-5000-OUTD-US-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z [208V] | Y | N | N | 5 kW, 208 Vac Utility Interactive Inverter | 5 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | ABB5PVI-5000-OUTD-US-Z [208V]
ABB | PVI-5000-OUTD-US-Z [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | ABB5PVI-5000-OUTD-US-Z [240V]
ABB | PVI-5000-OUTD-US-Z [277V] | Y | N | N | 5 kW, 277 Vac Utility Interactive Inverter | 5 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | ABB5PVI-5000-OUTD-US-Z [277V]
ABB | PVI-5000-OUTD-US-Z-A [208V] | Y | Y | Y | 5 kW, 208 Vac Grid Support Utility Interactive Inverter | 5 | 208 | 96 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | ABB5PVI-5000-OUTD-US-Z-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z-A [240V] | Y | Y | Y | 5 kW, 240 Vac Grid Support Utility Interactive Inverter | 5 | 240 | 96.5 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | ABB5PVI-5000-OUTD-US-Z-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z-A [277V] | Y | Y | Y | 5 kW, 277 Vac Grid Support Utility Interactive Inverter | 5 | 277 | 96.5 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | ABB5PVI-5000-OUTD-US-Z-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z-M-A [208V] | Y | Y | Y | 5 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 5 | 208 | 96 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | ABB5PVI-5000-OUTD-US-Z-M-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z-M-A [240V] | Y | Y | Y | 5 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 5 | 240 | 96.5 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | ABB5PVI-5000-OUTD-US-Z-M-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-5000-OUTD-US-Z-M-A [277V] | Y | Y | Y | 5 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 5 | 277 | 96.5 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | ABB5PVI-5000-OUTD-US-Z-M-A [277V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-5.0-TL-PLUS-US-SB-RA [240V] | N | Y | Y | 5.0 kW, 240 Vac Grid Support Interactive Inverter with arc detector, WLAN, and Rapid Shutdown power supply | 5 | 240 | 96.5 | [5/2/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 1 | 5 | 1 | 200 | 355 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.2 | 94 | 96.3 | 96.9 | 97.2 | 97.2 | 97 | 97 | 91.5 | 95.3 | 96.3 | 96.8 | 96.9 | 96.8 | 96.5 | ABB5UNO-DM-5.0-TL-PLUS-US-SB-RA [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-5.0-TL-PLUS-US-SE-RA [240V] | N | Y | Y | 5.0 kW, 240 Vac Grid Support Interactive Inverter with arc detector, Ethernet LAN, and Rapid Shutdown power supply | 5 | 240 | 96.5 | [5/2/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 1 | 5 | 1 | 200 | 355 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.2 | 94 | 96.3 | 96.9 | 97.2 | 97.2 | 97 | 97 | 91.5 | 95.3 | 96.3 | 96.8 | 96.9 | 96.8 | 96.5 | ABB5UNO-DM-5.0-TL-PLUS-US-SE-RA [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-5.0-TL-PLUS-US-SZM-RA [240V] | N | Y | Y | 5.0 kW, 240 Vac Grid Support Interactive Inverter with arc detector, revenue grade meter, Zigbee radio, and Rapid Shutdown power supply | 5 | 240 | 96.5 | [5/2/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 1 | 5 | 1 | 200 | 355 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.2 | 94 | 96.3 | 96.9 | 97.2 | 97.2 | 97 | 97 | 91.5 | 95.3 | 96.3 | 96.8 | 96.9 | 96.8 | 96.5 | ABB5UNO-DM-5.0-TL-PLUS-US-SZM-RA [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-5.0-TL-PLUS-US-SZ-RA [240V] | N | Y | Y | 5.0 kW, 240 Vac Grid Support Interactive Inverter with arc detector and Rapid Shutdown power supply | 5 | 240 | 96.5 | [5/2/2017] | [A.1.2.8, B.0.4.4, C.0.5.0] | 2018-10-15 | Y | N |  | 1 | 5 | 1 | 200 | 355 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.2 | 94 | 96.3 | 96.9 | 97.2 | 97.2 | 97 | 97 | 91.5 | 95.3 | 96.3 | 96.8 | 96.9 | 96.8 | 96.5 | ABB5UNO-DM-5.0-TL-PLUS-US-SZ-RA [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-S-US-A [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | ABB6PVI-6000-OUTD-S-US-A [208V]
ABB | PVI-6000-OUTD-S-US-A [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | ABB6PVI-6000-OUTD-S-US-A [240V]
ABB | PVI-6000-OUTD-S-US-A [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | ABB6PVI-6000-OUTD-S-US-A [277V]
ABB | PVI-6000-OUTD-S-US-Z [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | ABB6PVI-6000-OUTD-S-US-Z [208V]
ABB | PVI-6000-OUTD-S-US-Z [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | ABB6PVI-6000-OUTD-S-US-Z [240V]
ABB | PVI-6000-OUTD-S-US-Z [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | ABB6PVI-6000-OUTD-S-US-Z [277V]
ABB | PVI-6000-OUTD-S-US-Z-A [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | ABB6PVI-6000-OUTD-S-US-Z-A [208V]
ABB | PVI-6000-OUTD-S-US-Z-A [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | ABB6PVI-6000-OUTD-S-US-Z-A [240V]
ABB | PVI-6000-OUTD-S-US-Z-A [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter with meter and with arc detector | 6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | ABB6PVI-6000-OUTD-S-US-Z-A [277V]
ABB | PVI-6000-OUTD-US [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter | 6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | ABB6PVI-6000-OUTD-US [208V]
ABB | PVI-6000-OUTD-US [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | ABB6PVI-6000-OUTD-US [240V]
ABB | PVI-6000-OUTD-US [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | ABB6PVI-6000-OUTD-US [277V]
ABB | PVI-6000-OUTD-US-A [208V] | Y | Y | Y | 6 kW, 208 Vac Grid Support Utility Interactive Inverter | 6 | 208 | 96 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | ABB6PVI-6000-OUTD-US-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-A [240V] | Y | Y | Y | 6 kW, 240 Vac Grid Support Utility Interactive Inverter | 6 | 240 | 96.5 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | ABB6PVI-6000-OUTD-US-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-A [277V] | Y | Y | Y | 6 kW, 277 Vac Grid Support Utility Interactive Inverter | 6 | 277 | 96.5 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | ABB6PVI-6000-OUTD-US-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter | 6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | ABB6PVI-6000-OUTD-US-Z [208V]
ABB | PVI-6000-OUTD-US-Z [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | ABB6PVI-6000-OUTD-US-Z [240V]
ABB | PVI-6000-OUTD-US-Z [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | ABB6PVI-6000-OUTD-US-Z [277V]
ABB | PVI-6000-OUTD-US-Z-A [208V] | Y | Y | Y | 6 kW, 208 Vac Grid Support Utility Interactive Inverter | 6 | 208 | 96 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | ABB6PVI-6000-OUTD-US-Z-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z-A [240V] | Y | Y | Y | 6 kW, 240 Vac Grid Support Utility Interactive Inverter | 6 | 240 | 96.5 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | ABB6PVI-6000-OUTD-US-Z-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z-A [277V] | Y | Y | Y | 6 kW, 277 Vac Grid Support Utility Interactive Inverter | 6 | 277 | 96.5 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | ABB6PVI-6000-OUTD-US-Z-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z-M-A [208V] | Y | Y | Y | 6 kW, 208 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 6 | 208 | 96 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | ABB6PVI-6000-OUTD-US-Z-M-A [208V] | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z-M-A [240V] | Y | Y | Y | 6 kW, 240 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 6 | 240 | 96.5 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | ABB6PVI-6000-OUTD-US-Z-M-A [240V] | 2017-07-01 | 2018-10-15
ABB | PVI-6000-OUTD-US-Z-M-A [277V] | Y | Y | Y | 6 kW, 277 Vac Grid Support Utility Interactive Inverter with arc-fault detection and meter | 6 | 277 | 96.5 | [2/7/2017] | [A.4.1.0, B.4.2.0, C.2.0.0] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | ABB6PVI-6000-OUTD-US-Z-M-A [277V] | 2017-07-01 | 2018-10-15
ABB | UNO-DM-6.0-TL-PLUS-US-SB-RA [208V] | N | Y | Y | 6.0 kW (208Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, RSD PSU | 6 | 208 | 97 | [08/28/2017] | [A.1.2.B , B.0.4.9, C.0.5.7] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.3 |  |  | 240 | 340 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.6 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 96.9 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8 | 96.8 | ABB6UNO-DM-6.0-TL-PLUS-US-SB-RA (208V) | 2017-11-01 | 2018-10-15
ABB | UNO-DM-6.0-TL-PLUS-US-SB-RA [240V] | N | Y | Y | 6.0 kW (240Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, RSD PSU | 6 | 240 | 97 | [08/28/2017] | [A.1.2.B , B.0.4.9, C.0.5.7] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.3 |  |  | 200 | 355 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 96.6 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 97.3 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4 | 97.2 | ABB6UNO-DM-6.0-TL-PLUS-US-SB-RA (240V) | 2017-11-01 | 2018-10-15
ABB | UNO-DM-6.0-TL-PLUS-US-SC-RA [208V] | N | Y | Y | 6.0 kW (208Vac) Grid Support Utility Interactive Inverter w/ arc detector, cellular, RSD PSU | 6 | 208 | 97 | [08/28/2017] | [A.1.2.B , B.0.4.9, C.0.5.7] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.3 |  |  | 240 | 340 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.6 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 96.9 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8 | 96.8 | ABB6UNO-DM-6.0-TL-PLUS-US-SC-RA (208V) | 2017-11-01 | 2018-10-15
ABB | UNO-DM-6.0-TL-PLUS-US-SC-RA [240V] | N | Y | Y | 6.0 kW (240Vac) Grid Support Utility Interactive Inverter w/ arc detector, cellular, RSD PSU | 6 | 240 | 97 | [08/28/2017] | [A.1.2.B , B.0.4.9, C.0.5.7] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.3 |  |  | 200 | 355 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 96.6 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 97.3 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4 | 97.2 | ABB6UNO-DM-6.0-TL-PLUS-US-SC-RA (240V) | 2017-11-01 | 2018-10-15
ABB | UNO-DM-6.0-TL-PLUS-US-SE-RA [208V] | N | Y | Y | 6.0 kW (208Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, Ethernet card, RSD PSU | 6 | 208 | 97 | [08/28/2017] | [A.1.2.B , B.0.4.9, C.0.5.7] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.3 |  |  | 240 | 340 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.6 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 96.9 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8 | 96.8 | ABB6UNO-DM-6.0-TL-PLUS-US-SE-RA (208V) | 2017-11-01 | 2018-10-15
ABB | UNO-DM-6.0-TL-PLUS-US-SE-RA [240V] | N | Y | Y | 6.0 kW (240Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, Ethernet card, RSD PSU | 6 | 240 | 97 | [08/28/2017] | [A.1.2.B , B.0.4.9, C.0.5.7] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.3 |  |  | 200 | 355 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 96.6 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 97.3 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4 | 97.2 | ABB6UNO-DM-6.0-TL-PLUS-US-SE-RA (240V) | 2017-11-01 | 2018-10-15
ABB | UNO-DM-6.0-TL-PLUS-US-S-XRA [208V] | N | Y | Y | 6.0 kW (208Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, RSD PSU | 6 | 208 | 97 | [08/28/2017] | [A.1.2.B , B.0.4.9, C.0.5.7] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.3 |  |  | 240 | 340 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.6 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 96.9 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8 | 96.8 | ABB6UNO-DM-6.0-TL-PLUS-US-S-XRA (208V) | 2017-11-01 | 2018-10-15
ABB | UNO-DM-6.0-TL-PLUS-US-S-XRA [240V] | N | Y | Y | 6.0 kW (240Vac) Grid Support Utility Interactive Inverter w/ arc detector, WLAN, RSD PSU | 6 | 240 | 97 | [08/28/2017] | [A.1.2.B , B.0.4.9, C.0.5.7] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.3 |  |  | 200 | 355 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 96.6 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 97.3 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4 | 97.2 | ABB6UNO-DM-6.0-TL-PLUS-US-S-XRA (240V) | 2017-11-01 | 2018-10-15
ABB | UNO-DM-6.0-TL-PLUS-US-SZM-RA [208V] | N | Y | Y | 6.0 kW (208Vac) Grid Support Utility Interactive Inverter w/ arc detector, Zigbee, Revenue Grade Meter, RSD PSU | 6 | 208 | 97 | [08/28/2017] | [A.1.2.B , B.0.4.9, C.0.5.7] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.3 |  |  | 240 | 340 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.6 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 96.9 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 96.8 | 96.8 | ABB6UNO-DM-6.0-TL-PLUS-US-SZM-RA (208V) | 2017-11-01 | 2018-10-15
ABB | UNO-DM-6.0-TL-PLUS-US-SZM-RA [240V] | N | Y | Y | 6.0 kW (240Vac) Grid Support Utility Interactive Inverter w/ arc detector, Zigbee, Revenue Grade Meter, RSD PSU | 6 | 240 | 97 | [08/28/2017] | [A.1.2.B , B.0.4.9, C.0.5.7] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.3 |  |  | 200 | 355 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 96.3 | 96.6 | 96.8 | 96.7 | 96.4 | 96.6 | 95.1 | 96.9 | 97.3 | 97.4 | 97.4 | 97.2 | 97.3 | 93.8 | 96.4 | 97.1 | 97.4 | 97.5 | 97.4 | 97.2 | ABB6UNO-DM-6.0-TL-PLUS-US-SZM-RA (240V) | 2017-11-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-A [208V] | Y | Y | Y | 7.6 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 208 | 97 | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.3 |  |  | 200 | 340 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.9 | 96 | 96.4 | 96.5 | 96.4 | 96.1 | 96.3 | 95.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93.8 | 96.3 | 96.8 | 97.1 | 97 | 96.7 | 96.8 | ABB7.6UNO-7.6-TL-OUTD-S-US-A [208V] | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-A [240V] | Y | Y | Y | 7.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 240 | 97 | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.4 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.1 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 95.4 | 97.1 | 97.5 | 97.7 | 97.6 | 97.4 | 97.5 | 93.9 | 96.5 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | ABB7.6UNO-7.6-TL-OUTD-S-US-A [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-A [277V] | Y | Y | Y | 7.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 277 | 97 | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.5 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.1 | 95.3 | 96.1 | 96.6 | 96.6 | 96.4 | 96.3 | 93.9 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 94.2 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | ABB7.6UNO-7.6-TL-OUTD-S-US-A [277V] | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-A [208V] | Y | Y | Y | 7.6 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 208 | 97 | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.3 |  |  | 200 | 340 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.9 | 96 | 96.4 | 96.5 | 96.4 | 96.1 | 96.3 | 95.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93.8 | 96.3 | 96.8 | 97.1 | 97 | 96.7 | 96.8 | ABB7.6UNO-7.6-TL-OUTD-S-US-Z-A [208V] | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-A [240V] | Y | Y | Y | 7.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 240 | 97 | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.4 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.1 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 95.4 | 97.1 | 97.5 | 97.7 | 97.6 | 97.4 | 97.5 | 93.9 | 96.5 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | ABB7.6UNO-7.6-TL-OUTD-S-US-Z-A [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-A [277V] | Y | Y | Y | 7.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 277 | 97 | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.5 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.1 | 95.3 | 96.1 | 96.6 | 96.6 | 96.4 | 96.3 | 93.9 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 94.2 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | ABB7.6UNO-7.6-TL-OUTD-S-US-Z-A [277V] | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-M [208V] | Y | N | N | 7.6 kW, 208 Vac transformerless Utility Interactive Inverter with arc detector | 7.6 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.3 |  |  | 200 | 340 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.9 | 96 | 96.4 | 96.5 | 96.4 | 96.1 | 96.3 | 95.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93.8 | 96.3 | 96.8 | 97.1 | 97 | 96.7 | 96.8 | ABB7.6UNO-7.6-TL-OUTD-S-US-Z-M [208V]
ABB | UNO-7.6-TL-OUTD-S-US-Z-M [240V] | Y | N | N | 7.6 kW, 240 Vac transformerless Utility Interactive Inverter with arc detector | 7.6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.4 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.1 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 95.4 | 97.1 | 97.5 | 97.7 | 97.6 | 97.4 | 97.5 | 93.9 | 96.5 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | ABB7.6UNO-7.6-TL-OUTD-S-US-Z-M [240V]
ABB | UNO-7.6-TL-OUTD-S-US-Z-M [277V] | Y | N | N | 7.6 kW, 277 Vac transformerless Utility Interactive Inverter with arc detector | 7.6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.5 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.1 | 95.3 | 96.1 | 96.6 | 96.6 | 96.4 | 96.3 | 93.9 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 94.2 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | ABB7.6UNO-7.6-TL-OUTD-S-US-Z-M [277V]
ABB | UNO-7.6-TL-OUTD-S-US-Z-M-A [208V] | Y | Y | Y | 7.6 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 208 | 97 | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.3 |  |  | 200 | 340 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.9 | 96 | 96.4 | 96.5 | 96.4 | 96.1 | 96.3 | 95.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93.8 | 96.3 | 96.8 | 97.1 | 97 | 96.7 | 96.8 | ABB7.6UNO-7.6-TL-OUTD-S-US-Z-M-A [208V] | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-M-A [240V] | Y | Y | Y | 7.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 240 | 97 | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.4 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.1 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 95.4 | 97.1 | 97.5 | 97.7 | 97.6 | 97.4 | 97.5 | 93.9 | 96.5 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | ABB7.6UNO-7.6-TL-OUTD-S-US-Z-M-A [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-7.6-TL-OUTD-S-US-Z-M-A [277V] | Y | Y | Y | 7.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 7.6 | 277 | 97 | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.5 |  |  | 200 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.1 | 95.3 | 96.1 | 96.6 | 96.6 | 96.4 | 96.3 | 93.9 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 94.2 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | ABB7.6UNO-7.6-TL-OUTD-S-US-Z-M-A [277V] | 2017-07-01 | 2018-10-15
ABB | UNO-8.6-TL-OUTD-S-US-A [240V] | Y | Y | Y | 8.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 8.6 | 240 | 97 | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.4 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93.7 | 95.9 | 96.4 | 96.6 | 96.4 | 96.2 | 96.3 | 95.7 | 97.3 | 97.6 | 97.7 | 97.6 | 97.4 | 97.5 | 94.5 | 96.7 | 97.2 | 97.4 | 97.4 | 97.2 | 97.2 | ABB8.6UNO-8.6-TL-OUTD-S-US-A [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-8.6-TL-OUTD-S-US-A [277V] | Y | Y | Y | 8.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 8.6 | 277 | 97 | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.5 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.8 | 95.6 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 94.5 | 96.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97.2 | 94.8 | 96.9 | 97.5 | 97.8 | 97.7 | 97.6 | 97.5 | ABB8.6UNO-8.6-TL-OUTD-S-US-A [277V] | 2017-07-01 | 2018-10-15
ABB | UNO-8.6-TL-OUTD-S-US-Z-A [240V] | Y | Y | Y | 8.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 8.6 | 240 | 97 | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.4 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93.7 | 95.9 | 96.4 | 96.6 | 96.4 | 96.2 | 96.3 | 95.7 | 97.3 | 97.6 | 97.7 | 97.6 | 97.4 | 97.5 | 94.5 | 96.7 | 97.2 | 97.4 | 97.4 | 97.2 | 97.2 | ABB8.6UNO-8.6-TL-OUTD-S-US-Z-A [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-8.6-TL-OUTD-S-US-Z-A [277V] | Y | Y | Y | 8.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 8.6 | 277 | 97 | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.5 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.8 | 95.6 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 94.5 | 96.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97.2 | 94.8 | 96.9 | 97.5 | 97.8 | 97.7 | 97.6 | 97.5 | ABB8.6UNO-8.6-TL-OUTD-S-US-Z-A [277V] | 2017-07-01 | 2018-10-15
ABB | UNO-8.6-TL-OUTD-S-US-Z-M [240V] | Y | N | N | 8.6 kW, 240 Vac transformerless Utility Interactive Inverter with arc detector | 8.6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.4 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93.7 | 95.9 | 96.4 | 96.6 | 96.4 | 96.2 | 96.3 | 95.7 | 97.3 | 97.6 | 97.7 | 97.6 | 97.4 | 97.5 | 94.5 | 96.7 | 97.2 | 97.4 | 97.4 | 97.2 | 97.2 | ABB8.6UNO-8.6-TL-OUTD-S-US-Z-M [240V]
ABB | UNO-8.6-TL-OUTD-S-US-Z-M [277V] | Y | N | N | 8.6 kW, 277 Vac transformerless Utility Interactive Inverter with arc detector | 8.6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.5 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.8 | 95.6 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 94.5 | 96.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97.2 | 94.8 | 96.9 | 97.5 | 97.8 | 97.7 | 97.6 | 97.5 | ABB8.6UNO-8.6-TL-OUTD-S-US-Z-M [277V]
ABB | UNO-8.6-TL-OUTD-S-US-Z-M-A [240V] | Y | Y | Y | 8.6 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 8.6 | 240 | 97 | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.4 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93.7 | 95.9 | 96.4 | 96.6 | 96.4 | 96.2 | 96.3 | 95.7 | 97.3 | 97.6 | 97.7 | 97.6 | 97.4 | 97.5 | 94.5 | 96.7 | 97.2 | 97.4 | 97.4 | 97.2 | 97.2 | ABB8.6UNO-8.6-TL-OUTD-S-US-Z-M-A [240V] | 2017-07-01 | 2018-10-15
ABB | UNO-8.6-TL-OUTD-S-US-Z-M-A [277V] | Y | Y | Y | 8.6 kW, 277 Vac transformerless Grid Support Utility Interactive Inverter with arc detector | 8.6 | 277 | 97 | [2/7/2017] | [A.0.1.5, B.0.2.3, C.0.2.4, D.0.0.F] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1.5 |  |  | 200 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.8 | 95.6 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | 94.5 | 96.6 | 97.1 | 97.4 | 97.4 | 97.3 | 97.2 | 94.8 | 96.9 | 97.5 | 97.8 | 97.7 | 97.6 | 97.5 | ABB8.6UNO-8.6-TL-OUTD-S-US-Z-M-A [277V] | 2017-07-01 | 2018-10-15
ABB | PVI-10.0-I-OUTD-x-US-208-y [208V] | Y | N | N | 10 kW, 208 Vac Inverter, where x = (blank), S, S1, or S2 and y = PG or NG | 10 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.1 | 10 | 0.1 | 220 | 320 | 416 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.5 | 96.1 | 96.2 | 96.3 | 95.7 | 94.8 | 95.8 | 94.4 | 96.3 | 96.5 | 96.5 | 96.3 | 95.7 | 96.2 | 93.1 | 95.7 | 96.2 | 96.2 | 95.9 | 95.5 | 95.8 | ABB10PVI-10.0-I-OUTD-x-US-208-y [208V]
ABB | PVI-10.0-I-OUTD-x-US-480-y-z [480V] | Y | N | N | 10 kW, 480 Vac Inverter, where x = (blank), S, S1, or S2; y = PG or NG; and z = (blank) or 12A | 10 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.4 | 10 | 0.4 | 220 | 362 | 416 | 1 | 2 | 3 | 5 | 7.5 | 10 | 92.7 | 95.4 | 96.2 | 96.9 | 96.8 | 96.4 | 96.5 | 92.6 | 96 | 96.8 | 97.2 | 97.3 | 97.3 | 97 | 92.3 | 95.9 | 96.8 | 97.3 | 97.3 | 97.3 | 97 | ABB10PVI-10.0-I-OUTD-x-US-480-y-z [480V]
ABB | PVI-12.0-I-OUTD-x-US-480-y [480V] | Y | N | N | 12 kW, 480 Vac Inverter, where x = (blank), S, S1, or S2 and y =PG or NG | 12 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.4 | 12 | 0.4 | 250 | 370 | 416 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 93.7 | 96 | 96.5 | 97 | 96.9 | 96.4 | 96.7 | 93.6 | 96.3 | 97 | 97.2 | 97.3 | 97.2 | 97 | 93.4 | 96.4 | 97 | 97.2 | 97.3 | 97.3 | 97.1 | ABB12PVI-12.0-I-OUTD-x-US-480-y [480V]
ABB | TRIO-20.0-TL-OUTD-S1A-US-480 [480V] | Y | N | N | 20 kW, 480 Vac Inverter | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9 | ABB20TRIO-20.0-TL-OUTD-S1A-US-480 [480V]
ABB | TRIO-20.0-TL-OUTD-S1A-US-480-A [480V] | Y | N | N | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9 | ABB20TRIO-20.0-TL-OUTD-S1A-US-480-A [480V]
ABB | TRIO-20.0-TL-OUTD-S1B-US-480 [480V] | Y | N | N | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9 | ABB20TRIO-20.0-TL-OUTD-S1B-US-480 [480V]
ABB | TRIO-20.0-TL-OUTD-S1B-US-480-A [480V] | Y | N | N | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9 | ABB20TRIO-20.0-TL-OUTD-S1B-US-480-A [480V]
ABB | TRIO-20.0-TL-OUTD-S1-US-480 [480V] | Y | N | N | 20 kW, 480 Vac Inverter | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9 | ABB20TRIO-20.0-TL-OUTD-S1-US-480 [480V]
ABB | TRIO-20.0-TL-OUTD-S1-US-480-A [480V] | Y | N | N | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9 | ABB20TRIO-20.0-TL-OUTD-S1-US-480-A [480V]
ABB | TRIO-20.0-TL-OUTD-S-US-480 [480V] | Y | N | N | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9 | ABB20TRIO-20.0-TL-OUTD-S-US-480 [480V]
ABB | TRIO-20.0-TL-OUTD-S-US-480-A [480V] | Y | N | N | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9 | ABB20TRIO-20.0-TL-OUTD-S-US-480-A [480V]
ABB | TRIO-27.6-TL-OUTD-S1A-US-480 [480V] | Y | N | N | 27.6 kW, 480 Vac Inverter | 27.6 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1 | ABB27.6TRIO-27.6-TL-OUTD-S1A-US-480 [480V]
ABB | TRIO-27.6-TL-OUTD-S1A-US-480-A [480V] | Y | N | N | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1 | ABB27.6TRIO-27.6-TL-OUTD-S1A-US-480-A [480V]
ABB | TRIO-27.6-TL-OUTD-S1B-US-480 [480V] | Y | N | N | 27.6 kW, 480 Vac Inverter | 27.6 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1 | ABB27.6TRIO-27.6-TL-OUTD-S1B-US-480 [480V]
ABB | TRIO-27.6-TL-OUTD-S1B-US-480-A [480V] | Y | N | N | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1 | ABB27.6TRIO-27.6-TL-OUTD-S1B-US-480-A [480V]
ABB | TRIO-27.6-TL-OUTD-S1-US-480 [480V] | Y | N | N | 27.6 kW, 480 Vac Inverter | 27.6 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1 | ABB27.6TRIO-27.6-TL-OUTD-S1-US-480 [480V]
ABB | TRIO-27.6-TL-OUTD-S1-US-480-A [480V] | Y | N | N | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1 | ABB27.6TRIO-27.6-TL-OUTD-S1-US-480-A [480V]
ABB | TRIO-27.6-TL-OUTD-S-US-480 [480V] | Y | N | N | 27.6 kW, 480 Vac Inverter | 27.6 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1 | ABB27.6TRIO-27.6-TL-OUTD-S-US-480 [480V]
ABB | TRIO-27.6-TL-OUTD-S-US-480-A [480V] | Y | N | N | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1 | ABB27.6TRIO-27.6-TL-OUTD-S-US-480-A [480V]
ABB | PVI-CENTRAL-50-US [208V] | Y | N | N | 50 kW, 208 Vac Utility Interactive Inverter | 50 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 33 | 50 | 33 | 330 | 370 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.7 | 94.5 | 95.4 | 95.6 | 95.3 | 94.7 | 95.1 | 90.4 | 94.4 | 95.3 | 95.6 | 95.2 | 94.6 | 95 | 89.7 | 94 | 94.8 | 95.2 | 94.9 | 94.4 | 94.7 | ABB50PVI-CENTRAL-50-US [208V]
ABB | PVI-CENTRAL-50-US [480V] | Y | N | N | 50 kW, 480 Vac Utility Interactive Inverter | 50 | 480 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 41 | 50 | 41 | 330 | 370 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.5 | 94.4 | 95.3 | 95.7 | 95.6 | 95.1 | 95.3 | 90.2 | 94.2 | 95.2 | 95.6 | 95.5 | 95 | 95.2 | 89.5 | 93.8 | 94.9 | 95.3 | 95.3 | 94.8 | 94.9 | ABB50PVI-CENTRAL-50-US [480V]
ABB | TRIO-50.0-TL-OUTD-US-480 [480V] | Y | Y | Y | 50 kW, 480 Vac Grid Support Utility Interactive Inverter with arc detector | 50 | 480 | 98 | [1/27/2017] | [A.0.9.A, B.1.E.1, C.1.8.8] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 1 | 50 | 1 | 520 | 720 | 800 | 5 | 10 | 15 | 25 | 37.5 | 50 | 96.3426 | 97.3941 | 97.7305 | 97.8494 | 97.8642 | 97.7358 | 97.8 | 96.859 | 98.0033 | 98.3351 | 98.526 | 98.5515 | 98.4933 | 98.4222 | 95.9226 | 97.5683 | 98.0341 | 98.3179 | 98.3432 | 98.3043 | 98.1633 | ABB50TRIO-50.0-TL-OUTD-US-480 [480V] | 2017-07-01 | 2018-10-15
ABB | TRIO-60.0-TL-OUTD-US-480 [480V] | Y | Y | Y | 60 kW, 480 Vac Grid Support Utility Interactive Inverter with arc detector | 60 | 480 | 98 | [1/27/2017] | [A.0.9.A, B.1.E.1, C.1.8.8] | 2018-10-15 | Y | N | Multiple Listing of Power-One | 0.8 | 60 | 0.8 | 570 | 720 | 800 | 6 | 12 | 18 | 30 | 45 | 60 | 96.7 | 97.7 | 97.9 | 98 | 98 | 97.8 | 97.9 | 97.2 | 98.1 | 98.4 | 98.5 | 98.5 | 98.4 | 98.4 | 96.4 | 97.8 | 98.1 | 98.3 | 98.3 | 98.2 | 98.2 | ABB60TRIO-60.0-TL-OUTD-US-480 [480V] | 2017-07-01 | 2018-10-15
ABB | TRIO-TM-60.0-US-480 [480V] | N | Y | Y | 60 kVA, 480 Vac Grid Support Utility Interactive Inverter with arc detector | 60 | 480 | 98 | [04/12/2018] | [A.0.2.7, B.0.2.9, C.0.5.1] | 2018-10-15 | Y | N |  | 0.6 |  |  | 570 | 720 | 800 | 6 | 12 | 18 | 30 | 45 | 60 | 96.7 | 97.6 | 97.8 | 97.9 | 97.8 | 97.6 | 97.8 | 97.3 | 98.3 | 98.5 | 98.6 | 98.6 | 98.4 | 98.5 | 96.7 | 98 | 98.3 | 98.4 | 98.4 | 98.3 | 98.3 | ABB60TRIO-TM-60.0-US-480 [480V] | 2018-06-01 | 2018-10-15
ABB | PVI-CENTRAL-100-US [208V] | Y | N | N | 100 kW, 208 Vac Utility Interactive Inverter | 100 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 47 | 100 | 47 | 330 | 370 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.5 | 94.7 | 95.4 | 95.6 | 95.3 | 94.7 | 95.2 | 91.2 | 94.5 | 95.3 | 95.5 | 95.2 | 94.6 | 95.1 | 90.3 | 94.1 | 94.9 | 95.2 | 95 | 94.4 | 94.7 | ABB100PVI-CENTRAL-100-US [208V]
ABB | PVI-CENTRAL-100-US [480V] | Y | N | N | 100 kW, 480 Vac Utility Interactive Inverter | 100 | 480 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 50 | 100 | 50 | 330 | 370 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.5 | 94.8 | 95.5 | 95.7 | 95.5 | 94.7 | 95.3 | 91.2 | 94.6 | 95.3 | 95.6 | 95.4 | 94.6 | 95.2 | 90.3 | 94.2 | 95 | 95.3 | 95.1 | 94.4 | 94.8 | ABB100PVI-CENTRAL-100-US [480V]
ABB | PVI-CENTRAL-250-US [480V] | Y | N | N | 250 kW, 480 Vac Utility Interactive Inverter | 250 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 105.3 | 250 | 105.3 | 320 | 360 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 95.7 | 97.5 | 97.5 | 97.6 | 97 | 96.6 | 97.1 | 95.4 | 97.2 | 97.3 | 97.4 | 96.8 | 96.5 | 96.9 | 94.1 | 96 | 96.3 | 96.7 | 96.5 | 96 | 96.3 | ABB250PVI-CENTRAL-250-US [480V]
ABB | PVI-CENTRAL-300-US [480V] | Y | N | N | 300 kW, 480 Vac Utility Interactive Inverter | 300 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 119 | 300 | 119 | 320 | 360 | 480 | 30 | 60 | 90 | 150 | 225 | 300 | 96.2 | 97.5 | 97.6 | 97.6 | 97.1 | 96.5 | 97.2 | 95.8 | 97.3 | 97.4 | 97.4 | 96.9 | 96.4 | 97 | 94.8 | 96.2 | 96.3 | 96.6 | 96.3 | 95.8 | 96.3 | ABB300PVI-CENTRAL-300-US [480V]
ABB | ULTRA-750-TL-OUTD-2-US-690-x-y-z [690V] | Y | N | N | 750 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 750 | 690 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 301.7 |  |  | 585 | 746 | 800 | 75 | 150 | 225 | 375 | 562.5 | 750 | 94.5 | 95.8 | 96.2 | 96.2 | 95.9 | 95.1 | 95.9 | 95 | 96.5 | 96.7 | 96.9 | 96.5 | 95.9 | 96.5 | 95.1 | 96.6 | 96.9 | 97 | 96.7 | 96.1 | 96.7 | ABB750ULTRA-750-TL-OUTD-2-US-690-x-y-z [690V]
ABB | ULTRA-750-TL-OUTD-4-US-690-x-y-z [690V] | Y | N | N | 750 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 750 | 690 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 346.8 |  |  | 585 | 746 | 800 | 75 | 150 | 225 | 375 | 562.5 | 750 | 94.4 | 96 | 96.4 | 96.5 | 96.1 | 95.4 | 96.1 | 94.9 | 96.5 | 96.8 | 97.1 | 96.8 | 96.2 | 96.7 | 95 | 96.6 | 96.9 | 97.1 | 96.9 | 96.4 | 96.8 | ABB750ULTRA-750-TL-OUTD-4-US-690-x-y-z [690V]
ABB | ULTRA-750-TL-OUTD-1-US-690-x-y-z [690V] | Y | N | N | 750 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 780 | 690 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 302 |  |  | 585 | 746 | 800 | 78 | 156 | 234 | 390 | 585 | 780 | 94.4 | 95.8 | 96.1 | 96.2 | 95.8 | 95.1 | 95.8 | 94.9 | 96.4 | 96.7 | 96.9 | 96.5 | 96 | 96.5 | 95.1 | 96.6 | 96.9 | 97 | 96.7 | 96.2 | 96.7 | ABB780ULTRA-750-TL-OUTD-1-US-690-x-y-z [690V]
ABB | ULTRA-750-TL-OUTD-3-US-690-x-y-z [690V] | Y | N | N | 750 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 780 | 690 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 346.8 |  |  | 585 | 746 | 800 | 78 | 156 | 234 | 390 | 585 | 780 | 94.5 | 96 | 96.4 | 96.4 | 96 | 95.3 | 96.1 | 95 | 96.5 | 97 | 97.1 | 96.8 | 96.2 | 96.7 | 95.1 | 96.6 | 97.1 | 97.2 | 96.9 | 96.3 | 96.9 | ABB780ULTRA-750-TL-OUTD-3-US-690-x-y-z [690V]
ABB | ULTRA-1100-TL-OUTD-2-US-690-x-y-z [690V] | Y | N | N | 1100 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1000 | 690 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 328.8 |  |  | 585 | 746 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.5 | 96.1 | 96.5 | 96.5 | 96.2 | 95.4 | 96.2 | 94.9 | 96.7 | 97.1 | 97.1 | 96.8 | 96.2 | 96.8 | 95.1 | 96.9 | 97.2 | 97.3 | 96.9 | 96.4 | 96.9 | ABB1000ULTRA-1100-TL-OUTD-2-US-690-x-y-z [690V]
ABB | ULTRA-1100-TL-OUTD-4-US-690-x-y-z [690V] | Y | N | N | 1100 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1000 | 690 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 381.6 |  |  | 585 | 746 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.5 | 96.2 | 96.6 | 96.8 | 96.4 | 95.8 | 96.4 | 95 | 96.8 | 97.2 | 97.3 | 97 | 96.5 | 97 | 95.1 | 96.9 | 97.4 | 97.4 | 97.1 | 96.6 | 97.1 | ABB1000ULTRA-1100-TL-OUTD-4-US-690-x-y-z [690V]
ABB | ULTRA-1100-TL-OUTD-1-US-690-x-y-z [690V] | Y | N | N | 1100 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1154 | 690 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 329 |  |  | 585 | 746 | 800 | 117 | 234 | 351 | 585 | 877.5 | 1170 | 94.4 | 96 | 96.4 | 96.5 | 96.1 | 95.4 | 96.1 | 95 | 96.6 | 97 | 97.1 | 96.8 | 96.2 | 96.8 | 95.1 | 96.8 | 97.2 | 97.3 | 97 | 96.4 | 97 | ABB1154ULTRA-1100-TL-OUTD-1-US-690-x-y-z [690V]
ABB | ULTRA-1100-TL-OUTD-3-US-690-x-y-z [690V] | Y | N | N | 1100 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1170 | 690 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 381.6 |  |  | 585 | 746 | 800 | 117 | 234 | 351 | 585 | 877.5 | 1170 | 94.6 | 96.3 | 96.6 | 96.7 | 96.3 | 95.6 | 96.3 | 95.2 | 96.8 | 97.3 | 97.3 | 96.9 | 96.3 | 96.9 | 95.3 | 96.9 | 97.4 | 97.4 | 97 | 96.5 | 97 | ABB1170ULTRA-1100-TL-OUTD-3-US-690-x-y-z [690V]
ABB | ULTRA-1500-TL-OUTD-2-US-690-x-y-z [690V] | Y | N | N | 1500 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1500 | 690 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 373.9 |  |  | 585 | 746 | 800 | 150 | 300 | 450 | 750 | 1125 | 1500 | 94.9 | 96.3 | 96.5 | 96.7 | 96.3 | 95.6 | 96.3 | 95.3 | 96.8 | 97 | 97.2 | 96.9 | 96.3 | 96.9 | 95.4 | 96.9 | 97.2 | 97.4 | 97 | 96.5 | 97 | ABB1500ULTRA-1500-TL-OUTD-2-US-690-x-y-z [690V]
ABB | ULTRA-1500-TL-OUTD-4-US-690-x-y-z [690V] | Y | N | N | 1500 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1500 | 690 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 430.1 |  |  | 585 | 746 | 800 | 150 | 300 | 450 | 750 | 1125 | 1500 | 94.9 | 96.5 | 96.8 | 97 | 96.5 | 95.8 | 96.5 | 95.4 | 97 | 97.3 | 97.5 | 97.1 | 96.6 | 97.1 | 95.5 | 97.1 | 97.4 | 97.6 | 97.3 | 96.7 | 97.2 | ABB1500ULTRA-1500-TL-OUTD-4-US-690-x-y-z [690V]
ABB | ULTRA-1500-TL-OUTD-1-US-690-x-y-z [690V] | Y | N | N | 1500 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1550 | 690 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 374 |  |  | 585 | 746 | 800 | 156 | 312 | 468 | 780 | 1170 | 1560 | 94.9 | 96.3 | 96.5 | 96.8 | 96.2 | 95.4 | 96.2 | 95.3 | 96.8 | 97.1 | 97.2 | 96.9 | 96.3 | 96.9 | 95.5 | 97 | 97.2 | 97.4 | 97.1 | 96.5 | 97 | ABB1550ULTRA-1500-TL-OUTD-1-US-690-x-y-z [690V]
ABB | ULTRA-1500-TL-OUTD-3-US-690-x-y-z [690V] | Y | N | N | 1500 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1560 | 690 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of Power-One | 430.1 |  |  | 585 | 746 | 800 | 156 | 312 | 468 | 780 | 1170 | 1560 | 94.9 | 96.5 | 96.8 | 97 | 96.4 | 95.7 | 96.5 | 95.4 | 97 | 97.3 | 97.5 | 97.1 | 96.6 | 97.1 | 95.5 | 97.1 | 97.4 | 97.6 | 97.2 | 96.7 | 97.2 | ABB1560ULTRA-1500-TL-OUTD-3-US-690-x-y-z [690V]
ABB | PVS980-58-1818kVA-I [600V] | Y | N | N | 1827 kW Utility Interactive Inverter | 1827.3 | 600 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Weighted efficiency includes transformer efficiency of ABB JC04770. | 231.8 |  |  | 850 | 975 | 1100 | 182.73 | 365.46 | 548.19 | 913.65 | 1370.48 | 1827.3 | 96.15 | 97.62 | 97.94 | 97.98 | 97.74 | 97.35 | 97.72 | 95.5 | 97.18 | 97.56 | 97.64 | 97.39 | 97 | 97.36 | 95.16 | 97.03 | 97.44 | 97.54 | 97.3 | 96.93 | 97.25 | ABB1827.3PVS980-58-1818kVA-I [600V] |  | 2018-05-01
ABB | PVS980-58-2000kVA-K [660V] | Y | N | N | 2000 kW Utility Interactive Inverter | 2027.06 | 660 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Weighted efficiency includes transformer efficiency of ABB JC04770. | 230.9 |  |  | 935 | 1018 | 1100 | 202.71 | 405.41 | 608.12 | 1013.53 | 1520.3 | 2027.06 | 96.11 | 97.63 | 97.98 | 98.06 | 97.83 | 97.44 | 97.8 | 95.51 | 97.23 | 97.64 | 97.74 | 97.51 | 97.14 | 97.46 | 95.41 | 97.16 | 97.57 | 97.66 | 97.46 | 97.07 | 97.4 | ABB2027.06PVS980-58-2000kVA-K [660V] |  | 2018-05-01
Ablerex Electronics | ES 2200-US-240 [240V] | Y | N | N | 2110 W, 240 Vac Utility Interactive Inverter | 2.11 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.21 | 0.42 | 0.63 | 1.06 | 1.58 | 2.11 | 85.3 | 91.6 | 92.9 | 94.3 | 94.6 | 94.5 | 93.8 | 82.1 | 91.9 | 94.2 | 95.6 | 96.1 | 96.4 | 95 | 82.2 | 91.5 | 93.8 | 95.6 | 96.1 | 96.3 | 95 | Ablerex Electronics2.11ES 2200-US-240 [240V]
Ablerex Electronics | ES 3300-US-240 [240V] | Y | N | N | 3180 W, 240 Vac Utility Interactive Inverter | 3.18 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.32 | 0.64 | 0.95 | 1.59 | 2.39 | 3.18 | 88.8 | 92.9 | 94.1 | 94.6 | 94.3 | 94 | 94 | 88.8 | 94.4 | 95.3 | 96.2 | 96.3 | 95.9 | 95.7 | 89.5 | 93.7 | 95.3 | 96.2 | 96.3 | 96.1 | 95.7 | Ablerex Electronics3.18ES 3300-US-240 [240V]
Ablerex Electronics | ES 4200-US-240 [240V] | Y | N | N | 4100W, 240 Vac Utility Interactive Inverter | 4.16 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.42 | 0.83 | 1.25 | 2.08 | 3.12 | 4.16 | 90.6 | 93.8 | 94.5 | 94.8 | 94.6 | 94.2 | 94.4 | 91.4 | 95 | 95.7 | 96.1 | 96.2 | 95.9 | 95.9 | 90.7 | 94.7 | 95.5 | 96.1 | 96.1 | 95.9 | 95.7 | Ablerex Electronics4.16ES 4200-US-240 [240V]
Ablerex Electronics | ES 4200-US-240A [240V] | Y | N | N | 4160W, 240 Vac Utility Interactive Inverter | 4.16 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.42 | 0.83 | 1.25 | 2.08 | 3.12 | 4.16 | 90.6 | 93.8 | 94.5 | 94.8 | 94.6 | 94.2 | 94.4 | 91.4 | 95 | 95.7 | 96.1 | 96.2 | 95.9 | 95.9 | 90.7 | 94.7 | 95.5 | 96.1 | 96.1 | 95.9 | 95.7 | Ablerex Electronics4.16ES 4200-US-240A [240V]
Ablerex Electronics | ES 5000-US-240 [240V] | Y | N | N | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8 | Ablerex Electronics5.24ES 5000-US-240 [240V]
Ablerex Electronics | ES 5000-US-240A [240V] | Y | N | N | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8 | Ablerex Electronics5.24ES 5000-US-240A [240V]
Advanced Energy Industries | AE_3TL-12_10 [480V] | Y | N | N | 12 kW, 480 Vac string Inverter | 12 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.47 |  |  | 450 | 720 | 900 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 93.2 | 96 | 96.5 | 97.3 | 97.4 | 97.3 | 97 | 93.9 | 97 | 97 | 97.8 | 98 | 98.1 | 97.6 | 93 | 96.7 | 96.4 | 97.4 | 97.6 | 97.8 | 97.2 | Advanced Energy Industries12AE_3TL-12_10 [480V]
Advanced Energy Industries | AE_3TL-12_10-08 [480V] | Y | N | N | 12 kW, 480 Vac string Inverter | 12 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 450 | 720 | 900 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 93.2 | 96 | 96.5 | 97.3 | 97.4 | 97.3 | 97 | 93.9 | 97 | 97 | 97.8 | 98 | 98.1 | 97.6 | 93 | 96.7 | 96.4 | 97.4 | 97.6 | 97.8 | 97.2 | Advanced Energy Industries12AE_3TL-12_10-08 [480V]
Advanced Energy Industries | AE_3TL-12_6 [480V] | Y | N | N | 12 kW, 480 Vac string Inverter | 12 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.47 |  |  | 450 | 720 | 900 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 93.2 | 96 | 96.5 | 97.3 | 97.4 | 97.3 | 97 | 93.9 | 97 | 97 | 97.8 | 98 | 98.1 | 97.6 | 93 | 96.7 | 96.4 | 97.4 | 97.6 | 97.8 | 97.2 | Advanced Energy Industries12AE_3TL-12_6 [480V]
Advanced Energy Industries | AE_3TL-G3_12_10 [480V] | Y | N | N | 12 kW, 480 Vac string Inverter | 12 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.47 |  |  | 450 | 720 | 900 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 93.2 | 96 | 96.5 | 97.3 | 97.4 | 97.3 | 97 | 93.9 | 97 | 97 | 97.8 | 98 | 98.1 | 97.6 | 93 | 96.7 | 96.4 | 97.4 | 97.6 | 97.8 | 97.2 | Advanced Energy Industries12AE_3TL-G3_12_10 [480V]
Advanced Energy Industries | AE_3TL-G3_12_10-8 [480V] | Y | N | N | 12 kW, 480 Vac string Inverter | 12 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.47 |  |  | 450 | 720 | 900 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 93.2 | 96 | 96.5 | 97.3 | 97.4 | 97.3 | 97 | 93.9 | 97 | 97 | 97.8 | 98 | 98.1 | 97.6 | 93 | 96.7 | 96.4 | 97.4 | 97.6 | 97.8 | 97.2 | Advanced Energy Industries12AE_3TL-G3_12_10-8 [480V]
Advanced Energy Industries | 804R012 [480V] | Y | N | N | 12 kW, 480 Vac, 3-phase Utility Interactive Inverter | 12.12 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.87 |  |  | 450 | 720 | 900 | 1.21 | 2.42 | 3.64 | 6.06 | 9.09 | 12.12 | 94.9 | 96.1 | 96.9 | 97.4 | 97.5 | 97.3 | 97.2 | 96 | 96.5 | 97.4 | 97.9 | 98.1 | 98.1 | 97.8 | 95.2 | 95.9 | 96.8 | 97.4 | 97.6 | 97.7 | 97.3 | Advanced Energy Industries12.12804R012 [480V]
Advanced Energy Industries | AE_3TL-12_6-08 [480V] | Y | N | N | 12 kW, 480 Vac string Inverter | 12.12 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.87 |  |  | 450 | 720 | 900 | 1.21 | 2.42 | 3.64 | 6.06 | 9.09 | 12.12 | 94.9 | 96.1 | 96.9 | 97.4 | 97.5 | 97.3 | 97.2 | 96 | 96.5 | 97.4 | 97.9 | 98.1 | 98.1 | 97.8 | 95.2 | 95.9 | 96.8 | 97.4 | 97.6 | 97.7 | 97.3 | Advanced Energy Industries12.12AE_3TL-12_6-08 [480V]
Advanced Energy Industries | AE_3TL-G3_12_6 [480V] | Y | N | N | 12 kW, 480 Vac string Inverter | 12.12 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.87 |  |  | 450 | 720 | 900 | 1.21 | 2.42 | 3.64 | 6.06 | 9.09 | 12.12 | 94.9 | 96.1 | 96.9 | 97.4 | 97.5 | 97.3 | 97.2 | 96 | 96.5 | 97.4 | 97.9 | 98.1 | 98.1 | 97.8 | 95.2 | 95.9 | 96.8 | 97.4 | 97.6 | 97.7 | 97.3 | Advanced Energy Industries12.12AE_3TL-G3_12_6 [480V]
Advanced Energy Industries | AE_3TL-G3_12_6-08 [480V] | Y | N | N | 12 kW, 480 Vac string Inverter | 12.12 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.87 |  |  | 450 | 720 | 900 | 1.21 | 2.42 | 3.64 | 6.06 | 9.09 | 12.12 | 94.9 | 96.1 | 96.9 | 97.4 | 97.5 | 97.3 | 97.2 | 96 | 96.5 | 97.4 | 97.9 | 98.1 | 98.1 | 97.8 | 95.2 | 95.9 | 96.8 | 97.4 | 97.6 | 97.7 | 97.3 | Advanced Energy Industries12.12AE_3TL-G3_12_6-08 [480V]
Advanced Energy Industries | AE_3TL-16_10 [480V] | Y | N | N | 16 kW, 480 Vac string Inverter | 16 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.47 |  |  | 500 | 720 | 900 | 1.6 | 3.2 | 4.8 | 8 | 12 | 16 | 94.9 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 95.3 | 96.7 | 97.5 | 98 | 98 | 98 | 97.8 | 94.7 | 96.1 | 97 | 97.6 | 97.7 | 97.7 | 97.4 | Advanced Energy Industries16AE_3TL-16_10 [480V]
Advanced Energy Industries | AE_3TL-16_10-08 [480V] | Y | N | N | 16 kW, 480 Vac string Inverter | 16 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 500 | 720 | 900 | 1.6 | 3.2 | 4.8 | 8 | 12 | 16 | 94.9 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 95.3 | 96.7 | 97.5 | 98 | 98 | 98 | 97.8 | 94.7 | 96.1 | 97 | 97.6 | 97.7 | 97.7 | 97.4 | Advanced Energy Industries16AE_3TL-16_10-08 [480V]
Advanced Energy Industries | AE_3TL-16_6 [480V] | Y | N | N | 16 kW, 480 Vac string Inverter | 16 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.47 |  |  | 500 | 720 | 900 | 1.6 | 3.2 | 4.8 | 8 | 12 | 16 | 94.9 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 95.3 | 96.7 | 97.5 | 98 | 98 | 98 | 97.8 | 94.7 | 96.1 | 97 | 97.6 | 97.7 | 97.7 | 97.4 | Advanced Energy Industries16AE_3TL-16_6 [480V]
Advanced Energy Industries | AE_3TL-G3_16_10 [480V] | Y | N | N | 16 kW, 480 Vac string Inverter | 16 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.47 |  |  | 500 | 720 | 900 | 1.6 | 3.2 | 4.8 | 8 | 12 | 16 | 94.9 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 95.3 | 96.7 | 97.5 | 98 | 98 | 98 | 97.8 | 94.7 | 96.1 | 97 | 97.6 | 97.7 | 97.7 | 97.4 | Advanced Energy Industries16AE_3TL-G3_16_10 [480V]
Advanced Energy Industries | AE_3TL-G3_16_10-08 [480V] | Y | N | N | 16 kW, 480 Vac string Inverter | 16 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.47 |  |  | 500 | 720 | 900 | 1.6 | 3.2 | 4.8 | 8 | 12 | 16 | 94.9 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 95.3 | 96.7 | 97.5 | 98 | 98 | 98 | 97.8 | 94.7 | 96.1 | 97 | 97.6 | 97.7 | 97.7 | 97.4 | Advanced Energy Industries16AE_3TL-G3_16_10-08 [480V]
Advanced Energy Industries | 804R016 [480V] | Y | N | N | 16 kW, 480 Vac, 3-phase Utility Interactive Inverter | 16.1 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.087 |  |  | 500 | 720 | 900 | 1.61 | 3.22 | 4.83 | 8.05 | 12.08 | 16.1 | 96 | 96.8 | 97.4 | 97.6 | 97.6 | 97.4 | 97.5 | 96.6 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.9 | 95.9 | 96.5 | 97.2 | 97.6 | 97.7 | 97.7 | 97.5 | Advanced Energy Industries16.1804R016 [480V]
Advanced Energy Industries | AE_3TL-16_6-08 [480V] | Y | N | N | 16 kW, 480 Vac string Inverter | 16.1 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.087 |  |  | 500 | 720 | 900 | 1.61 | 3.22 | 4.83 | 8.05 | 12.08 | 16.1 | 96 | 96.8 | 97.4 | 97.6 | 97.6 | 97.4 | 97.5 | 96.6 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.9 | 95.9 | 96.5 | 97.2 | 97.6 | 97.7 | 97.7 | 97.5 | Advanced Energy Industries16.1AE_3TL-16_6-08 [480V]
Advanced Energy Industries | AE_3TL-G3_16_6 [480V] | Y | N | N | 16 kW, 480 Vac string Inverter | 16.1 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.09 |  |  | 500 | 720 | 900 | 1.61 | 3.22 | 4.83 | 8.05 | 12.08 | 16.1 | 96 | 96.8 | 97.4 | 97.6 | 97.6 | 97.4 | 97.5 | 96.6 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.9 | 95.9 | 96.5 | 97.2 | 97.6 | 97.7 | 97.7 | 97.5 | Advanced Energy Industries16.1AE_3TL-G3_16_6 [480V]
Advanced Energy Industries | AE_3TL-G3_16_6-08 [480V] | Y | N | N | 16 kW, 480 Vac string Inverter | 16.1 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.09 |  |  | 500 | 720 | 900 | 1.61 | 3.22 | 4.83 | 8.05 | 12.08 | 16.1 | 96 | 96.8 | 97.4 | 97.6 | 97.6 | 97.4 | 97.5 | 96.6 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.9 | 95.9 | 96.5 | 97.2 | 97.6 | 97.7 | 97.7 | 97.5 | Advanced Energy Industries16.1AE_3TL-G3_16_6-08 [480V]
Advanced Energy Industries | 804R020 [480V] | Y | N | N | 20 kW, 480 Vac, 3-phase Utility Interactive Inverter | 19.65 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.087 |  |  | 550 | 720 | 900 | 1.97 | 3.93 | 5.9 | 9.83 | 14.74 | 19.65 | 96.5 | 97.3 | 97.7 | 97.8 | 97.7 | 97.5 | 97.6 | 96.7 | 97.5 | 97.9 | 98.1 | 98.1 | 98 | 98 | 96 | 96.6 | 97.2 | 97.6 | 97.6 | 97.5 | 97.4 | Advanced Energy Industries19.65804R020 [480V]
Advanced Energy Industries | AE_3TL-20_6-08 [480V] | Y | N | N | 20 kW, 480 Vac string Inverter | 19.65 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.087 |  |  | 550 | 720 | 900 | 1.97 | 3.93 | 5.9 | 9.83 | 14.74 | 19.65 | 96.5 | 97.3 | 97.7 | 97.8 | 97.7 | 97.5 | 97.6 | 96.7 | 97.5 | 97.9 | 98.1 | 98.1 | 98 | 98 | 96 | 96.6 | 97.2 | 97.6 | 97.6 | 97.5 | 97.4 | Advanced Energy Industries19.65AE_3TL-20_6-08 [480V]
Advanced Energy Industries | AE_3TL-G3_20_6 [480V] | Y | N | N | 20 kW, 480 Vac string Inverter | 19.65 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.09 |  |  | 550 | 720 | 900 | 1.97 | 3.93 | 5.9 | 9.83 | 14.74 | 19.65 | 96.5 | 97.3 | 97.7 | 97.8 | 97.7 | 97.5 | 97.6 | 96.7 | 97.5 | 97.9 | 98.1 | 98.1 | 98 | 98 | 96 | 96.6 | 97.2 | 97.6 | 97.6 | 97.5 | 97.4 | Advanced Energy Industries19.65AE_3TL-G3_20_6 [480V]
Advanced Energy Industries | AE_3TL-G3_20_6-08 [480V] | Y | N | N | 20 kW, 480 Vac string Inverter | 19.65 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.09 |  |  | 550 | 720 | 900 | 1.97 | 3.93 | 5.9 | 9.83 | 14.74 | 19.65 | 96.5 | 97.3 | 97.7 | 97.8 | 97.7 | 97.5 | 97.6 | 96.7 | 97.5 | 97.9 | 98.1 | 98.1 | 98 | 98 | 96 | 96.6 | 97.2 | 97.6 | 97.6 | 97.5 | 97.4 | Advanced Energy Industries19.65AE_3TL-G3_20_6-08 [480V]
Advanced Energy Industries | AE_3TL-20_10 [480V] | Y | N | N | 20 kW, 480 Vac string Inverter | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.47 |  |  | 550 | 720 | 900 | 2 | 4 | 6 | 10 | 15 | 20 | 95.4 | 96.6 | 97.4 | 97.7 | 97.7 | 97.5 | 97.5 | 95.9 | 96.8 | 97.7 | 98 | 98.1 | 98 | 97.9 | 94.8 | 96.2 | 97.1 | 97.6 | 97.7 | 97.6 | 97.4 | Advanced Energy Industries20AE_3TL-20_10 [480V]
Advanced Energy Industries | AE_3TL-20_10-08 [480V] | Y | N | N | 20 kW, 480 Vac string Inverter | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 550 | 720 | 900 | 2 | 4 | 6 | 10 | 15 | 20 | 95.4 | 96.6 | 97.4 | 97.7 | 97.7 | 97.5 | 97.5 | 95.9 | 96.8 | 97.7 | 98 | 98.1 | 98 | 97.9 | 94.8 | 96.2 | 97.1 | 97.6 | 97.7 | 97.6 | 97.4 | Advanced Energy Industries20AE_3TL-20_10-08 [480V]
Advanced Energy Industries | AE_3TL-20_6 [480V] | Y | N | N | 20 kW, 480 Vac string Inverter | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.47 |  |  | 550 | 720 | 900 | 2 | 4 | 6 | 10 | 15 | 20 | 95.4 | 96.6 | 97.4 | 97.7 | 97.7 | 97.5 | 97.5 | 95.9 | 96.8 | 97.7 | 98 | 98.1 | 98 | 97.9 | 94.8 | 96.2 | 97.1 | 97.6 | 97.7 | 97.6 | 97.4 | Advanced Energy Industries20AE_3TL-20_6 [480V]
Advanced Energy Industries | AE_3TL-G3_20_10 [480V] | Y | N | N | 20 kW, 480 Vac string Inverter | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.47 |  |  | 550 | 720 | 900 | 2 | 4 | 6 | 10 | 15 | 20 | 95.4 | 96.6 | 97.4 | 97.7 | 97.7 | 97.5 | 97.5 | 95.9 | 96.8 | 97.7 | 98 | 98.1 | 98 | 97.9 | 94.8 | 96.2 | 97.1 | 97.6 | 97.7 | 97.6 | 97.4 | Advanced Energy Industries20AE_3TL-G3_20_10 [480V]
Advanced Energy Industries | AE_3TL-G3_20_10-08 [480V] | Y | N | N | 20 kW, 480 Vac string Inverter | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.47 |  |  | 550 | 720 | 900 | 2 | 4 | 6 | 10 | 15 | 20 | 95.4 | 96.6 | 97.4 | 97.7 | 97.7 | 97.5 | 97.5 | 95.9 | 96.8 | 97.7 | 98 | 98.1 | 98 | 97.9 | 94.8 | 96.2 | 97.1 | 97.6 | 97.7 | 97.6 | 97.4 | Advanced Energy Industries20AE_3TL-G3_20_10-08 [480V]
Advanced Energy Industries | AE_3TL-23_10 [480V] | Y | N | N | 23 kW, 480 Vac string Inverter | 20.04 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.47 |  |  | 600 | 720 | 900 | 2 | 4 | 6 | 10 | 15 | 20 | 96.6 | 97.4 | 97.8 | 98 | 97.9 | 97.6 | 97.8 | 96.9 | 97.5 | 97.9 | 98.1 | 98 | 97.9 | 98 | 96.3 | 97 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | Advanced Energy Industries20.04AE_3TL-23_10 [480V]
Advanced Energy Industries | AE_3TL-23_10-08 [480V] | Y | N | N | 23 kW, 480 Vac string Inverter | 20.04 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 600 | 720 | 900 | 2 | 4.01 | 6.01 | 10.02 | 15.03 | 20.04 | 96.6 | 97.4 | 97.8 | 98 | 97.9 | 97.6 | 97.8 | 96.9 | 97.5 | 97.9 | 98.1 | 98 | 97.9 | 98 | 96.3 | 97 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | Advanced Energy Industries20.04AE_3TL-23_10-08 [480V]
Advanced Energy Industries | 804R024 [480V] | Y | N | N | 22.2 kW, 480 Vac, 3-phase Utility Interactive Inverter | 22.23 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.49 |  |  | 600 | 720 | 900 | 2.22 | 4.45 | 6.67 | 11.12 | 16.67 | 22.23 | 97.2 | 97.7 | 97.9 | 97.9 | 97.8 | 97.6 | 97.8 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.8 | 98 | 96.7 | 97.1 | 97.5 | 97.7 | 97.6 | 97.5 | 97.6 | Advanced Energy Industries22.23804R024 [480V]
Advanced Energy Industries | AE_3TL-23_06 [480V] | Y | N | N | 23 kW, 480 Vac string Inverter | 22.23 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.49 |  |  | 600 | 720 | 900 | 2.2 | 4.4 | 6.7 | 11.1 | 16.7 | 22.2 | 97.2 | 97.7 | 97.9 | 97.9 | 97.8 | 97.6 | 97.8 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.8 | 98 | 96.7 | 97.1 | 97.5 | 97.7 | 97.6 | 97.5 | 97.6 | Advanced Energy Industries22.23AE_3TL-23_06 [480V]
Advanced Energy Industries | AE_3TL-23_6-08 [480V] | Y | N | N | 23 kW, 480 Vac string Inverter | 22.23 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.49 |  |  | 600 | 720 | 900 | 2.22 | 4.45 | 6.67 | 11.12 | 16.67 | 22.23 | 97.2 | 97.7 | 97.9 | 97.9 | 97.8 | 97.6 | 97.8 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.8 | 98 | 96.7 | 97.1 | 97.5 | 97.7 | 97.6 | 97.5 | 97.6 | Advanced Energy Industries22.23AE_3TL-23_6-08 [480V]
Advanced Energy Industries | AE 35TX-208 [208V] | Y | N | N | 35 kW, 208 Vac, 3-Phase Utility Interactive Inverter | 35 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 38.63 |  |  | 295 | 341 | 480 | 3.5 | 7 | 10.5 | 17.5 | 26.25 | 35 | 93.3 | 95.6 | 96.2 | 96.2 | 95.8 | 95.3 | 95.8 | 92.6 | 95.3 | 95.9 | 95.9 | 95.6 | 95.1 | 95.5 | 90.5 | 94.1 | 94.9 | 95.1 | 94.9 | 94.5 | 94.7 | Advanced Energy Industries35AE 35TX-208 [208V]
Advanced Energy Industries | AE 35TX-480 [480V] | Y | N | N | 35 kW, 480 Vac, 3-Phase Utility Interactive Inverter | 35 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 37.79 |  |  | 295 | 341 | 480 | 3.5 | 7 | 10.5 | 17.5 | 26.25 | 35 | 94.1 | 96.4 | 96.9 | 97 | 96.8 | 96.3 | 96.7 | 93.3 | 95.9 | 96.5 | 96.7 | 96.5 | 96 | 96.4 | 91.1 | 94.7 | 95.4 | 95.7 | 95.6 | 95.2 | 95.3 | Advanced Energy Industries35AE 35TX-480 [480V]
Advanced Energy Industries | AE 35TX-600 [600V] | Y | N | N | 35 kW, 600 Vac, 3-Phase Utility Interactive Inverter | 35 | 600 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 37.27 |  |  | 295 | 341 | 480 | 3.5 | 7 | 10.5 | 17.5 | 26.25 | 35 | 93.6 | 95.9 | 96.3 | 96.4 | 96.1 | 95.7 | 96.1 | 93 | 95.5 | 96 | 96.1 | 96 | 95.6 | 95.8 | 91 | 94.5 | 95.1 | 95.4 | 95.3 | 95 | 95.1 | Advanced Energy Industries35AE 35TX-600 [600V]
Advanced Energy Industries | AE 50TX-208 [208V] | Y | N | N | 50 kW, 208 Vac, 3-Phase Utility Interactive Inverter with 295-600 Vdc input | 50 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 33 |  |  | 295 | 341 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95 | 96.7 | 96.6 | 96.6 | 96 | 95.3 | 96.2 | 94.4 | 96.3 | 96.3 | 96.3 | 95.8 | 95.2 | 95.9 | 92.7 | 95.5 | 95.4 | 95.6 | 95.2 | 94.7 | 95.2 | Advanced Energy Industries50AE 50TX-208 [208V]
Advanced Energy Industries | AE 50TX-480 [480V] | Y | N | N | 50 kW, 480 Vac, 3-Phase Utility Interactive Inverter with 295-600 Vdc input | 50 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 33 |  |  | 295 | 341 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95.7 | 96.8 | 97.2 | 97 | 96.4 | 95.9 | 96.6 | 95.2 | 96.5 | 97 | 96.8 | 96.2 | 95.8 | 96.4 | 93.8 | 95.6 | 96.3 | 96 | 95.6 | 95.3 | 95.7 | Advanced Energy Industries50AE 50TX-480 [480V]
Advanced Energy Industries | AE 50TX-600 [600V] | Y | N | N | 50 kW, 600 Vac, 3-Phase Utility Interactive Inverter | 50 | 600 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 43 |  |  | 295 | 341 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 94.2 | 96.2 | 96.6 | 96.6 | 96.2 | 95.7 | 96.2 | 93.6 | 95.9 | 96.3 | 96.3 | 96 | 95.6 | 95.9 | 91.6 | 94.8 | 95.4 | 95.5 | 95.3 | 95 | 95.1 | Advanced Energy Industries50AE 50TX-600 [600V]
Advanced Energy Industries | AE 75TX-208 [208V] | Y | N | N | 75 kW, 208 Vac, 3-Phase Utility Interactive Inverter with 295-600 Vdc input | 75 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 50 |  |  | 295 | 341 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.7 | 95.6 | 96.1 | 96 | 95.9 | 95.6 | 95.8 | 92 | 95.2 | 95.8 | 95.8 | 95.7 | 95.3 | 95.5 | 89.8 | 93.8 | 94.8 | 94.9 | 95 | 94.6 | 94.6 | Advanced Energy Industries75AE 75TX-208 [208V]
Advanced Energy Industries | AE 75TX-480 [480V] | Y | N | N | 75 kW, 480 Vac, 3-Phase Utility Interactive Inverter with 295-600 Vdc input | 75 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 50 |  |  | 295 | 341 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.7 | 95.6 | 96.2 | 96.6 | 96.4 | 96.1 | 96.2 | 91.9 | 95 | 95.6 | 96.3 | 96.1 | 95.8 | 95.9 | 89.2 | 93.3 | 94.1 | 95.2 | 95.1 | 95 | 94.6 | Advanced Energy Industries75AE 75TX-480 [480V]
Advanced Energy Industries | AE 75TX-600 [600V] | Y | N | N | 75 kW, 600 Vac, 3-Phase Utility Interactive Inverter | 75 | 600 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 105.8 |  |  | 295 | 341 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.3 | 95.5 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | 91.5 | 95.1 | 95.9 | 96.3 | 96.3 | 96.1 | 96 | 89.4 | 93.9 | 95 | 95.5 | 95.7 | 95.6 | 95.3 | Advanced Energy Industries75AE 75TX-600 [600V]
Advanced Energy Industries | AE 100TX-208 [208V] | Y | N | N | 100 kW, 208 Vac, 3-Phase Utility Interactive Inverter with 295-600 Vdc input | 100 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 42 |  |  | 295 | 341 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 94.2 | 96.4 | 96.3 | 96.3 | 95.8 | 95.2 | 95.9 | 93.6 | 96 | 96.1 | 96.1 | 95.7 | 95.1 | 95.7 | 91.7 | 95 | 95.2 | 95.3 | 95.1 | 94.6 | 95 | Advanced Energy Industries100AE 100TX-208 [208V]
Advanced Energy Industries | AE 100TX-480 [480V] | Y | N | N | 100 kW, 480 Vac 3-Phase Utility Interactive Inverter with 295-600 Vdc input | 100 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 36 |  |  | 295 | 341 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 94.4 | 96.6 | 97.1 | 97 | 96.2 | 95.8 | 96.4 | 93.7 | 96.2 | 96.8 | 96.7 | 96 | 95.6 | 96.1 | 91.9 | 95 | 95.9 | 96 | 95.2 | 94.9 | 95.3 | Advanced Energy Industries100AE 100TX-480 [480V]
Advanced Energy Industries | AE 100TX-600 [600V] | Y | N | N | 100 kW, 600 Vac, 3-Phase Utility Interactive Inverter | 100 | 600 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 99.56 |  |  | 295 | 341 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 93.8 | 96.1 | 96.5 | 96.6 | 96.3 | 95.9 | 96.3 | 93.2 | 95.8 | 96.3 | 96.4 | 96.1 | 95.8 | 96.1 | 91.5 | 94.8 | 95.5 | 95.8 | 95.6 | 95.2 | 95.4 | Advanced Energy Industries100AE 100TX-600 [600V]
Advanced Energy Industries | AE 250TX-480 [480V] | Y | N | N | 250 kW, 480 Vac, 3-Phase Utility Interactive Inverter | 249.5 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 54.14 |  |  | 295 | 341 | 480 | 24.95 | 49.9 | 74.85 | 124.8 | 187.1 | 249.5 | 96 | 97 | 96.9 | 96.9 | 96.6 | 96.1 | 96.7 | 95.6 | 96.6 | 96.7 | 96.8 | 96.4 | 96 | 96.5 | 94.7 | 95.8 | 96.2 | 96.2 | 95.9 | 95.4 | 95.9 | Advanced Energy Industries249.5AE 250TX-480 [480V]
Advanced Energy Industries | AE 250TX-600 [600V] | Y | N | N | 250 kW, 600 Vac, 3-Phase Utility Interactive Inverter | 249.5 | 600 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 101 |  |  | 295 | 341 | 480 | 24.95 | 49.9 | 74.85 | 124.8 | 187.1 | 249.5 | 95.2 | 96.8 | 97.1 | 97.1 | 96.8 | 96.4 | 96.8 | 94.8 | 96.5 | 96.8 | 96.9 | 96.6 | 96.3 | 96.6 | 93.4 | 95.6 | 96.1 | 96.2 | 96 | 95.7 | 95.9 | Advanced Energy Industries249.5AE 250TX-600 [600V]
Advanced Energy Industries | AE 250NX (3159200-XXXX) [480V] | Y | N | N | 250 kW, 480 Vac, 3-phase Utility Interactive Inverter | 250 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 60 |  |  | 660 | 740 | 960 | 25 | 50 | 75 | 125 | 187.5 | 250 | 96 | 97.7 | 98.1 | 98.1 | 98 | 97.7 | 97.9 | 95.5 | 97.3 | 97.7 | 97.8 | 97.8 | 97.5 | 97.6 | 92.8 | 95.8 | 96.4 | 96.9 | 96.8 | 96.7 | 96.6 | Advanced Energy Industries250AE 250NX (3159200-XXXX) [480V]
Advanced Energy Industries | Solaron 250 kW (3159200-XXXX) [480V] | Y | N | N | 250 kW, 480 Vac, 3-phase Utility Interactive Inverter | 250 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 60 |  |  | 660 | 740 | 960 | 25 | 50 | 75 | 125 | 187.5 | 250 | 95.98 | 97.75 | 98.11 | 98.11 | 98.02 | 97.75 | 97.94 | 95.47 | 97.33 | 97.74 | 97.82 | 97.76 | 97.55 | 97.65 | 92.81 | 95.79 | 96.4 | 96.91 | 96.81 | 96.66 | 96.56 | Advanced Energy Industries250Solaron 250 kW (3159200-XXXX) [480V]
Advanced Energy Industries | AE 260TX-480 [480V] | Y | N | N | 260 kW, 480 Vac, 3-Phase Utility Interactive Inverter with 295-600 Vdc input | 260 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 67 |  |  | 295 | 341 | 480 | 26 | 52 | 78 | 130 | 195 | 260 | 96 | 97.5 | 97.7 | 97.6 | 97.1 | 96.4 | 97.2 | 95.6 | 97.3 | 97.5 | 97.4 | 97 | 96.4 | 97 | 94.4 | 96.5 | 96.9 | 97 | 96.6 | 96.1 | 96.6 | Advanced Energy Industries260AE 260TX-480 [480V]
Advanced Energy Industries | AE 260TX-480-LV [480V] | Y | N | N | 260 kW, 480 Vac, 3-Phase Utility Interactive Inverter with 265-600 Vdc input | 260 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 67 |  |  | 265 | 319 | 480 | 26 | 52 | 78 | 130 | 195 | 260 | 96.1 | 97.6 | 97.8 | 97.5 | 96.9 | 96 | 97.1 | 95.6 | 97.3 | 97.5 | 97.3 | 96.7 | 95.9 | 96.9 | 94 | 96.2 | 96.7 | 96.8 | 96.2 | 95.5 | 96.3 | Advanced Energy Industries260AE 260TX-480-LV [480V]
Advanced Energy Industries | AE 333NX (3159000-XXXX) [480V] | Y | N | N | 333 kW, 480 Vac, 3-phase Utility Interactive Inverter | 333 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 60 |  |  | 660 | 740 | 960 | 33.3 | 66.6 | 99.9 | 166.5 | 249.8 | 333 | 96.6 | 98 | 98.3 | 98.2 | 98 | 97.5 | 98 | 95.8 | 97.5 | 97.8 | 97.8 | 97.6 | 97.4 | 97.6 | 94.5 | 96.6 | 97 | 97 | 96.7 | 96.3 | 96.7 | Advanced Energy Industries333AE 333NX (3159000-XXXX) [480V]
Advanced Energy Industries | Solaron 333 kW (3159000-XXXX) [480V] | Y | N | N | 333 kW, 480 Vac, 3-phase Utility Interactive Inverter | 333 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 60 |  |  | 660 | 740 | 960 | 33.3 | 66.6 | 99.9 | 166.5 | 249.8 | 333 | 96.59 | 98.03 | 98.28 | 98.23 | 98.01 | 97.48 | 98.01 | 95.8 | 97.52 | 97.84 | 97.85 | 97.62 | 97.36 | 97.6 | 94.47 | 96.6 | 97.01 | 97.01 | 96.73 | 96.3 | 96.7 | Advanced Energy Industries333Solaron 333 kW (3159000-XXXX) [480V]
Advanced Energy Industries | AE 500NX (3159500-XXXX) [480V] | Y | N | N | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 85 |  |  | 660 | 740 | 960 | 50 | 100 | 150 | 250 | 375 | 500 | 98 | 98.5 | 98.5 | 98.3 | 97.8 | 97 | 98 | 97.3 | 98 | 98.1 | 97.9 | 97.6 | 97 | 97.7 | 95.8 | 96.9 | 97 | 96.8 | 96.2 | 95.5 | 96.4 | Advanced Energy Industries500AE 500NX (3159500-XXXX) [480V]
Advanced Energy Industries | AE 500NX-HE (3159502-XXXX) [480V] | Y | N | N | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 88 |  |  | 660 | 740 | 960 | 50 | 100 | 150 | 250 | 375 | 500 | 97.4 | 98.6 | 98.7 | 98.7 | 98.4 | 97.9 | 98.4 | 96.7 | 98 | 98.3 | 98.3 | 98.2 | 97.9 | 98.1 | 94.9 | 96.9 | 97.3 | 97.3 | 97.2 | 96.7 | 97.1 | Advanced Energy Industries500AE 500NX-HE (3159502-XXXX) [480V]
Advanced Energy Industries | AE 500TX-480 [480V] | Y | N | N | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 58 |  |  | 310 | 353 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 96.98 | 97.76 | 97.82 | 97.66 | 97.22 | 96.7 | 97.37 | 96.68 | 97.54 | 97.59 | 97.42 | 97.02 | 96.49 | 97.16 | 95.74 | 96.84 | 96.96 | 96.82 | 96.47 | 95.98 | 96.57 | Advanced Energy Industries500AE 500TX-480 [480V]
Advanced Energy Industries | AE 500TX-600 [600V] | Y | N | N | 500 kW, 600 Vac, 3-phase Utility Interactive Inverter | 500 | 600 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 69.04 |  |  | 310 | 353 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 96.4 | 97.3 | 97.4 | 97.3 | 96.8 | 96.3 | 97 | 96.1 | 97.1 | 97.2 | 97.1 | 96.7 | 96.3 | 96.8 | 95 | 96.5 | 96.7 | 96.7 | 96.4 | 96 | 96.5 | Advanced Energy Industries500AE 500TX-600 [600V]
Advanced Energy Industries | Solaron 500 HE (3159502-XXXX) [480V] | Y | N | N | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 88 |  |  | 660 | 740 | 960 | 50 | 100 | 150 | 250 | 375 | 500 | 97.4 | 98.6 | 98.7 | 98.7 | 98.4 | 97.9 | 98.4 | 96.7 | 98 | 98.3 | 98.3 | 98.2 | 97.9 | 98.1 | 94.9 | 96.9 | 97.3 | 97.3 | 97.2 | 96.7 | 97.1 | Advanced Energy Industries500Solaron 500 HE (3159502-XXXX) [480V]
Advanced Energy Industries | Solaron 500kW (3159500-XXXX) [480V] | Y | N | N | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 85 |  |  | 660 | 740 | 960 | 50 | 100 | 150 | 250 | 375 | 500 | 97.99 | 98.49 | 98.52 | 98.33 | 97.79 | 97.02 | 97.99 | 97.32 | 97.99 | 98.08 | 97.89 | 97.65 | 97.05 | 97.73 | 95.79 | 96.9 | 97 | 96.77 | 96.16 | 95.5 | 96.38 | Advanced Energy Industries500Solaron 500kW (3159500-XXXX) [480V]
Advanced Energy Industries | AE 1000NX (3159700-XXXX) | Y | N | N | Utility Interactive Photovoltaic Inverter | 1000 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 192.8 |  |  | 1100 | 1230 | 1600 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.3 | 96.9 | 97.7 | 98.1 | 98.1 | 98.1 | 97.9 | 95.4 | 97.3 | 97.8 | 98.1 | 98.1 | 98.1 | 97.9 | 94.6 | 96.8 | 97.3 | 97.7 | 97.8 | 97.7 | 97.5 | Advanced Energy Industries1000AE 1000NX (3159700-XXXX)
Advanced Solar Photonics | PV240 [208V] | Y | N | N | 3.7 kW, 208 Vac Utility Interactive Inverter | 3.69 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.21 |  |  | 100 | 360 | 470 | 0.37 | 0.74 | 1.11 | 1.85 | 2.77 | 3.69 | 94.7 | 96.6 | 97.3 | 97.7 | 97.6 | 97.4 | 97.4 | 94.1 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 92.5 | 95.5 | 96.6 | 97.2 | 97.2 | 97.2 | 96.9 | Advanced Solar Photonics3.69PV240 [208V]
Advanced Solar Photonics | PV240 [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 3.98 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.16 |  |  | 100 | 360 | 450 | 0.398 | 0.796 | 1.194 | 1.99 | 2.985 | 3.98 | 92 | 95.13 | 96.3 | 97.03 | 97 | 96.87 | 96.62 | 94.07 | 96.5 | 97.41 | 97.32 | 97.09 | 97.69 | 97.06 | 92.29 | 95.79 | 96.93 | 97.46 | 97.63 | 97.59 | 97.2 | Advanced Solar Photonics3.98PV240 [240V]
Advanced Solar Photonics | PV240 [277V] | Y | N | N | 4 kW, 277 Vac Utility Interactive Inverter | 3.98 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 |  |  | 100 | 360 | 450 | 0.398 | 0.796 | 1.194 | 1.99 | 2.985 | 3.98 | 90.72 | 94.5 | 95.98 | 96.87 | 97.03 | 96.96 | 96.49 | 92.75 | 95.85 | 96.88 | 97.51 | 97.66 | 97.62 | 97.25 | 93.04 | 96.04 | 97.18 | 97.87 | 98.02 | 97.89 | 97.59 | Advanced Solar Photonics3.98PV240 [277V]
Advanced Solar Photonics | PV250 [208V] | Y | N | N | 4.5 kW, 208 Vac Utility Interactive Inverter | 4.47 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 360 | 470 | 0.45 | 0.89 | 1.34 | 2.24 | 3.35 | 4.47 | 94.5 | 96.9 | 97.5 | 97.7 | 97.6 | 97.4 | 97.4 | 94 | 96.6 | 97.2 | 97.5 | 97.5 | 97.3 | 97.2 | 92.6 | 95.4 | 96.3 | 97.1 | 97.2 | 97.1 | 96.8 | Advanced Solar Photonics4.47PV250 [208V]
Advanced Solar Photonics | PV250 [240V] | Y | N | N | 4.8 kW, 240 Vac Utility Interactive Inverter | 4.83 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.12 |  |  | 100 | 360 | 450 | 0.48 | 0.97 | 1.45 | 2.42 | 3.62 | 4.83 | 92.8 | 95.8 | 96.6 | 96.9 | 96.9 | 96.8 | 96.6 | 94.7 | 96.8 | 97.2 | 97.7 | 97.5 | 97.6 | 97.4 | 93.2 | 96.3 | 97 | 97.5 | 97.5 | 97.5 | 97.2 | Advanced Solar Photonics4.83PV250 [240V]
Advanced Solar Photonics | PV250 [277V] | Y | N | N | 4.8 kW, 277 Vac Utility Interactive Inverter | 4.83 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.09 |  |  | 100 | 360 | 450 | 0.48 | 0.97 | 1.45 | 2.42 | 3.62 | 4.83 | 91 | 94.4 | 95.7 | 96.6 | 96.9 | 96.9 | 96.3 | 93.3 | 96.3 | 97 | 97.5 | 97.6 | 97.6 | 97.3 | 94 | 96.7 | 97.3 | 97.8 | 97.9 | 97.9 | 97.6 | Advanced Solar Photonics4.83PV250 [277V]
Advanced Solar Photonics | PV260 [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter | 5.98 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 |  |  | 100 | 360 | 470 | 0.6 | 1.2 | 1.79 | 2.99 | 4.49 | 5.98 | 95.9 | 97.2 | 97.5 | 97.5 | 97.3 | 97 | 97.3 | 94.9 | 96.9 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93 | 96 | 96.6 | 97.1 | 97 | 96.8 | 96.7 | Advanced Solar Photonics5.98PV260 [208V]
Advanced Solar Photonics | PV260 [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 360 | 450 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 91.46 | 94.66 | 95.86 | 96.6 | 96.84 | 96.78 | 96.35 | 93.31 | 96.16 | 96.87 | 97.36 | 97.44 | 97.37 | 97.12 | 94.29 | 96.68 | 97.28 | 97.88 | 97.82 | 97.7 | 97.56 | Advanced Solar Photonics6PV260 [277V]
Advanced Solar Photonics | PV260 [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter | 6.01 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 100 | 360 | 450 | 0.601 | 1.202 | 1.803 | 3.005 | 4.508 | 6.01 | 93.77 | 96.12 | 96.45 | 96.82 | 96.82 | 96.64 | 96.61 | 95.48 | 97.14 | 97.68 | 97.75 | 97.65 | 97.4 | 97.55 | 93.92 | 96.18 | 97.13 | 97.45 | 97.39 | 97.23 | 97.16 | Advanced Solar Photonics6.01PV260 [240V]
Advanced Solar Photonics | PV270 [208V] | Y | N | N | 7 kW, 208 Vac Utility Interactive Inverter | 6.92 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.17 |  |  | 100 | 360 | 450 | 0.692 | 1.384 | 2.076 | 3.46 | 5.19 | 6.92 | 94.26 | 96.15 | 96.67 | 96.79 | 96.7 | 96.41 | 96.58 | 95.45 | 96.96 | 97.46 | 97.64 | 97.5 | 97.26 | 97.4 | 93.99 | 96.24 | 96.92 | 97.31 | 97.31 | 97.18 | 97.07 | Advanced Solar Photonics6.92PV270 [208V]
Advanced Solar Photonics | PV270 [240V] | Y | N | N | 7 kW, 240 Vac Utility Interactive Inverter | 6.95 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.09 |  |  | 100 | 360 | 470 | 0.695 | 1.39 | 2.085 | 3.475 | 5.213 | 6.95 | 96.14 | 97.28 | 97.53 | 97.29 | 96.98 | 96.47 | 97.07 | 95.62 | 97.01 | 97.37 | 97.14 | 96.94 | 96.55 | 96.96 | 93.81 | 95.96 | 96.63 | 96.9 | 96.68 | 96.36 | 96.55 | Advanced Solar Photonics6.95PV270 [240V]
Advanced Solar Photonics | PV270 [277V] | Y | N | N | 7 kW, 277 Vac Utility Interactive Inverter | 7.01 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.02 |  |  | 100 | 360 | 450 | 0.701 | 1.402 | 2.103 | 3.505 | 5.258 | 7.01 | 93.35 | 95.87 | 96.55 | 96.76 | 96.63 | 96.41 | 96.46 | 94.76 | 96.57 | 97.16 | 97.45 | 97.1 | 97.06 | 97.06 | 94.91 | 96.87 | 97.37 | 97.75 | 97.6 | 97.43 | 97.45 | Advanced Solar Photonics7.01PV270 [277V]
AE Solar Energy | AE3.8 [208V] | Y | N | N | 3.7 kW, 208 Vac Utility Interactive Inverter | 3.69 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.21 |  |  | 100 | 360 | 470 | 0.369 | 0.738 | 1.107 | 1.845 | 2.768 | 3.69 | 94.68 | 96.62 | 97.3 | 97.7 | 97.62 | 97.43 | 97.42 | 94.13 | 96.35 | 97.17 | 97.65 | 97.51 | 97.39 | 97.3 | 92.51 | 95.49 | 96.56 | 97.15 | 97.23 | 97.2 | 96.85 | AE Solar Energy3.69AE3.8 [208V]
AE Solar Energy | AE3.8 [240V] | Y | N | N | 3.7 kW, 240 Vac Utility Interactive Inverter | 3.71 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.06 |  |  | 100 | 360 | 450 | 0.371 | 0.742 | 1.113 | 1.855 | 2.783 | 3.71 | 92 | 95.13 | 96.3 | 97.03 | 97 | 96.87 | 96.62 | 94.07 | 96.5 | 97.41 | 97.32 | 97.09 | 97.69 | 97.06 | 92.29 | 95.79 | 96.93 | 97.46 | 97.63 | 97.59 | 97.2 | AE Solar Energy3.71AE3.8 [240V]
AE Solar Energy | AE3.8 [277V] | Y | N | N | 3.7 kW, 277 Vac Utility Interactive Inverter | 3.71 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 360 | 450 | 0.371 | 0.742 | 1.113 | 1.855 | 2.783 | 3.71 | 90.77 | 94.61 | 95.92 | 96.83 | 97.03 | 97.03 | 96.48 | 92.91 | 95.94 | 96.82 | 97.55 | 97.64 | 97.61 | 97.25 | 93.36 | 96.29 | 97.17 | 97.84 | 97.9 | 97.92 | 97.54 | AE Solar Energy3.71AE3.8 [277V]
AE Solar Energy | AE5.0 [208V] | Y | N | N | 4.5 kW, 208 Vac Utility Interactive Inverter | 4.47 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 360 | 470 | 0.447 | 0.894 | 1.341 | 2.235 | 3.353 | 4.47 | 94.53 | 96.91 | 97.46 | 97.74 | 97.58 | 97.38 | 97.44 | 94.04 | 96.55 | 97.17 | 97.49 | 97.47 | 97.3 | 97.25 | 92.64 | 95.42 | 96.3 | 97.15 | 97.17 | 97.06 | 96.78 | AE Solar Energy4.47AE5.0 [208V]
AE Solar Energy | AE5.0 [240V] | Y | N | N | 4.8 kW, 240 Vac Utility Interactive Inverter | 4.83 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.12 |  |  | 100 | 360 | 450 | 0.483 | 0.966 | 1.449 | 2.415 | 3.623 | 4.83 | 92.83 | 95.8 | 96.65 | 96.94 | 96.86 | 96.76 | 96.63 | 94.65 | 96.82 | 97.23 | 97.75 | 97.55 | 97.65 | 97.4 | 93.23 | 96.3 | 97 | 97.53 | 97.53 | 97.47 | 97.23 | AE Solar Energy4.83AE5.0 [240V]
AE Solar Energy | AE5.0 [277V] | Y | N | N | 4.8 kW, 277 Vac Utility Interactive Inverter | 4.83 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.09 |  |  | 100 | 360 | 450 | 0.483 | 0.966 | 1.449 | 2.415 | 3.623 | 4.83 | 90.98 | 94.41 | 95.72 | 96.56 | 96.89 | 96.89 | 96.32 | 93.27 | 96.27 | 97.02 | 97.46 | 97.64 | 97.59 | 97.28 | 94 | 96.65 | 97.32 | 97.8 | 97.9 | 97.9 | 97.59 | AE Solar Energy4.83AE5.0 [277V]
AE Solar Energy | AE6.0 [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter | 5.98 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 |  |  | 100 | 360 | 470 | 0.598 | 1.196 | 1.794 | 2.99 | 4.485 | 5.98 | 95.88 | 97.18 | 97.51 | 97.51 | 97.31 | 96.96 | 97.3 | 94.92 | 96.89 | 97.39 | 97.42 | 97.27 | 96.96 | 97.19 | 93.01 | 95.98 | 96.59 | 97.09 | 96.96 | 96.81 | 96.72 | AE Solar Energy5.98AE6.0 [208V]
AE Solar Energy | AE6.0 [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 360 | 450 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 91.46 | 94.66 | 95.86 | 96.6 | 96.84 | 96.78 | 96.35 | 93.31 | 96.16 | 96.87 | 97.36 | 97.44 | 97.37 | 97.12 | 94.29 | 96.68 | 97.28 | 97.88 | 97.82 | 97.7 | 97.56 | AE Solar Energy6AE6.0 [277V]
AE Solar Energy | AE6.0 [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter | 6.01 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 100 | 360 | 450 | 0.601 | 1.202 | 1.803 | 3.005 | 4.508 | 6.01 | 93.77 | 96.12 | 96.45 | 96.82 | 96.82 | 96.64 | 96.61 | 95.48 | 97.14 | 97.68 | 97.75 | 97.65 | 97.4 | 97.55 | 93.92 | 96.18 | 97.13 | 97.45 | 97.39 | 97.23 | 97.16 | AE Solar Energy6.01AE6.0 [240V]
AE Solar Energy | AE7.0 [208V] | Y | N | N | 7 kW, 208 Vac Utility Interactive Inverter | 6.92 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.17 |  |  | 100 | 360 | 450 | 0.692 | 1.384 | 2.076 | 3.46 | 5.19 | 6.92 | 94.26 | 96.15 | 96.67 | 96.79 | 96.7 | 96.41 | 96.58 | 95.45 | 96.96 | 97.46 | 97.64 | 97.5 | 97.26 | 97.4 | 93.99 | 96.24 | 96.92 | 97.31 | 97.31 | 97.18 | 97.07 | AE Solar Energy6.92AE7.0 [208V]
AE Solar Energy | AE7.0 [240V] | Y | N | N | 7 kW, 240 Vac Utility Interactive Inverter | 6.95 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.09 |  |  | 100 | 360 | 470 | 0.695 | 1.39 | 2.085 | 3.475 | 5.213 | 6.95 | 96.14 | 97.28 | 97.53 | 97.29 | 96.98 | 96.47 | 97.07 | 95.62 | 97.01 | 97.37 | 97.14 | 96.94 | 96.55 | 96.96 | 93.81 | 95.96 | 96.63 | 96.9 | 96.68 | 96.36 | 96.55 | AE Solar Energy6.95AE7.0 [240V]
AE Solar Energy | AE7.0 [277V] | Y | N | N | 7 kW, 277 Vac Utility Interactive Inverter | 7.01 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.02 |  |  | 100 | 360 | 450 | 0.701 | 1.402 | 2.103 | 3.505 | 5.258 | 7.01 | 93.35 | 95.87 | 96.55 | 96.76 | 96.63 | 96.41 | 96.46 | 94.76 | 96.57 | 97.16 | 97.45 | 97.1 | 97.06 | 97.06 | 94.91 | 96.87 | 97.37 | 97.75 | 97.6 | 97.43 | 97.45 | AE Solar Energy7.01AE7.0 [277V]
AEconversion GMbH | INV250-45US xxxxx [208V] | Y | N | N | 250 W, 208 Vac Utility Interactive modular Inverter | 0.24 | 208 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.02 |  |  | 20 | 30 | 40 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 82.9 | 89.7 | 91.7 | 92.8 | 92.7 | 91.9 | 92 | 82.5 | 89.2 | 91.5 | 92.6 | 92.4 | 91.7 | 91.8 | 81.6 | 88.7 | 90.8 | 92.3 | 92 | 91.4 | 91.3 | AEconversion GMbH0.24INV250-45US xxxxx [208V]
AEconversion GMbH | INV250-45US xxxxx [240V] | Y | N | N | 250 W, 240 Vac Utility Interactive modular Inverter | 0.24 | 240 | 92 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 |  |  | 20 | 30 | 40 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 82.1 | 89.3 | 91.7 | 93.2 | 93.3 | 92.9 | 92.4 | 81.8 | 88.6 | 91.1 | 92.8 | 93.1 | 92.7 | 92.1 | 80.6 | 87.7 | 90.3 | 92.3 | 92.7 | 92.4 | 91.6 | AEconversion GMbH0.24INV250-45US xxxxx [240V]
AEconversion GMbH | INV350-60US xxxxx [208V] | Y | N | N | 350 W, 208 Vac Utility Interactive modular Inverter | 0.3 | 208 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.02 |  |  | 20 | 35 | 50 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 86.5 | 90.9 | 92.7 | 92.9 | 92.1 | 90.6 | 92 | 85.5 | 90.3 | 92.2 | 92.5 | 91.7 | 90 | 91.5 | 84.2 | 89.4 | 91.4 | 92 | 91.2 | 89.5 | 90.9 | AEconversion GMbH0.3INV350-60US xxxxx [208V]
AEconversion GMbH | INV350-60US xxxxx [240V] | Y | N | N | 350 W, 240 Vac Utility Interactive modular Inverter | 0.3 | 240 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 |  |  | 20 | 35 | 50 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 85.9 | 90.9 | 92.8 | 93.7 | 93.4 | 92.2 | 92.9 | 84.9 | 90.1 | 92.2 | 93.2 | 93 | 92.1 | 92.4 | 83.5 | 89.3 | 91.6 | 92.7 | 92.6 | 91.7 | 91.9 | AEconversion GMbH0.3INV350-60US xxxxx [240V]
AEconversion GMbH | INV500-90US-xxxxx [208V] | Y | N | N | 500 W, 208 Vac Utility Interactive modular Inverter, xxxxx are communication variants | 0.48 | 208 | 94 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.028 |  |  | 40 | 60 | 80 | 0.05 | 0.1 | 0.14 | 0.24 | 0.36 | 0.48 | 89.2 | 93.8 | 94.6 | 94.7 | 94.3 | 93.5 | 94.2 | 88.5 | 93.1 | 94.1 | 94.4 | 94 | 93.3 | 93.8 | 87.3 | 92.4 | 93.6 | 94 | 93.7 | 92.9 | 93.4 | AEconversion GMbH0.48INV500-90US-xxxxx [208V]
AEconversion GMbH | INV500-90US-xxxxx [240V] | Y | N | N | 500 W, 240 Vac Utility Interactive modular Inverter, xxxxx are communication variants | 0.48 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.035 |  |  | 40 | 60 | 80 | 0.05 | 0.1 | 0.14 | 0.24 | 0.36 | 0.48 | 89.1 | 93.6 | 94.8 | 95.3 | 95.1 | 94.7 | 94.8 | 88.1 | 93 | 94.3 | 94.9 | 94.8 | 94.4 | 94.4 | 86.9 | 92.4 | 93.9 | 94.6 | 94.5 | 94.1 | 94 | AEconversion GMbH0.48INV500-90US-xxxxx [240V]
AEG Power Solutions | Protect MPV.015.01 [480V] | Y | N | N | 15 kW, 480 Vac, 3-phase Utility Interactive Inverter | 15 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 19 |  |  | 305 | 405 | 595 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8 | AEG Power Solutions15Protect MPV.015.01 [480V]
AEG Power Solutions | Protect MPV.030.01 [480V] | Y | N | N | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter | 30 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 38 |  |  | 305 | 405 | 595 | 3 | 6 | 9 | 15 | 22.5 | 30 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8 | AEG Power Solutions30Protect MPV.030.01 [480V]
AEG Power Solutions | Protect MPV.045.01 [480V] | Y | N | N | 45 kW, 480 Vac, 3-phase Utility Interactive Inverter | 44.41 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 54.94 |  |  | 305 | 405 | 595 | 4.44 | 8.88 | 13.32 | 22.21 | 33.31 | 44.41 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8 | AEG Power Solutions44.41Protect MPV.045.01 [480V]
AEG Power Solutions | Protect MPV.060.01 [480V] | Y | N | N | 60 kW, 480 Vac, 3-phase Utility Interactive Inverter | 60 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 73.3 |  |  | 305 | 405 | 595 | 6 | 12 | 18 | 30 | 45 | 60 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8 | AEG Power Solutions60Protect MPV.060.01 [480V]
AEG Power Solutions | Protect MPV.075.01 [480V] | Y | N | N | 75 kW, 480 Vac, 3-phase Utility Interactive Inverter | 75 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 90 |  |  | 305 | 405 | 595 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8 | AEG Power Solutions75Protect MPV.075.01 [480V]
AEG Power Solutions | Protect MPV.090.01 [480V] | Y | N | N | 90 kW, 480 Vac, 3-phase Utility Interactive Inverter | 90 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 108 |  |  | 305 | 405 | 595 | 9 | 18 | 27 | 45 | 67.5 | 90 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8 | AEG Power Solutions90Protect MPV.090.01 [480V]
AEG Power Solutions | Protect MPV.105.01 [480V] | Y | N | N | 105 kW, 480 Vac, 3-phase Utility Interactive Inverter | 105 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 126 |  |  | 305 | 405 | 595 | 10.5 | 21 | 31.5 | 52.5 | 78.75 | 105 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8 | AEG Power Solutions105Protect MPV.105.01 [480V]
AEG Power Solutions | Protect MPV.120.01 [480V] | Y | N | N | 120 kW, 480 Vac, 3-phase Utility Interactive Inverter | 120 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 144 |  |  | 305 | 405 | 595 | 12 | 24 | 36 | 60 | 90 | 120 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8 | AEG Power Solutions120Protect MPV.120.01 [480V]
AEG Power Solutions | Protect MPV.135.01 [480V] | Y | N | N | 135 kW, 480 Vac, 3-phase Utility Interactive Inverter | 135 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 162 |  |  | 305 | 405 | 595 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8 | AEG Power Solutions135Protect MPV.135.01 [480V]
AEG Power Solutions | Protect MPV.150.01 [480V] | Y | N | N | 150 kW, 480 Vac, 3-phase Utility Interactive Inverter | 150 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 180 |  |  | 305 | 405 | 595 | 15 | 30 | 45 | 75 | 112.5 | 150 | 94.2 | 95.9 | 95.9 | 96.3 | 96.4 | 96 | 96.2 | 91.1 | 94.8 | 96.2 | 96.3 | 96.9 | 96.6 | 96.3 | 93.8 | 96.1 | 96.4 | 96.9 | 97 | 96.9 | 96.8 | AEG Power Solutions150Protect MPV.150.01 [480V]
AEG Power Solutions | Protect PV.500-UL | Y | N | N | 500 kW Utility Interactive Inverter for use with MV transformer | 510 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 123 |  |  | 500 | 660 | 820 | 51 | 102 | 153 | 255 | 382.5 | 510 | 95.1 | 97 | 97.5 | 97.6 | 97.3 | 96.9 | 97.3 | 92.3 | 95.5 | 96.4 | 96.9 | 96.8 | 96.5 | 96.5 | 91.2 | 94.7 | 95.8 | 96.4 | 96.4 | 96.2 | 96 | AEG Power Solutions510Protect PV.500-UL
Aero-Sharp | X01-030L2E1 [240V] | Y | N | N | 3000 W, 240 Vac Utility Interactive Inverter | 2.98 | 240 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.7 |  |  | 100 | 275 | 400 | 0.3 | 0.6 | 0.89 | 1.49 | 2.24 | 2.98 | 78.68 | 88.27 | 90.8 | 92.32 | 92.57 | 92.26 | 91.52 | 78.21 | 89.57 | 91.75 | 93.35 | 93.77 | 93.77 | 92.61 | 83.64 | 90.93 | 92.79 | 94.2 | 94.43 | 94.27 | 93.57 | Aero-Sharp2.98X01-030L2E1 [240V]
Aero-Sharp | X01-040L2E1 [240V] | Y | N | N | 4000 W, 240 Vac Utility Interactive Inverter | 4.012 | 240 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.71 |  |  | 100 | 275 | 400 | 0.4012 | 0.8024 | 1.204 | 2.006 | 3.009 | 4.012 | 84.63 | 90.56 | 92.15 | 92.88 | 92.64 | 91.99 | 92.17 | 84.91 | 91.73 | 93.31 | 94.16 | 94.19 | 93.84 | 93.57 | 88.7 | 93.32 | 94.61 | 95.09 | 94.97 | 94.6 | 94.6 | Aero-Sharp4.012X01-040L2E1 [240V]
Aero-Sharp | X01-050L2E1 [240V] | Y | N | N | 5000 W, 240 Vac Utility Interactive Inverter | 4.986 | 240 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.78 |  |  | 100 | 275 | 400 | 0.4986 | 0.9972 | 1.496 | 2.493 | 3.74 | 4.986 | 84.4 | 91.02 | 92.46 | 93.16 | 92.82 | 92.19 | 92.39 | 85.63 | 91.8 | 93.48 | 94.33 | 94.29 | 93.94 | 93.71 | 85.23 | 92.29 | 93.74 | 94.68 | 94.7 | 94.37 | 94.07 | Aero-Sharp4.986X01-050L2E1 [240V]
Aero-Sharp | X01-060L2E1 [240V] | Y | N | N | 6000 W, 240 Vac Utility Interactive Inverter | 5.993 | 240 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.8 |  |  | 100 | 275 | 400 | 0.5993 | 1.199 | 1.798 | 2.997 | 4.495 | 5.993 | 87.08 | 91.91 | 92.98 | 93.18 | 92.58 | 91.69 | 92.45 | 88.35 | 93.41 | 94.35 | 94.41 | 94.14 | 93.55 | 93.93 | 88.05 | 93.2 | 94.38 | 94.92 | 94.75 | 94.33 | 94.37 | Aero-Sharp5.993X01-060L2E1 [240V]
Agepower Limit | Agepower AP 1500TL-US [208V] | Y | N | N | 1500 W, 208 Vac Utility Interactive Inverter | 1.5 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 330 | 360 | 0.15 | 0.3 | 0.45 | 0.75 | 1.125 | 1.5 | 91.1 | 94.9 | 96 | 96.4 | 96.2 | 96 | 95.9 | 91.7 | 95.5 | 96.5 | 96.8 | 96.7 | 96.5 | 96.4 | 91.5 | 95.2 | 96.2 | 96.7 | 96.7 | 96.5 | 96.3 | Agepower Limit1.5Agepower AP 1500TL-US [208V]
Agepower Limit | Agepower AP 1500TL-US [240V] | Y | N | N | 1650 W, 240 Vac Utility Interactive Inverter | 1.65 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 |  |  | 100 | 330 | 360 | 0.17 | 0.33 | 0.5 | 0.83 | 1.24 | 1.65 | 89.5 | 94.2 | 95.5 | 96.3 | 96.3 | 96 | 95.8 | 90.2 | 94.7 | 95.9 | 96.6 | 96.6 | 96.5 | 96.2 | 91.3 | 95.4 | 96.5 | 97 | 97 | 96.8 | 96.6 | Agepower Limit1.65Agepower AP 1500TL-US [240V]
Agepower Limit | Agepower AP 1500TL-US [277V] | Y | N | N | 1650 W, 277 Vac Utility Interactive Inverter | 1.65 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.13 |  |  | 100 | 330 | 360 | 0.17 | 0.33 | 0.5 | 0.83 | 1.24 | 1.65 | 89.2 | 93.5 | 95 | 96.1 | 96.2 | 96.1 | 95.6 | 89.3 | 94 | 95.6 | 96.4 | 96.6 | 96.7 | 96 | 89.3 | 94.3 | 95.7 | 96.6 | 96.8 | 96.8 | 96.2 | Agepower Limit1.65Agepower AP 1500TL-US [277V]
Agepower Limit | Agepower AP 2000TL-US [208V] | Y | N | N | 1800 W, 208 Vac Utility Interactive Inverter | 1.8 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.09 |  |  | 100 | 360 | 400 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 92.3 | 95.4 | 96 | 96.4 | 96.3 | 96 | 96.1 | 92.8 | 96 | 96.6 | 96.8 | 96.6 | 96.4 | 96.5 | 92.7 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | Agepower Limit1.8Agepower AP 2000TL-US [208V]
Agepower Limit | Agepower AP 2000TL-US [240V] | Y | N | N | 2000 W, 240 Vac Utility Interactive Inverter | 2 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 100 | 360 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.4 | 94.6 | 95.7 | 96.3 | 96.4 | 96.1 | 96 | 92.9 | 96.1 | 96.8 | 97.1 | 97.1 | 96.9 | 96.9 | 92.3 | 95.8 | 96.6 | 96.9 | 97 | 96.8 | 96.7 | Agepower Limit2Agepower AP 2000TL-US [240V]
Agepower Limit | Agepower AP 2000TL-US [277V] | Y | N | N | 2000 W, 277 Vac Utility Interactive Inverter | 2 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 360 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89.3 | 93.7 | 95.1 | 96 | 96.3 | 96.1 | 95.7 | 91.1 | 94.8 | 95.9 | 96.5 | 96.8 | 96.8 | 96.3 | 92.9 | 96.1 | 96.9 | 97.3 | 97.4 | 97.3 | 97.1 | Agepower Limit2Agepower AP 2000TL-US [277V]
Agepower Limit | Agepower AP 3000TL-US [208V] | Y | N | N | 2500 W, 208 Vac Utility Interactive Inverter | 2.5 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 100 | 360 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 92.3 | 95.4 | 96.2 | 96.5 | 96.2 | 95.8 | 96 | 93.9 | 96.2 | 96.8 | 97 | 96.8 | 96.4 | 96.7 | 92.7 | 95.8 | 96.5 | 96.8 | 96.6 | 96.3 | 96.4 | Agepower Limit2.5Agepower AP 3000TL-US [208V]
Agepower Limit | Agepower AP 3000TL-US [240V] | Y | N | N | 3000 W, 240 Vac Utility Interactive Inverter | 2.8 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 |  |  | 100 | 360 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 91 | 94.4 | 95.6 | 96.4 | 96.4 | 96.1 | 96 | 94 | 96.6 | 97.1 | 97.5 | 97.4 | 97 | 97.2 | 93.3 | 96.1 | 96.8 | 97.4 | 97.3 | 97 | 97 | Agepower Limit2.8Agepower AP 3000TL-US [240V]
Agepower Limit | Agepower AP 3000TL-US [277V] | Y | N | N | 3000 W, 277 Vac Utility Interactive Inverter | 2.8 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.19 |  |  | 100 | 360 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.4 | 93.4 | 94.8 | 95.9 | 96.2 | 96 | 95.5 | 91.6 | 95.2 | 96.3 | 96.9 | 97 | 96.8 | 96.6 | 94.1 | 96.6 | 97.3 | 97.7 | 97.6 | 97.4 | 97.4 | Agepower Limit2.8Agepower AP 3000TL-US [277V]
Agepower Limit | Agepower AP 3600MTL-US [208V] | Y | N | N | 3600 W, 208 Vac Utility Interactive Inverter | 3.6 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.23 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.9 | 94.6 | 95.5 | 96.4 | 96.5 | 96.3 | 96.1 | 94.5 | 96.7 | 97.3 | 97.6 | 97.4 | 97.2 | 97.3 | 93 | 96 | 96.9 | 97.3 | 97.3 | 97.1 | 97 | Agepower Limit3.6Agepower AP 3600MTL-US [208V]
Agepower Limit | Agepower AP 3600MTL-US [240V] | Y | N | N | 3600 W, 240 Vac Utility Interactive Inverter | 3.6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.31 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.4 | 94.6 | 95.5 | 96.5 | 96.7 | 96.7 | 96.2 | 95.3 | 97.1 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | 94.2 | 96.5 | 97.1 | 97.5 | 97.6 | 97.4 | 97.3 | Agepower Limit3.6Agepower AP 3600MTL-US [240V]
Agepower Limit | Agepower AP 3600MTL-US [277V] | Y | N | N | 3600 W, 277 Vac Utility Interactive Inverter | 3.6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.2 | 93.9 | 94.7 | 96.1 | 96.6 | 96.6 | 95.9 | 93.4 | 96 | 96.6 | 97.4 | 97.5 | 97.5 | 97.2 | 94.5 | 96.8 | 97.4 | 97.9 | 98 | 97.9 | 97.7 | Agepower Limit3.6Agepower AP 3600MTL-US [277V]
Agepower Limit | Agepower AP 4200MTL-US [208V] | Y | N | N | 4200 W, 208 Vac Utility Interactive Inverter | 4.2 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.6 | 94.4 | 95.5 | 96.6 | 96.8 | 96.7 | 96.3 | 94.1 | 96.5 | 97.1 | 97.3 | 97.1 | 96.7 | 97 | 93.6 | 96.2 | 96.8 | 97.2 | 97.5 | 97.1 | 97.1 | Agepower Limit4.2Agepower AP 4200MTL-US [208V]
Agepower Limit | Agepower AP 4200MTL-US [240V] | Y | N | N | 4200 W, 240 Vac Utility Interactive Inverter | 4.2 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.33 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.4 | 94.6 | 95.5 | 96.5 | 96.7 | 96.7 | 96.2 | 95.3 | 97.1 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | 94.2 | 96.5 | 97.1 | 97.5 | 97.6 | 97.4 | 97.3 | Agepower Limit4.2Agepower AP 4200MTL-US [240V]
Agepower Limit | Agepower AP 4200MTL-US [277V] | Y | N | N | 4200 W, 277 Vac Utility Interactive Inverter | 4.2 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.4 | 94.4 | 96 | 96.6 | 96.8 | 96.6 | 96.3 | 92.1 | 95.2 | 96.3 | 97.3 | 97.6 | 97.1 | 97 | 93.6 | 96.3 | 97.2 | 97.6 | 97.6 | 97.6 | 97.4 | Agepower Limit4.2Agepower AP 4200MTL-US [277V]
Agepower Limit | Agepower AP 5000MTL-US [208V] | Y | N | N | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.7 | 96.5 | 96.8 | 96.9 | 96.5 | 96 | 96.5 | 95.4 | 97 | 97.3 | 97.4 | 97 | 96.5 | 97 | 94.3 | 96.4 | 96.9 | 97.1 | 97 | 96.5 | 96.8 | Agepower Limit4.6Agepower AP 5000MTL-US [208V]
Agepower Limit | Agepower AP 5000MTL-US [240V] | Y | N | N | 4600 W, 240 Vac Utility Interactive Inverter | 4.6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.8 | 95.2 | 96 | 96.7 | 96.6 | 96.4 | 96.3 | 95.8 | 97.3 | 97.7 | 97.8 | 97.5 | 97.1 | 97.5 | 96.7 | 96.7 | 97.2 | 97.5 | 97.4 | 97.1 | 97.3 | Agepower Limit4.6Agepower AP 5000MTL-US [240V]
Agepower Limit | Agepower AP 5000MTL-US [277V] | Y | N | N | 4600 W, 277 Vac Utility Interactive Inverter | 4.6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.43 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.2 | 94.9 | 95.6 | 96.6 | 96.8 | 96.8 | 96.4 | 94.6 | 96.7 | 97.2 | 97.6 | 97.6 | 97.4 | 97.4 | 95.4 | 97.1 | 97.6 | 97.9 | 97.8 | 97.7 | 97.7 | Agepower Limit4.6Agepower AP 5000MTL-US [277V]
Agepower Limit | Agepower AP 10000 TL3-US [277V] | Y | N | N | 10000 W, 277 Vac Utility Interactive Inverter | 10.1 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.01 |  |  | 250 | 420 | 480 | 1.1 | 2.2 | 3.3 | 5.5 | 7.58 | 10.1 | 89.5 | 93.1 | 94.1 | 94.9 | 95 | 95 | 94.6 | 90.1 | 93.9 | 95.2 | 96 | 96.3 | 96.4 | 95.7 | 89.9 | 94.2 | 95.4 | 96.3 | 96.7 | 96.8 | 96 | Agepower Limit10.1Agepower AP 10000 TL3-US [277V]
Agepower Limit | Agepower AP 12000 TL3-US [277V] | Y | N | N | 11620 W, 277 Vac Utility Interactive Inverter | 11.62 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.01 |  |  | 250 | 420 | 480 | 1.16 | 2.32 | 3.49 | 5.81 | 8.72 | 11.62 | 89.8 | 93.4 | 94.4 | 95.2 | 94.9 | 95 | 94.6 | 90.2 | 94.2 | 95.3 | 96.2 | 96.4 | 96.5 | 95.9 | 91 | 94.6 | 95.6 | 96.4 | 96.6 | 96.7 | 96.1 | Agepower Limit11.62Agepower AP 12000 TL3-US [277V]
Agepower Limit | Agepower AP 18000 TL3-US [277V] | Y | N | N | 18220 W, 277 Vac Utility Interactive Inverter | 18.31 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.01 |  |  | 250 | 420 | 480 | 1.83 | 3.66 | 5.49 | 9.15 | 13.73 | 18.31 | 92.3 | 94.9 | 95.4 | 95.2 | 95.5 | 95.4 | 95.3 | 92.5 | 95.8 | 96.4 | 96.8 | 96.9 | 96.6 | 96.6 | 92.9 | 95.8 | 96.5 | 96.9 | 97.1 | 96.8 | 96.7 | Agepower Limit18.31Agepower AP 18000 TL3-US [277V]
Agepower Limit | Agepower AP 20000 TL3-US [277V] | Y | N | N | 20000 W, 277 Vac Utility Interactive Inverter | 20.42 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 250 | 420 | 480 | 2.04 | 4.08 | 6.12 | 10.21 | 15.31 | 20.42 | 92.7 | 95.1 | 95.5 | 95.6 | 95.7 | 95.7 | 95.5 | 93.1 | 96 | 96.5 | 96.8 | 96.8 | 96.8 | 96.6 | 93.5 | 96 | 96.6 | 97 | 97.1 | 97 | 96.8 | Agepower Limit20.42Agepower AP 20000 TL3-US [277V]
Alpha Technologies | Solaris 3500 XP [240V] | Y | N | N | 3.5 kW, 240 Vac, NEMA Type 3R, Grid Interactive PV Inverter & Battery Backed UPS, MPPT | 3.5 | 240 | 90.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 15 |  |  | 48 | 51 | 52 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 87.5 | 91 | 92.3 | 91.6 | 90.4 | 88.4 | 90.7 | 86.3 | 90.8 | 92.3 | 91.3 | 90.1 | 88.2 | 90.4 | 85 | 90.6 | 92.2 | 91.6 | 90.4 | 88.7 | 90.6 | Alpha Technologies3.5Solaris 3500 XP [240V]
Altenergy Power System Inc. | YC200-NA [240V] | Y | N | N | 220 W, 240 Vac Utility Interactive Inverter | 0.22 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.08 |  |  | 27 | 36 | 45 | 0.022 | 0.044 | 0.066 | 0.11 | 0.165 | 0.22 | 90.1 | 92.4 | 92.8 | 94.6 | 94.8 | 94.3 | 94.2 | 89.9 | 91.3 | 92.9 | 93.9 | 94.8 | 94.9 | 94 | 90.6 | 89.7 | 91.8 | 93.4 | 94.4 | 94.8 | 93.5 | Altenergy Power System Inc.0.22YC200-NA [240V] |  | 2017-12-15
Altenergy Power System Inc. | YC250A [240V] | Y | N | N | 225 W, 240 Vac Utility Interactive Inverter | 0.225 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.15 |  |  | 24 | 35 | 45 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 88.43 | 93.05 | 93.8 | 94.71 | 94.57 | 93.17 | 94.11 | 89.77 | 92.52 | 93.7 | 94.51 | 95.06 | 95.02 | 94.44 | 88.24 | 90.29 | 92.46 | 93.92 | 94.84 | 95.14 | 93.89 | Altenergy Power System Inc.0.225YC250A [240V] |  | 2017-12-15
Altenergy Power System Inc. | YC250I [240V] | Y | N | N | 225 W, 240 Vac Utility Interactive Inverter | 0.225 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.15 |  |  | 24 | 35 | 45 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 88.43 | 93.05 | 93.8 | 94.71 | 94.57 | 93.17 | 94.11 | 89.77 | 92.52 | 93.7 | 94.51 | 95.06 | 95.02 | 94.44 | 88.24 | 90.29 | 92.46 | 93.92 | 94.84 | 95.14 | 93.89 | Altenergy Power System Inc.0.225YC250I [240V] |  | 2017-12-15
Altenergy Power System Inc. | YC500A [208V] | Y | N | N | 500 W, 208 Vac, Utility Interactive Inverter | 0.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.12 |  |  | 24 | 35 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.375 | 0.5 | 93.7 | 95.1 | 95.4 | 95.4 | 94.4 | 92.7 | 94.6 | 94.3 | 95.2 | 95.5 | 95.5 | 95.5 | 94.9 | 95.4 | 94.2 | 94.2 | 93.9 | 94.9 | 95.5 | 95.3 | 95 | Altenergy Power System Inc.0.5YC500A [208V] |  | 2017-12-15
Altenergy Power System Inc. | YC500A [240V] | Y | N | N | 500 W, 240 Vac, Utility Interactive Inverter | 0.5 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.15 |  |  | 24 | 35 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.375 | 0.5 | 93.3 | 95.1 | 93.8 | 95.6 | 94.5 | 93 | 94.6 | 92.5 | 95.1 | 95.6 | 95.6 | 95.7 | 95.3 | 95.5 | 94 | 94.5 | 93.6 | 95 | 95.7 | 95.6 | 95.2 | Altenergy Power System Inc.0.5YC500A [240V] |  | 2017-12-15
Altenergy Power System Inc. | YC500I [208V] | Y | N | N | 500 W, 208 Vac, Utility Interactive Inverter | 0.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.12 |  |  | 24 | 35 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.375 | 0.5 | 93.7 | 95.1 | 95.4 | 95.4 | 94.4 | 92.7 | 94.6 | 94.3 | 95.2 | 95.5 | 95.5 | 95.5 | 94.9 | 95.4 | 94.2 | 94.2 | 93.9 | 94.9 | 95.5 | 95.3 | 95 | Altenergy Power System Inc.0.5YC500I [208V] |  | 2017-12-15
Altenergy Power System Inc. | YC500I [240V] | Y | N | N | 500 W, 240 Vac, Utility Interactive Inverter | 0.5 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.15 |  |  | 24 | 35 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.375 | 0.5 | 93.3 | 95.1 | 93.8 | 95.6 | 94.5 | 93 | 94.6 | 92.5 | 95.1 | 95.6 | 95.6 | 95.7 | 95.3 | 95.5 | 94 | 94.5 | 93.6 | 95 | 95.7 | 95.6 | 95.2 | Altenergy Power System Inc.0.5YC500I [240V] |  | 2017-12-15
Altenergy Power System Inc. | YC600 [240V] | Y | Y | Y | 548 W, 240 Vac Grid Support Utility Interactive Microinverter, Rack mounted | 0.55 | 240 | 96.5 | [02/10/2018] | [V5] | 2018-10-15 | N | Y |  | 0.02 |  |  | 24 | 36 | 45 | 0.0548 | 0.1096 | 0.1644 | 0.274 | 0.411 | 0.548 | 94.4 | 95.9 | 96 | 96.4 | 96.3 | 96.1 | 96.2 | 94.1 | 95.8 | 96.2 | 96.5 | 96.7 | 96.6 | 96.4 | 93.7 | 95.7 | 95.8 | 96.4 | 96.7 | 96.7 | 96.4 | Altenergy Power System Inc.0.548YC600 [240V] [SI1] | 2018-03-01 | 2018-10-15
Altenergy Power System Inc. | YC1000-3-208 [480V] | Y | N | N | 900 W, 3-phase, Utility Interactive Inverter | 0.9 | 480 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.11 |  |  | 33 | 40 | 48 | 0.09 | 0.18 | 0.27 | 0.45 | 0.68 | 0.9 | 90.3 | 94.2 | 94.4 | 94.8 | 94.6 | 93.7 | 94.4 | 89.4 | 93.8 | 94.5 | 94.6 | 94.7 | 94.1 | 94.4 | 88.9 | 93.1 | 94.2 | 94.2 | 94.6 | 94.1 | 94.1 | Altenergy Power System Inc.0.9YC1000-3-208 [480V] |  | 2017-12-15
Altenergy Power System Inc. | YC1000-3-480 [480V] | Y | N | N | 0.9 kW, 480 Vac, 3-phase Utility Interactive Inverter | 0.9 | 480 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.88 |  |  | 28 | 36 | 48 | 0.09 | 0.18 | 0.27 | 0.45 | 0.675 | 0.9 | 89.9 | 93.9 | 92.7 | 94.9 | 95.2 | 94.7 | 94.6 | 88.9 | 93.6 | 94.3 | 94.5 | 95.3 | 95.2 | 94.7 | 81.8 | 92.2 | 93.9 | 93.3 | 94.8 | 95.1 | 93.7 | Altenergy Power System Inc.0.9YC1000-3-480 [480V] |  | 2017-12-15
Altenergy Power System Inc. | YC1000-3-K480 | Y | N | N | 1200 W, 3-phase, Utility Interactive Inverter | 1.16 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.83 |  |  | 50 | 51.5 | 55 | 0.12 | 0.23 | 0.35 | 0.58 | 0.87 | 1.16 | 91.1 | 94.7 | 95.3 | 95.4 | 95 | 93.5 | 94.9 | 90.7 | 94.6 | 95.3 | 95.3 | 94.9 | 93.4 | 94.8 | 89.7 | 94.3 | 95.2 | 95.1 | 94.7 | 93.4 | 94.6 | Altenergy Power System Inc.1.16YC1000-3-K480 |  | 2017-12-15
American Electric Technologies | ISIS-1000-15000-60 | Y | N | N | 1000 kW, 3-phase Utility Interactive Inverter | 1000 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 300 |  |  | 610 | 720 | 1000 | 100 | 200 | 300 | 500 | 750 | 1000 | 93.8 | 95.6 | 96.2 | 96.7 | 97.7 | 97.4 | 97 | 93.3 | 95.2 | 95.7 | 96.3 | 96.6 | 97.1 | 96.2 | 92.1 | 94.2 | 95.2 | 95.6 | 96 | 95.9 | 95.6 | American Electric Technologies1000ISIS-1000-15000-60
American Electric Technologies | ISIS-1000-410-60 | Y | N | N | 1000 kW, 3-phase Inverter for 410 Vac applications with TP-1 transformer | 1000 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 350 |  |  | 610 | 720 | 1000 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.5 | 96.2 | 96.7 | 96.9 | 97.1 | 96.7 | 96.9 | 94 | 95.8 | 96.2 | 96.5 | 96.4 | 96.5 | 96.3 | 92.8 | 94.8 | 95.5 | 95.8 | 95.7 | 95.4 | 95.5 | American Electric Technologies1000ISIS-1000-410-60
AMETEK Solidstate Control | RECon 30L-100-US | Y | N | N | 100 kW, 3-phase Utility Interactive Inverter | 100 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 59.63 |  |  | 325 | 487 | 650 | 10 | 20 | 30 | 50 | 75 | 100 | 96.5 | 98.1 | 98.4 | 98 | 97.3 | 96.9 | 97.5 | 95.3 | 97.8 | 98.3 | 98.2 | 98.1 | 97.9 | 98 | 96 | 98.2 | 98.8 | 98.7 | 98.3 | 97.7 | 98.3 | AMETEK Solidstate Control100RECon 30L-100-US
AMETEK Solidstate Control | RECon 30H-150-US [300V] | Y | N | N | 150 kW, 3-phase output 300Vac/LV/MV Utility Interactive Inverter | 150 | 300 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 62.53 |  |  | 480 | 615 | 750 | 15 | 30 | 45 | 75 | 112.5 | 150 | 93.6 | 96.3 | 97 | 97.5 | 97.4 | 97.7 | 97.2 | 95.6 | 97.6 | 98.4 | 98.3 | 98 | 98 | 98 | 94.1 | 96.7 | 97.7 | 97.9 | 97.8 | 97.6 | 97.6 | AMETEK Solidstate Control150RECon 30H-150-US [300V]
Andalay Solar | LW-230-1-AC1-A-B [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Andalay Solar0.19LW-230-1-AC1-A-B [240V]
Andalay Solar | LW-230-1-AC3-B-B [208V] | Y | N | N | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Andalay Solar0.19LW-230-1-AC3-B-B [208V]
Andalay Solar | LW-235-1-AC1-A-B [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Andalay Solar0.19LW-235-1-AC1-A-B [240V]
Andalay Solar | LW-235-1-AC3-B-B [208V] | Y | N | N | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Andalay Solar0.19LW-235-1-AC3-B-B [208V]
Andalay Solar | LW-240-1-AC1-A-B [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Andalay Solar0.19LW-240-1-AC1-A-B [240V]
Andalay Solar | LW-240-1-AC3-B-B [208V] | Y | N | N | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Andalay Solar0.19LW-240-1-AC3-B-B [208V]
Andalay Solar | ST-175-1AC1-A-A [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Andalay Solar0.19ST-175-1AC1-A-A [240V]
Andalay Solar | ST-175-1AC3-B-A [208V] | Y | N | N | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.02 | 0.04 | 0.06 | 0.1 | 0.1 | 0.2 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Andalay Solar0.19ST-175-1AC3-B-A [208V]
Andalay Solar | ST-185-1AC1-A-A [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Andalay Solar0.19ST-185-1AC1-A-A [240V]
Andalay Solar | ST-185-1AC1-A-B [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Andalay Solar0.19ST-185-1AC1-A-B [240V]
Andalay Solar | ST-185-1AC3-B-A [208V] | Y | N | N | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.02 | 0.04 | 0.06 | 0.1 | 0.1 | 0.2 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Andalay Solar0.19ST-185-1AC3-B-A [208V]
Andalay Solar | ST-185-1AC3-B-B [208V] | Y | N | N | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.02 | 0.04 | 0.06 | 0.1 | 0.1 | 0.2 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Andalay Solar0.19ST-185-1AC3-B-B [208V]
Andalay Solar | ST-190-1AC1-A-B [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Andalay Solar0.19ST-190-1AC1-A-B [240V]
Andalay Solar | ST-190-1AC3-B-B [208V] | Y | N | N | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Andalay Solar0.19ST-190-1AC3-B-B [208V]
Andalay Solar | ST-195-1AC1-A-B [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Andalay Solar0.19ST-195-1AC1-A-B [240V]
Andalay Solar | ST-195-1AC3-B-B [208V] | Y | N | N | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Andalay Solar0.19ST-195-1AC3-B-B [208V]
Andalay Solar | LW-230-1-AC0-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215LW-230-1-AC0-D-B [208V]
Andalay Solar | LW-230-1-AC0-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215LW-230-1-AC0-D-B [240V]
Andalay Solar | LW-230-1-AC2-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215LW-230-1-AC2-D-B [208V]
Andalay Solar | LW-230-1-AC2-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215LW-230-1-AC2-D-B [240V]
Andalay Solar | LW-235-1-AC0-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215LW-235-1-AC0-D-B [208V]
Andalay Solar | LW-235-1-AC0-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215LW-235-1-AC0-D-B [240V]
Andalay Solar | LW-235-1-AC2-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215LW-235-1-AC2-D-B [208V]
Andalay Solar | LW-235-1-AC2-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215LW-235-1-AC2-D-B [240V]
Andalay Solar | LW-240-1-AC0-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215LW-240-1-AC0-D-B [208V]
Andalay Solar | LW-240-1-AC0-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215LW-240-1-AC0-D-B [240V]
Andalay Solar | LW-240-1-AC2-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215LW-240-1-AC2-D-B [208V]
Andalay Solar | LW-240-1-AC2-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215LW-240-1-AC2-D-B [240V]
Andalay Solar | TW-240-1-AC2-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215TW-240-1-AC2-D-B [208V]
Andalay Solar | TW-240-1-AC2-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215TW-240-1-AC2-D-B [240V]
Andalay Solar | TW-245-1-AC2-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215TW-245-1-AC2-D-B [208V]
Andalay Solar | TW-245-1-AC2-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215TW-245-1-AC2-D-B [240V]
Andalay Solar | TW-250-1-AC2-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215TW-250-1-AC2-D-B [208V]
Andalay Solar | TW-250-1-AC2-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Andalay Solar0.215TW-250-1-AC2-D-B [240V]
Apparent | MGI220-xxx [240V] | Y | N | N | 180 W, 240 Vac Inverter, where xxx are connector types | 0.18 | 240 | 90 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.4 |  |  | 23 | 28 | 36 | 0.02 | 0.04 | 0.05 | 0.09 | 0.14 | 0.18 | 80.5 | 87 | 88.4 | 90.6 | 91.2 | 91.2 | 90.1 | 81.6 | 86.8 | 89 | 90.2 | 91.2 | 91.4 | 90.1 | 79.7 | 85.7 | 88.2 | 89.7 | 90.7 | 91.2 | 89.5 | Apparent0.18MGI220-xxx [240V]
Apparent | SG424-120V [120V] | Y | N | N | 230 W, Utility Interactive Inverter, 120V Split Phase | 0.23 | 120 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.45 |  |  | 29 | 36 | 48 | 0.02 | 0.05 | 0.07 | 0.12 | 0.17 | 0.23 | 85.6 | 89.7 | 91.5 | 92.1 | 91.8 | 91.1 | 91.5 | 85.3 | 90.2 | 91.4 | 92.2 | 92.2 | 91.6 | 91.7 | 84.2 | 89.9 | 90.8 | 92.4 | 92.4 | 91.9 | 91.7 | Apparent0.23SG424-120V [120V]
AU Optronics | PM060MA0_240 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM060MA0_240 [240V]
AU Optronics | PM060MA0_245 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM060MA0_245 [240V]
AU Optronics | PM060MA0_250 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM060MA0_250 [240V]
AU Optronics | PM060MA0_255 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM060MA0_255 [240V]
AU Optronics | PM060MA0_260 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM060MA0_260 [240V]
AU Optronics | PM060MA0_265 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM060MA0_265 [240V]
AU Optronics | PM060MA0_270 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM060MA0_270 [240V]
AU Optronics | PM060MA0_275 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.023 | 0.045 | 0.068 | 0.113 | 0.169 | 0.225 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM060MA0_275 [240V]
AU Optronics | PM060MA1_275 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.023 | 0.045 | 0.068 | 0.113 | 0.169 | 0.225 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM060MA1_275 [240V]
AU Optronics | PM060MA2_275 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.023 | 0.045 | 0.068 | 0.113 | 0.169 | 0.225 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM060MA2_275 [240V]
AU Optronics | PM060PA0_235 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM060PA0_235 [240V]
AU Optronics | PM060PA0_240 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM060PA0_240 [240V]
AU Optronics | PM060PA0_250 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM060PA0_250 [240V]
AU Optronics | PM060PA0_255 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM060PA0_255 [240V]
AU Optronics | PM060PA0_260 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM060PA0_260 [240V]
AU Optronics | PM240PA0_235 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41 | AU Optronics0.225PM240PA0_235 [240V]
AU Optronics | PM240PA0_240 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41 | AU Optronics0.225PM240PA0_240 [240V]
AU Optronics | PM240PA0_245 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41 | AU Optronics0.225PM240PA0_245 [240V]
AU Optronics | PM245PA0_235 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41 | AU Optronics0.225PM245PA0_235 [240V]
AU Optronics | PM245PA0_240 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41 | AU Optronics0.225PM245PA0_240 [240V]
AU Optronics | PM245PA0_245 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41 | AU Optronics0.225PM245PA0_245 [240V]
AU Optronics | PM245PA0_250 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41 | AU Optronics0.225PM245PA0_250 [240V]
AU Optronics | PM245PA0_255 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM245PA0_255 [240V]
AU Optronics | PM245PA0_260 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM245PA0_260 [240V]
AU Optronics | PM250MA0_240 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM250MA0_240 [240V]
AU Optronics | PM250MA0_245 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41 | AU Optronics0.225PM250MA0_245 [240V]
AU Optronics | PM250MA0_250 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41 | AU Optronics0.225PM250MA0_250 [240V]
AU Optronics | PM250MA0_255 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41 | AU Optronics0.225PM250MA0_255 [240V]
AU Optronics | PM250MA0_260 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41 | AU Optronics0.225PM250MA0_260 [240V]
AU Optronics | PM250MA0_265 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41 | AU Optronics0.225PM250MA0_265 [240V]
AU Optronics | PM250MA0_270 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM250MA0_270 [240V]
AU Optronics | PM250MA0_275 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.023 | 0.045 | 0.068 | 0.113 | 0.169 | 0.225 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM250MA0_275 [240V]
AU Optronics | PM250MA1_275 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.023 | 0.045 | 0.068 | 0.113 | 0.169 | 0.225 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM250MA1_275 [240V]
AU Optronics | PM250MA2_275 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.023 | 0.045 | 0.068 | 0.113 | 0.169 | 0.225 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | AU Optronics0.225PM250MA2_275 [240V]
AU Optronics | PM060MA1_240 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA1_240 [208V]
AU Optronics | PM060MA1_240 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA1_240 [240V]
AU Optronics | PM060MA1_245 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA1_245 [208V]
AU Optronics | PM060MA1_245 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA1_245 [240V]
AU Optronics | PM060MA1_250 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA1_250 [208V]
AU Optronics | PM060MA1_250 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA1_250 [240V]
AU Optronics | PM060MA1_255 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA1_255 [208V]
AU Optronics | PM060MA1_255 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA1_255 [240V]
AU Optronics | PM060MA1_260 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA1_260 [208V]
AU Optronics | PM060MA1_260 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA1_260 [240V]
AU Optronics | PM060MA1_265 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA1_265 [208V]
AU Optronics | PM060MA1_265 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA1_265 [240V]
AU Optronics | PM060MA1_270 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA1_270 [208V]
AU Optronics | PM060MA1_270 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA1_270 [240V]
AU Optronics | PM060MA2_240 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA2_240 [208V]
AU Optronics | PM060MA2_240 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA2_240 [240V]
AU Optronics | PM060MA2_245 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA2_245 [208V]
AU Optronics | PM060MA2_245 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA2_245 [240V]
AU Optronics | PM060MA2_250 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA2_250 [208V]
AU Optronics | PM060MA2_250 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA2_250 [240V]
AU Optronics | PM060MA2_255 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA2_255 [208V]
AU Optronics | PM060MA2_255 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA2_255 [240V]
AU Optronics | PM060MA2_260 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA2_260 [208V]
AU Optronics | PM060MA2_260 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA2_260 [240V]
AU Optronics | PM060MA2_265 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA2_265 [208V]
AU Optronics | PM060MA2_265 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA2_265 [240V]
AU Optronics | PM060MA2_270 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA2_270 [208V]
AU Optronics | PM060MA2_270 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060MA2_270 [240V]
AU Optronics | PM060PA0_245 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.24 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA0_245 [240V]
AU Optronics | PM060PA1_235 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA1_235 [208V]
AU Optronics | PM060PA1_235 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA1_235 [240V]
AU Optronics | PM060PA1_240 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA1_240 [208V]
AU Optronics | PM060PA1_240 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA1_240 [240V]
AU Optronics | PM060PA1_245 [208V] | Y | N | N | 240 W, 208/Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA1_245 [208V]
AU Optronics | PM060PA1_245 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA1_245 [240V]
AU Optronics | PM060PA1_250 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA1_250 [208V]
AU Optronics | PM060PA1_250 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA1_250 [240V]
AU Optronics | PM060PA1_255 [208V] | Y | N | N | 240 W, 208/Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA1_255 [208V]
AU Optronics | PM060PA1_255 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA1_255 [240V]
AU Optronics | PM060PA1_260 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA1_260 [208V]
AU Optronics | PM060PA1_260 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA1_260 [240V]
AU Optronics | PM060PA2_235 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA2_235 [208V]
AU Optronics | PM060PA2_235 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA2_235 [240V]
AU Optronics | PM060PA2_240 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA2_240 [208V]
AU Optronics | PM060PA2_240 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA2_240 [240V]
AU Optronics | PM060PA2_245 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA2_245 [208V]
AU Optronics | PM060PA2_245 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA2_245 [240V]
AU Optronics | PM060PA2_250 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA2_250 [208V]
AU Optronics | PM060PA2_250 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA2_250 [240V]
AU Optronics | PM060PA2_255 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA2_255 [208V]
AU Optronics | PM060PA2_255 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA2_255 [240V]
AU Optronics | PM060PA2_260 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA2_260 [208V]
AU Optronics | PM060PA2_260 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM060PA2_260 [240V]
AU Optronics | PM245PA1_235 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | AU Optronics0.24PM245PA1_235 [240V]
AU Optronics | PM245PA1_240 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | AU Optronics0.24PM245PA1_240 [240V]
AU Optronics | PM245PA1_245 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | AU Optronics0.24PM245PA1_245 [240V]
AU Optronics | PM245PA1_250 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | AU Optronics0.24PM245PA1_250 [240V]
AU Optronics | PM245PA1_255 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM245PA1_255 [208V]
AU Optronics | PM245PA1_255 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM245PA1_255 [240V]
AU Optronics | PM245PA1_260 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM245PA1_260 [208V]
AU Optronics | PM245PA1_260 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM245PA1_260 [240V]
AU Optronics | PM245PA2_235 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM245PA2_235 [208V]
AU Optronics | PM245PA2_235 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM245PA2_235 [240V]
AU Optronics | PM245PA2_240 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM245PA2_240 [208V]
AU Optronics | PM245PA2_240 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM245PA2_240 [240V]
AU Optronics | PM245PA2_245 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM245PA2_245 [208V]
AU Optronics | PM245PA2_245 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM245PA2_245 [240V]
AU Optronics | PM245PA2_250 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM245PA2_250 [208V]
AU Optronics | PM245PA2_250 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM245PA2_250 [240V]
AU Optronics | PM245PA2_255 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM245PA2_255 [208V]
AU Optronics | PM245PA2_255 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM245PA2_255 [240V]
AU Optronics | PM245PA2_260 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM245PA2_260 [208V]
AU Optronics | PM245PA2_260 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM245PA2_260 [240V]
AU Optronics | PM250MA1_240 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA1_240 [240V]
AU Optronics | PM250MA1_245 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | AU Optronics0.24PM250MA1_245 [240V]
AU Optronics | PM250MA1_250 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | AU Optronics0.24PM250MA1_250 [240V]
AU Optronics | PM250MA1_255 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | AU Optronics0.24PM250MA1_255 [240V]
AU Optronics | PM250MA1_260 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | AU Optronics0.24PM250MA1_260 [240V]
AU Optronics | PM250MA1_265 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | AU Optronics0.24PM250MA1_265 [208V]
AU Optronics | PM250MA1_265 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | AU Optronics0.24PM250MA1_265 [240V]
AU Optronics | PM250MA1_270 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA1_270 [208V]
AU Optronics | PM250MA1_270 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA1_270 [240V]
AU Optronics | PM250MA2_240 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA2_240 [208V]
AU Optronics | PM250MA2_240 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA2_240 [240V]
AU Optronics | PM250MA2_245 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA2_245 [208V]
AU Optronics | PM250MA2_245 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA2_245 [240V]
AU Optronics | PM250MA2_250 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA2_250 [208V]
AU Optronics | PM250MA2_250 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA2_250 [240V]
AU Optronics | PM250MA2_255 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA2_255 [208V]
AU Optronics | PM250MA2_255 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA2_255 [240V]
AU Optronics | PM250MA2_260 [208V] | Y | N | N | 240 W, 208/Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA2_260 [208V]
AU Optronics | PM250MA2_260 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA2_260 [240V]
AU Optronics | PM250MA2_265 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA2_265 [208V]
AU Optronics | PM250MA2_265 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA2_265 [240V]
AU Optronics | PM250MA2_270 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA2_270 [208V]
AU Optronics | PM250MA2_270 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | AU Optronics0.24PM250MA2_270 [240V]
Auxin Solar | AXU-PV1500U [208V] | Y | N | N | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.46 | 90.49 | 92.52 | 94.25 | 94.92 | 95.02 | 93.86 | 85.04 | 91.04 | 93.19 | 94.79 | 95.41 | 95.53 | 94.38 | 85.31 | 91.19 | 93.54 | 95.02 | 95.55 | 95.76 | 94.58 | Auxin Solar1.55AXU-PV1500U [208V]
Auxin Solar | AXU-PV1500U [240V] | Y | N | N | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.62 | 90.46 | 92.57 | 94.42 | 95.07 | 95.25 | 93.99 | 84.89 | 90.97 | 93.04 | 94.81 | 95.51 | 95.73 | 94.42 | 85.22 | 91.38 | 93.44 | 95.12 | 95.65 | 95.93 | 94.66 | Auxin Solar1.55AXU-PV1500U [240V]
Auxin Solar | AXU-PV2000U [208V] | Y | N | N | 2 kW, 208 Vac Utility Interactive Inverter | 2.06 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.29 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 88.28 | 93.12 | 94.41 | 95.27 | 95.43 | 95.37 | 94.87 | 89.63 | 93.68 | 94.91 | 95.73 | 95.84 | 95.8 | 95.34 | 89.74 | 94.01 | 95.11 | 96.13 | 96.38 | 96.07 | 95.77 | Auxin Solar2.06AXU-PV2000U [208V]
Auxin Solar | AXU-PV2000U [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter | 2.06 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 86.91 | 92.14 | 93.78 | 94.94 | 95.3 | 95.37 | 94.55 | 87.84 | 92.87 | 94.26 | 95.56 | 95.79 | 95.73 | 95.09 | 88.1 | 93.05 | 94.37 | 95.71 | 96 | 95.94 | 95.28 | Auxin Solar2.06AXU-PV2000U [240V]
Auxin Solar | AXU-PV3000U [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.57 | 94.41 | 95.16 | 95.47 | 95.31 | 94.62 | 95.1 | 92.05 | 94.92 | 95.58 | 95.89 | 95.76 | 95.37 | 95.56 | 92.22 | 95.17 | 95.79 | 96.25 | 95.93 | 95.8 | 95.78 | Auxin Solar3AXU-PV3000U [208V]
Auxin Solar | AXU-PV3000U [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.301 | 0.602 | 0.903 | 1.505 | 2.258 | 3.01 | 90 | 93.9 | 94.85 | 95.4 | 95.31 | 94.83 | 94.97 | 90.64 | 94.34 | 95.34 | 95.79 | 95.87 | 95.6 | 95.49 | 91 | 94.59 | 95.44 | 95.97 | 96.01 | 95.77 | 95.65 | Auxin Solar3.01AXU-PV3000U [240V]
Auxin Solar | AXN-PV4000U [208V] | Y | N | N | 4 kW, 208 Vac Utility Interactive Inverter | 3.98 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.398 | 0.796 | 1.194 | 1.99 | 2.985 | 3.98 | 90.53 | 94.32 | 95.17 | 95.44 | 95.41 | 95.16 | 95.13 | 91.58 | 94.87 | 95.63 | 96.05 | 96 | 95.45 | 95.7 | 91.82 | 95.03 | 95.8 | 96.45 | 96.31 | 95.76 | 96.01 | Auxin Solar3.98AXN-PV4000U [208V]
Auxin Solar | AXN-PV4000U [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.399 | 0.798 | 1.197 | 1.995 | 2.993 | 3.99 | 90.55 | 94.3 | 95.24 | 95.69 | 95.74 | 95.56 | 95.38 | 91.53 | 94.95 | 95.81 | 96.33 | 96.33 | 96.05 | 95.99 | 91.95 | 95.23 | 95.96 | 96.4 | 96.48 | 96.25 | 96.15 | Auxin Solar3.99AXN-PV4000U [240V]
Ballard Power Systems | EPC-PV-208-30KW [208V] | Y | N | N | Utility Interactive 208 Vac , 30 kW PV Power Converter System | 30 | 208 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 32 |  |  | 290 | 322 | 420 | 3 | 6 | 9 | 15 | 22.5 | 30 | 83.72 | 90.23 | 92.39 | 93.75 | 94.13 | 93.87 | 93.22 | 83.3 | 89.7 | 92.12 | 93.58 | 94 | 93.77 | 93.03 | 81.74 | 89.02 | 91.17 | 93 | 93.45 | 93.37 | 92.39 | Ballard Power Systems30EPC-PV-208-30KW [208V]
Ballard Power Systems | EPC-PV-480-30KW [480V] | Y | N | N | Utility Interactive 480 Vac, 30 kW PV Power Converter System | 30 | 480 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 27 |  |  | 290 | 322 | 420 | 3 | 6 | 9 | 15 | 22.5 | 30 | 83.8 | 90.14 | 92.4 | 93.85 | 94.24 | 93.93 | 93.3 | 83.23 | 89.86 | 92.1 | 93.66 | 94.07 | 93.8 | 93.09 | 81.53 | 88.67 | 91.17 | 93.05 | 93.5 | 93.3 | 92.39 | Ballard Power Systems30EPC-PV-480-30KW [480V]
Ballard Power Systems | EPC-PV-208-75KW | Y | N | N | Utility Interactive 75 kW PV Power Converter System | 75 |  | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 107 |  |  | 330 | 352 | 420 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 81.8 | 88.6 | 91 | 92.6 | 93 | 92.8 | 92 | 81.2 | 88.3 | 90.7 | 92.4 | 92.9 | 92.7 | 91.8 | 79.9 | 87.5 | 90 | 91.9 | 92.4 | 92.2 | 91.2 | Ballard Power Systems75EPC-PV-208-75KW
Ballard Power Systems | EPC-PV-480-75KW [480V] | Y | N | N | Utility Interactive 480 Vac, 75 kW PV Power Converter System | 75 | 480 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 110 |  |  | 330 | 352 | 420 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 81.4 | 88.5 | 90.9 | 92.6 | 93.1 | 93 | 92 | 81.1 | 88.2 | 90.7 | 92.4 | 92.9 | 92.8 | 91.9 | 79.7 | 87.5 | 90.1 | 92 | 92.5 | 92.3 | 91.3 | Ballard Power Systems75EPC-PV-480-75KW [480V]
Beacon Power | M4 | Y | N | N | 4 kW Power Conversion System | 4 |  | 90 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 14 |  |  | 46.5 | 54.5 | 58 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 88.63 | 92.11 | 92.88 | 92.82 | 91.6 | 89.17 | 91.79 | 86.23 | 90.4 | 91.55 | 91.38 | 89.29 | 87.38 | 89.84 | 84.47 | 89.04 | 90.58 | 90.79 | 88.45 | 86.39 | 88.97 | Beacon Power4M4
Beacon Power | M4 Plus | Y | N | N | 4 kW Power Conversion System with Meter | 4 |  | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 14 |  |  | 46.5 | 54.5 | 58 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 89.16 | 92.55 | 93.39 | 93.49 | 92.37 | 89.68 | 92.48 | 86.23 | 90.71 | 91.58 | 91.8 | 90.08 | 87.97 | 90.39 | 85.9 | 90.28 | 91.4 | 93.28 | 91.68 | 88.3 | 91.51 | Beacon Power4M4 Plus
Beacon Power | M5 | Y | N | N | 5 kW Power Conversion System | 5 |  | 89 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 14 |  |  | 46.5 | 54.5 | 58 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 89.99 | 92.65 | 93.04 | 92.33 | 89.68 | 87.6 | 90.7 | 87.66 | 91.12 | 91.61 | 90.41 | 87.83 | 85.17 | 88.85 | 86.14 | 90.07 | 90.87 | 90.27 | 87.18 | 83.21 | 88.18 | Beacon Power5M5
Beacon Power | M5 Plus | Y | N | N | 5 kW Power Conversion System with Meter | 5 |  | 90 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 14 |  |  | 46.5 | 54.5 | 58 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90.49 | 93.1 | 93.64 | 92.85 | 90.35 | 88.11 | 91.3 | 87.93 | 91.36 | 91.96 | 90.96 | 88.65 | 85.7 | 89.49 | 87.48 | 91.09 | 91.81 | 91.38 | 88.89 | 85.33 | 89.64 | Beacon Power5M5 Plus
Beijing Kinglong New Energy Technology | Sunteams 1500 [208V] | Y | N | N | 1500 W, 208 Vac Utility Interactive Inverter | 1.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 100 | 300 | 360 | 0.15 | 0.3 | 0.45 | 0.75 | 1.13 | 1.5 | 86.5 | 91.8 | 93.5 | 95 | 94.9 | 95.1 | 94.3 | 88.8 | 93.4 | 94.7 | 95.7 | 95.9 | 95.8 | 95.3 | 90.7 | 94.2 | 95.6 | 96.4 | 96.3 | 96.4 | 95.9 | Beijing Kinglong New Energy Technology1.5Sunteams 1500 [208V]
Beijing Kinglong New Energy Technology | Sunteams 1500 [240V] | Y | N | N | 1500 W, 240 Vac Utility Interactive Inverter | 1.5 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.13 |  |  | 100 | 300 | 360 | 0.15 | 0.3 | 0.45 | 0.75 | 1.13 | 1.5 | 85.9 | 91.4 | 93.2 | 94.8 | 95 | 95.2 | 94.2 | 87.5 | 92.8 | 94.3 | 95.6 | 96 | 96 | 95.2 | 90.4 | 94 | 95 | 96 | 96.4 | 96.4 | 95.8 | Beijing Kinglong New Energy Technology1.5Sunteams 1500 [240V]
Beijing Kinglong New Energy Technology | Sunteams 2000 [208V] | Y | N | N | 2000 W, 208 Vac Utility Interactive Inverter | 2 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.13 |  |  | 100 | 350 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.1 | 93.6 | 94.7 | 95.3 | 95.4 | 95.2 | 95 | 92.6 | 95 | 96 | 96.1 | 96.2 | 96 | 95.9 | 91.6 | 94.7 | 95.4 | 95.9 | 96.2 | 95.8 | 95.7 | Beijing Kinglong New Energy Technology2Sunteams 2000 [208V]
Beijing Kinglong New Energy Technology | Sunteams 2000 [240V] | Y | N | N | 2000 W, 240 Vac Utility Interactive Inverter | 2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.17 |  |  | 100 | 380 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89.6 | 93.2 | 94.5 | 95.3 | 95.6 | 95.5 | 95 | 92.2 | 94.7 | 96 | 96.5 | 96.7 | 96.4 | 96.3 | 94.1 | 95.4 | 96.2 | 96.5 | 96.5 | 96.4 | 96.3 | Beijing Kinglong New Energy Technology2Sunteams 2000 [240V]
Beijing Kinglong New Energy Technology | Sunteams 3000 [208V] | Y | N | N | 2800 W, 208 Vac Utility Interactive Inverter | 2.8 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 |  |  | 100 | 350 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 90.3 | 93.4 | 94.8 | 95.6 | 95.6 | 95.6 | 95.2 | 93.1 | 95.7 | 96.3 | 96.7 | 96.5 | 95.9 | 96.3 | 92 | 95 | 95.9 | 96.5 | 96.4 | 96 | 96.1 | Beijing Kinglong New Energy Technology2.8Sunteams 3000 [208V]
Beijing Kinglong New Energy Technology | Sunteams 3000 [240V] | Y | N | N | 2800 W, 240 Vac Utility Interactive Inverter | 2.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 |  |  | 100 | 380 | 440 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.1 | 93 | 94.5 | 95.5 | 95.8 | 95.8 | 95.2 | 93.1 | 95.9 | 96.3 | 96.9 | 96.9 | 96.9 | 96.7 | 92.7 | 95.6 | 96.7 | 96.9 | 96.9 | 96.9 | 96.6 | Beijing Kinglong New Energy Technology2.8Sunteams 3000 [240V]
Beijing Kinglong New Energy Technology | Sunteams 4000 [208V] | Y | N | N | 4000 W, 208 Vac Utility Interactive Inverter | 4 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 350 | 440 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 93.7 | 96.1 | 96.8 | 97.2 | 97.1 | 96.8 | 96.9 | 95.4 | 97.1 | 97.5 | 97.6 | 97.4 | 97.2 | 97.4 | 94 | 96.3 | 97 | 97.4 | 97.3 | 97.1 | 97.1 | Beijing Kinglong New Energy Technology4Sunteams 4000 [208V]
Beijing Kinglong New Energy Technology | Sunteams 4000 [240V] | Y | N | N | 4000 W, 240 Vac Utility Interactive Inverter | 4 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 |  |  | 100 | 380 | 440 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 93.1 | 95.8 | 96.6 | 97.3 | 97.4 | 97.2 | 97 | 95.5 | 97.1 | 97.6 | 97.9 | 97.8 | 97.5 | 97.6 | 94.6 | 96.7 | 97.4 | 97.6 | 97.6 | 97.4 | 97.4 | Beijing Kinglong New Energy Technology4Sunteams 4000 [240V]
Beijing Kinglong New Energy Technology | Sunteams 5000 [208V] | Y | N | N | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 350 | 440 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.8 | 96.1 | 96.8 | 97.1 | 96.9 | 96.4 | 96.7 | 95.3 | 97 | 97.5 | 97.5 | 97.3 | 96.8 | 97.2 | 94 | 96.3 | 96.9 | 97.2 | 97.1 | 96.7 | 96.9 | Beijing Kinglong New Energy Technology4.6Sunteams 5000 [208V]
Beijing Kinglong New Energy Technology | Sunteams 5000 [240V] | Y | N | N | 4600 W, 240 Vac Utility Interactive Inverter | 4.6 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 100 | 380 | 440 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.3 | 95.8 | 96.7 | 97.2 | 97.2 | 96.9 | 96.9 | 95.4 | 96.9 | 97.6 | 97.9 | 97.8 | 97.5 | 97.6 | 94.6 | 96.7 | 97.2 | 97.6 | 97.6 | 97.4 | 97.4 | Beijing Kinglong New Energy Technology4.6Sunteams 5000 [240V]
Beyond Building Group | SR1500TLI [208V] | Y | N | N | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.46 | 90.49 | 92.52 | 94.25 | 94.92 | 95.02 | 93.86 | 85.04 | 91.04 | 93.19 | 94.79 | 95.41 | 95.53 | 94.38 | 85.31 | 91.19 | 93.54 | 95.02 | 95.55 | 95.76 | 94.58 | Beyond Building Group1.55SR1500TLI [208V]
Beyond Building Group | SR1500TLI [240V] | Y | N | N | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.62 | 90.46 | 92.57 | 94.42 | 95.07 | 95.25 | 93.99 | 84.89 | 90.97 | 93.04 | 94.81 | 95.51 | 95.73 | 94.42 | 85.22 | 91.38 | 93.44 | 95.12 | 95.65 | 95.93 | 94.66 | Beyond Building Group1.55SR1500TLI [240V]
Beyond Building Group | SR2000TLI [208V] | Y | N | N | 2 kW, 208 Vac Utility Interactive Inverter | 2.06 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.29 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 88.28 | 93.12 | 94.41 | 95.27 | 95.43 | 95.37 | 94.87 | 89.63 | 93.68 | 94.91 | 95.73 | 95.84 | 95.8 | 95.34 | 89.74 | 94.01 | 95.11 | 96.13 | 96.38 | 96.07 | 95.77 | Beyond Building Group2.06SR2000TLI [208V]
Beyond Building Group | SR2000TLI [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter | 2.06 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 86.91 | 92.14 | 93.78 | 94.94 | 95.3 | 95.37 | 94.55 | 87.84 | 92.87 | 94.26 | 95.56 | 95.79 | 95.73 | 95.09 | 88.1 | 93.05 | 94.37 | 95.71 | 96 | 95.94 | 95.28 | Beyond Building Group2.06SR2000TLI [240V]
Beyond Building Group | SR3000TLI [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.57 | 94.41 | 95.16 | 95.47 | 95.31 | 94.62 | 95.1 | 92.05 | 94.92 | 95.58 | 95.89 | 95.76 | 95.37 | 95.56 | 92.22 | 95.17 | 95.79 | 96.25 | 95.93 | 95.8 | 95.78 | Beyond Building Group3SR3000TLI [208V]
Beyond Building Group | SR3000TLI [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.301 | 0.602 | 0.903 | 1.505 | 2.258 | 3.01 | 90 | 93.9 | 94.85 | 95.4 | 95.31 | 94.83 | 94.97 | 90.64 | 94.34 | 95.34 | 95.79 | 95.87 | 95.6 | 95.49 | 91 | 94.59 | 95.44 | 95.97 | 96.01 | 95.77 | 95.65 | Beyond Building Group3.01SR3000TLI [240V]
Beyond Building Group | SR4000TLI [208V] | Y | N | N | 4 kW, 208 Vac Utility Interactive Inverter | 3.98 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.398 | 0.796 | 1.194 | 1.99 | 2.985 | 3.98 | 90.53 | 94.32 | 95.17 | 95.44 | 95.41 | 95.16 | 95.13 | 91.58 | 94.87 | 95.63 | 96.05 | 96 | 95.45 | 95.7 | 91.82 | 95.03 | 95.8 | 96.45 | 96.31 | 95.76 | 96.01 | Beyond Building Group3.98SR4000TLI [208V]
Beyond Building Group | SR4000TLI [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.399 | 0.798 | 1.197 | 1.995 | 2.993 | 3.99 | 90.55 | 94.3 | 95.24 | 95.69 | 95.74 | 95.56 | 95.38 | 91.53 | 94.95 | 95.81 | 96.33 | 96.33 | 96.05 | 95.99 | 91.95 | 95.23 | 95.96 | 96.4 | 96.48 | 96.25 | 96.15 | Beyond Building Group3.99SR4000TLI [240V]
Beyond Building Systems | SR2000TL-US-240 [240V] | Y | N | N | 2110 W, 240 Vac Utility Interactive Inverter | 2.11 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.21 | 0.42 | 0.63 | 1.06 | 1.58 | 2.11 | 85.3 | 91.6 | 92.9 | 94.3 | 94.6 | 94.5 | 93.8 | 82.1 | 91.9 | 94.2 | 95.6 | 96.1 | 96.4 | 95 | 82.2 | 91.5 | 93.8 | 95.6 | 96.1 | 96.3 | 95 | Beyond Building Systems2.11SR2000TL-US-240 [240V]
Beyond Building Systems | SR3000TL-US-240 [240V] | Y | N | N | 3180 W, 240 Vac Utility Interactive Inverter | 3.18 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.32 | 0.64 | 0.95 | 1.59 | 2.39 | 3.18 | 88.8 | 92.9 | 94.1 | 94.6 | 94.3 | 94 | 94 | 88.8 | 94.4 | 95.3 | 96.2 | 96.3 | 95.9 | 95.7 | 89.5 | 93.7 | 95.3 | 96.2 | 96.3 | 96.1 | 95.7 | Beyond Building Systems3.18SR3000TL-US-240 [240V]
Beyond Building Systems | SR4200TL-US-240 [240V] | Y | N | N | 4100 W, 240 Vac Utility Interactive Inverter | 4.16 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.42 | 0.83 | 1.25 | 2.08 | 3.12 | 4.16 | 90.6 | 93.8 | 94.5 | 94.8 | 94.6 | 94.2 | 94.4 | 91.4 | 95 | 95.7 | 96.1 | 96.2 | 95.9 | 95.9 | 90.7 | 94.7 | 95.5 | 96.1 | 96.1 | 95.9 | 95.7 | Beyond Building Systems4.16SR4200TL-US-240 [240V]
Beyond Building Systems | SR5000TL-US-240 [240V] | Y | N | N | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8 | Beyond Building Systems5.24SR5000TL-US-240 [240V]
Canadian Solar Inc. | CM-240-EC | Y | N | N | 1-phase Microinverter | 0.24 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 | Canadian Solar Inc.0.24CM-240-EC |  | 2017-10-03
Canadian Solar Inc. | CS6P-245M-EA | Y | N | N | 1-phase Microinverter | 0.24 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 | Canadian Solar Inc.0.24CS6P-245M-EA |  | 2017-10-03
Canadian Solar Inc. | CS6P-245P-EA | Y | N | N | 1-phase Microinverter | 0.24 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 | Canadian Solar Inc.0.24CS6P-245P-EA |  | 2017-10-03
Canadian Solar Inc. | CS6P-250M-EA | Y | N | N | 1-phase Microinverter | 0.24 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 | Canadian Solar Inc.0.24CS6P-250M-EA |  | 2017-10-03
Canadian Solar Inc. | CS6P-250P-EA | Y | N | N | 1-phase Microinverter | 0.24 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 | Canadian Solar Inc.0.24CS6P-250P-EA |  | 2017-10-03
Canadian Solar Inc. | CS6P-255M-EA | Y | N | N | 1-phase Microinverter | 0.24 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 | Canadian Solar Inc.0.24CS6P-255M-EA |  | 2017-10-03
Canadian Solar Inc. | CS6P-255P-EA | Y | N | N | 1-phase Microinverter | 0.24 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 | Canadian Solar Inc.0.24CS6P-255P-EA |  | 2017-10-03
Canadian Solar Inc. | CS6P-260M-EA | Y | N | N | 1-phase Microinverter | 0.24 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 | Canadian Solar Inc.0.24CS6P-260M-EA |  | 2017-10-03
Canadian Solar Inc. | CS6P-260P-EA | Y | N | N | 240 W, 1-phase Microinverter | 0.24 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 | Canadian Solar Inc.0.24CS6P-260P-EA |  | 2017-10-03
Canadian Solar Inc. | CM-260-EC | Y | N | N | 1-phase Microinverter | 0.26 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 |  |  | 24 | 29 | 35 | 0.03 | 0.05 | 0.08 | 0.13 | 0.2 | 0.26 | 93 | 95.2 | 95.6 | 96.4 | 96.2 | 95.7 | 96 | 91.2 | 94.6 | 95.3 | 96.2 | 96.3 | 96 | 95.9 | 90.2 | 93.6 | 94.8 | 95.7 | 96.2 | 96.1 | 95.5 | Canadian Solar Inc.0.26CM-260-EC |  | 2017-10-03
Canadian Solar Inc. | CM-280-EC | Y | N | N | 1-phase Microinverter | 0.28 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 |  |  | 24 | 29 | 35 | 0.03 | 0.06 | 0.08 | 0.14 | 0.21 | 0.28 | 93.3 | 95.3 | 95.6 | 96.4 | 96.1 | 95.5 | 95.9 | 91.4 | 94.7 | 95.4 | 96.4 | 96.3 | 95.9 | 95.9 | 90.5 | 93.9 | 94.8 | 95.8 | 96.1 | 96 | 95.6 | Canadian Solar Inc.0.28CM-280-EC |  | 2017-10-03
Canadian Solar Inc. | CM-300-EC | Y | N | N | 1-phase Microinverter | 0.3 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 |  |  | 24 | 29 | 35 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 93.6 | 95.4 | 95.7 | 96.4 | 95.9 | 95.3 | 95.9 | 91.9 | 94.8 | 95.4 | 96.4 | 96.2 | 95.8 | 95.9 | 91.1 | 94.1 | 95 | 96 | 96.1 | 96 | 95.7 | Canadian Solar Inc.0.3CM-300-EC |  | 2017-10-03
Canadian Solar Inc. | CSI-3000TL-CT [208V] | Y | N | N | Utility Interactive Inverter | 2.86 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.29 | 0.57 | 0.86 | 1.43 | 2.15 | 2.86 | 91.1 | 94.1 | 95.1 | 95.6 | 95.6 | 95 | 95.3 | 93.4 | 95.7 | 96.7 | 97.1 | 97 | 96.6 | 96.8 | 93 | 95.4 | 96.4 | 96.9 | 96.8 | 96.4 | 96.6 | Canadian Solar Inc.2.86CSI-3000TL-CT [208V] |  | 2017-10-03
Canadian Solar Inc. | CSI-3000TL-CT [240V] | Y | N | N | Utility Interactive Inverter | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.5 | 94.5 | 95.5 | 96 | 96 | 95.6 | 95.7 | 94.1 | 96.2 | 97.1 | 97.5 | 97.4 | 97.1 | 97.2 | 93.8 | 95.8 | 96.8 | 97.3 | 97.3 | 97 | 97 | Canadian Solar Inc.3CSI-3000TL-CT [240V] |  | 2017-10-03
Canadian Solar Inc. | CSI-4000TL-CT [208V] | Y | N | N | Utility Interactive Inverter | 3.81 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.38 | 0.76 | 1.14 | 1.91 | 2.86 | 3.81 | 91.4 | 94.6 | 95.4 | 96 | 95.8 | 95.2 | 95.5 | 93.7 | 96.2 | 97 | 97.3 | 97.2 | 96.8 | 97 | 93.1 | 95.6 | 96.5 | 97.1 | 97 | 96.6 | 96.7 | Canadian Solar Inc.3.81CSI-4000TL-CT [208V] |  | 2017-10-03
Canadian Solar Inc. | CSI-4000TL-CT [240V] | Y | N | N | Utility Interactive Inverter | 4.02 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.4 | 0.8 | 1.21 | 2.01 | 3.02 | 4.02 | 92.1 | 94.9 | 95.8 | 96.3 | 96.2 | 95.8 | 95.9 | 94.2 | 96.6 | 97.2 | 97.7 | 97.6 | 97.4 | 97.4 | 93.4 | 95.9 | 96.8 | 97.4 | 97.5 | 97.1 | 97.1 | Canadian Solar Inc.4.02CSI-4000TL-CT [240V] |  | 2017-10-03
Canadian Solar Inc. | CSI-5000TL-CT [208V] | Y | N | N | Utility Interactive Inverter | 4.61 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.7 |  |  | 100 | 390 | 470 | 0.46 | 0.92 | 1.38 | 2.31 | 3.46 | 4.61 | 93 | 95.3 | 95.9 | 96.1 | 95.7 | 95 | 95.7 | 94.8 | 96.8 | 97.3 | 97.5 | 97.2 | 96.6 | 97.1 | 94.6 | 96.6 | 97.1 | 97.3 | 97.1 | 96.5 | 97 | Canadian Solar Inc.4.61CSI-5000TL-CT [208V] |  | 2017-10-03
Canadian Solar Inc. | CSI-5000TL-CT [240V] | Y | N | N | Utility Interactive Inverter | 5 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.6 | 95.7 | 96.1 | 96.5 | 96.1 | 95.4 | 96 | 95.4 | 97.1 | 97.6 | 97.8 | 97.6 | 97.1 | 97.5 | 95 | 96.9 | 97.4 | 97.6 | 97.4 | 97.1 | 97.3 | Canadian Solar Inc.5CSI-5000TL-CT [240V] |  | 2017-10-03
Canadian Solar Inc. | CSI-6000TL-CT [208V] | Y | N | N | 5.5 kW, 208 Vac Utility Interactive Inverter | 5.5 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 380 | 470 | 0.55 | 1.1 | 1.65 | 2.75 | 4.125 | 5.5 | 92.1 | 94.8 | 95.5 | 96.1 | 96 | 95.5 | 95.7 | 93.6 | 96.1 | 96.8 | 97.3 | 97.2 | 96.8 | 97 | 93 | 95.7 | 96.5 | 97 | 96.9 | 96.6 | 96.7 | Canadian Solar Inc.5.5CSI-6000TL-CT [208V] |  | 2017-10-03
Canadian Solar Inc. | CSI-6000TL-CT [240V] | Y | N | N | 6.0 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 380 | 470 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 95.3 | 95.9 | 96.5 | 96.4 | 95.9 | 96.1 | 94.3 | 96.6 | 97.3 | 97.7 | 97.6 | 97.3 | 97.4 | 93.7 | 96.1 | 96.9 | 97.4 | 97.4 | 97.2 | 97.1 | Canadian Solar Inc.6CSI-6000TL-CT [240V] |  | 2017-10-03
Canadian Solar Inc. | CSI-23KTL-CT [480V] | Y | N | N | 23 kW, 480 Vac Utility Interactive Inverter | 23 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 480 | 720 | 800 | 2.3 | 4.6 | 6.9 | 11.5 | 17.25 | 23 | 95.8 | 97 | 97.2 | 97.4 | 97.4 | 97.3 | 97.3 | 97 | 98.2 | 98.4 | 98.6 | 98.5 | 98.4 | 98.4 | 96.6 | 98 | 98.2 | 98.4 | 98.4 | 98.3 | 98.3 | Canadian Solar Inc.23CSI-23KTL-CT [480V] |  | 2017-10-03
Canadian Solar Inc. | CSI-25KTL-GS-FL [480V] | N | Y | Y | 25 kW, 480 Vac, Fanless, 3-phase Utility Interactive Inverter | 25.05 | 480 | 98 | [01/31/2018] | [1D] | 2018-11-01 | N | N | Multiple Listing of Ningbo Ginlong Technologies Co., Ltd. Solis-25K-US | 14 |  |  | 580 | 650 | 780 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 97.1 | 97.4 | 97.6 | 97.9 | 98 | 97.8 | 97.9 | 97.1 | 97.3 | 97.6 | 97.8 | 98.3 | 97.6 | 98 | 97.2 | 97.4 | 97.7 | 97.8 | 98 | 97.5 | 97.9 | Canadian Solar Inc.25.05CSI-25KTL-GS-FL [480V] | 2018-02-15 | 2018-11-01
Canadian Solar Inc. | CSI-28KTL-CT [480V] | Y | N | N | 28 kW, 480 Vac Utility Interactive Inverter | 28 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 500 | 725 | 800 | 2.8 | 5.6 | 8.4 | 14 | 21 | 28 | 96.3 | 97.2 | 97.4 | 97.5 | 97.4 | 97.2 | 97.3 | 97.5 | 98.3 | 98.5 | 98.5 | 98.4 | 98.2 | 98.4 | 97.2 | 98.1 | 98.4 | 98.4 | 98.3 | 98.1 | 98.3 | Canadian Solar Inc.28CSI-28KTL-CT [480V] |  | 2018-11-01
Canadian Solar Inc. | CSI-30KTL-GS-FL [480V] | N | Y | Y | 30 kW, 480 Vac, Fanless, 3-phase Utility Interactive Inverter | 30.05 | 480 | 98 | [01/31/2018] | [1D] | 2018-11-01 | N | N | Multiple Listing of Ningbo Ginlong Technologies Co., Ltd. Solis-30K-US | 15 |  |  | 580 | 650 | 780 | 3 | 6 | 9 | 15 | 22.5 | 30 | 97.1 | 97.9 | 97.9 | 98.3 | 97.5 | 97.9 | 97.8 | 97.4 | 98.1 | 98.1 | 98.4 | 98.1 | 97.9 | 98.1 | 97.1 | 97.9 | 98 | 98.3 | 98 | 97.8 | 98 | Canadian Solar Inc.30.05CSI-30KTL-GS-FL [480V] | 2018-02-15 | 2018-11-01
Canadian Solar Inc. | CSI-36KTL-CT | Y | N | N | 36 kVA, 3-phase, transformerless Utility Interactive Inverter | 36 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of CHINT POWER SYSTEMS America CPS SCA36KTL-DO/US and Solectria Renewables,LLC PVI 36TL-479 | 0 |  |  | 540 | 730 | 800 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 95.5 | 96.8 | 97.2 | 97.5 | 97.5 | 97.3 | 97.3 | 97.4 | 98.3 | 98.5 | 98.5 | 98.5 | 98.3 | 98.4 | 97.1 | 98 | 98.3 | 98.4 | 98.3 | 98.2 | 98.3 | Canadian Solar Inc.36CSI-36KTL-CT |  | 2018-11-01
Canadian Solar Inc. | CSI-36KTL-CT [480V] | N | Y | Y | 36 kVA , 480 Vac, 3-phase Grid Support Utility Interactive Inverter, non-isolated, 1000 Vdc | 36 | 480 | 98 | [8/2/2017] | [V0.60] | 2018-10-15 | N | N | Multiple Listing of CHINT POWER SYSTEMS America CPS SCA36KTL-DO/US and Solectria Renewables,LLC PVI 36TL-480 | 0 |  |  | 540 | 730 | 800 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 95.5 | 96.8 | 97.2 | 97.5 | 97.5 | 97.3 | 97.3 | 97.4 | 98.3 | 98.5 | 98.5 | 98.5 | 98.3 | 98.4 | 97.1 | 98 | 98.3 | 98.4 | 98.3 | 98.2 | 98.3 | Canadian Solar Inc.36CSI-36KTL-CT [480V] | 2017-10-01 | 2018-11-01
Canadian Solar Inc. | CSI-36KTL-GS-FL [480V] | N | Y | Y | 36 kW, 480 Vac, Fanless, 3-phase Utility Interactive Inverter | 36.05 | 480 | 98 | [01/31/2018] | [1D] | 2018-11-01 | N | N | Multiple Listing of Ningbo Ginlong Technologies Co., Ltd. Solis-36K-US | 15 |  |  | 580 | 650 | 780 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 97.3 | 98.2 | 98.1 | 98.4 | 97.6 | 98.1 | 97.9 | 97.7 | 98.3 | 98.3 | 98.4 | 98.3 | 98.1 | 98.3 | 97.4 | 98.1 | 98.2 | 98.3 | 98.2 | 98.1 | 98.2 | Canadian Solar Inc.36.05CSI-36KTL-GS-FL [480V] | 2018-02-15 | 2018-11-01
Canadian Solar Inc. | CSI-40KTL-GS [480V] | N | Y | Y | 40 kW, 480 Vac, 3-phase Utility Interactive Inverter, with external fan | 40.05 | 480 | 98.5 | [01/31/2018] | [1D] | 2018-11-01 | N | N | Multiple Listing of Ningbo Ginlong Technologies Co., Ltd. Solis-40K-US-F | 1 |  |  | 580 | 650 | 780 | 4 | 8 | 12 | 20 | 30 | 40 | 97.5 | 98 | 98.1 | 98.2 | 98.1 | 97.7 | 98.1 | 97.8 | 98.3 | 98.4 | 98.6 | 98.5 | 98.3 | 98.5 | 97.6 | 98.1 | 98.2 | 98.4 | 98.3 | 98 | 98.3 | Canadian Solar Inc.40.05CSI-40KTL-GS [480V] | 2018-02-15 | 2018-11-01
Canadian Solar Inc. | CSI-40KTL-GS-FL [480V] | N | Y | Y | 40 kW, 480 Vac, Fanless, 3-phase Utility Interactive Inverter | 40.05 | 480 | 98.5 | [01/31/2018] | [1D] | 2018-11-01 | N | N | Multiple Listing of Ningbo Ginlong Technologies Co., Ltd. Solis-40K-US | 1 |  |  | 580 | 650 | 780 | 4 | 8 | 12 | 20 | 30 | 40 | 97.5 | 98 | 98.1 | 98.2 | 98.1 | 98 | 98.1 | 97.9 | 98.3 | 98.4 | 98.7 | 98.6 | 98.3 | 98.5 | 97.6 | 98.2 | 98.2 | 98.4 | 98.3 | 98.2 | 98.3 | Canadian Solar Inc.40.05CSI-40KTL-GS-FL [480V] | 2018-02-15 | 2018-11-01
Canadian Solar Inc. | CSI-50KTL-CT [480V] | Y | Y | Y | 50 kVA , 480 Vac, 3-phase Grid Support Utility Interactive Inverter, non-isolated, 1000Vdc | 50 | 480 | 98.5 | [7/6/2017] | [V5.00] | 2018-10-15 | N | N | Multiple Listing of CHINT POWER SYSTEMS America CPS SCA50KTL-DO/US and Solectria Renewables,LLC PVI 50TL-480 | 0.88 |  |  | 480 | 730 | 850 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95.6089 | 96.843 | 97.4816 | 97.8549 | 97.8327 | 97.6904 | 97.6497 | 98.0184 | 98.6275 | 98.7749 | 98.8023 | 98.7196 | 98.6108 | 98.7055 | 97.7339 | 98.4586 | 98.6223 | 98.6594 | 98.5869 | 98.4698 | 98.56 | Canadian Solar Inc.50CSI-50KTL-CT [480V] | 2017-10-01 | 2018-11-01
Canadian Solar Inc. | CSI-60KTL-CT [480V] | Y | Y | Y | 60 kVA , 480 Vac, 3-phase Grid Support Utility Interactive Inverter, non-isolated, 1000Vdc | 60 | 480 | 98.5 | [7/6/2017] | [V5.00] | 2018-10-15 | N | N | Multiple Listing of CHINT POWER SYSTEMS America CPS SCA60KTL-DO/US and Solectria Renewables,LLC PVI 60TL-480 | 0.88 |  |  | 540 | 730 | 850 | 6 | 12 | 18 | 30 | 45 | 60 | 96.5104 | 97.4761 | 97.8852 | 98.0525 | 97.9434 | 97.7271 | 97.8678 | 98.2227 | 98.7116 | 98.7911 | 98.779 | 98.6548 | 98.4981 | 98.6749 | 98.0008 | 98.5506 | 98.6633 | 98.6588 | 98.5228 | 98.3541 | 98.5403 | Canadian Solar Inc.60CSI-60KTL-CT [480V] | 2017-10-01 | 2018-11-01
Canadian Solar Incorporated. | CSI-50KTL-GS [480V] | N | Y | Y | 50 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, | 50.083 | 480 | 98.5 | [01/08/2018] | [19/01] | 2018-11-01 | N | N | Multiple Listing of Ningbo Ginlong Technologies Co., LTD Solis-50K-US-F | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.7 | 98.4 | 98.5 | 98.6 | 98.5 | 98.4 | 98.4 | 97.8 | 98.5 | 98.6 | 98.7 | 98.5 | 98.4 | 98.5 | 97.9 | 98.6 | 98.7 | 98.8 | 98.6 | 98.5 | 98.6 | Canadian Solar Incorporated50.083CSI-50KTL-GS [480V] [SI1] | 2018-02-01 | 2018-11-01
Canadian Solar Incorporated. | CSI-50KTL-GS-B [480V] | N | Y | Y | 50 kW, 480 Vac, Seperated Wiring Box, 3-phase Grid Support Utility Interactive Inverter, | 50.083 | 480 | 98.5 | [01/08/2018] | [19/01] | 2018-11-01 | N | N | Multiple Listing of Ningbo Ginlong Technologies Co., LTD Solis-50K-US-F-SW | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.7362 | 98.4442 | 98.4559 | 98.5822 | 98.45 | 98.3475 | 98.4445 | 97.7983 | 98.5313 | 98.5521 | 98.7004 | 98.5123 | 98.3959 | 98.5232 | 97.8768 | 98.5781 | 98.6506 | 98.7596 | 98.5678 | 98.4644 | 98.5857 | Canadian Solar Incorporated.50.083CSI-50KTL-GS-B [480V] [SI1] | 2018-02-01 | 2018-11-01
Canadian Solar Incorporated. | CSI-50KTL-GS-FLB [480V] | N | Y | Y | 50 kW, 480 Vac, Seperated Wiring Box, Fanless, 3-phase Grid Support Utility Interactive Inverter, | 50.083 | 480 | 98.5 | [01/08/2018] | [19/01] | 2018-11-01 | N | N | Multiple Listing of Ningbo Ginlong Technologies Co., LTD Solis-50K-US-SW | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.5167 | 98.5279 | 98.441 | 98.5562 | 98.3221 | 98.4464 | 98.3698 | 97.7469 | 98.5505 | 98.5222 | 98.6539 | 98.4338 | 98.4888 | 98.4718 | 97.9805 | 98.7 | 98.8047 | 98.7919 | 98.5679 | 98.5006 | 98.6231 | Canadian Solar Incorporated.50.083CSI-50KTL-GS-FLB [480V] [SI1] | 2018-02-01 | 2018-11-01
Canadian Solar Incorporated. | CSI-50KTL-GS-FL [480V] | N | Y | Y | 50 kW, 480 Vac, Fanless, 3-phase Grid Support Utility Interactive Inverter, | 50.084 | 480 | 98.5 | [01/08/2018] | [19/01] | 2018-11-01 | N | N | Multiple Listing of Ningbo Ginlong Technologies Co., LTD Solis-50K-US | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.5 | 98.5 | 98.4 | 98.6 | 98.3 | 98.5 | 98.4 | 97.8 | 98.6 | 98.5 | 98.7 | 98.4 | 98.5 | 98.5 | 98 | 98.7 | 98.8 | 98.8 | 98.6 | 98.5 | 98.6 | Canadian Solar Incorporated50.084CSI-50KTL-GS-FL [480V] [SI1] | 2018-02-01 | 2018-11-01
Canadian Solar Incorporated. | CSI-60KTL-GS [480V] | N | Y | Y | 60 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, | 60.086 | 480 | 98.5 | [01/08/2018] | [19/01] | 2018-11-01 | N | N | Multiple Listing of Ningbo Ginlong Technologies Co., LTD Solis-60K-US-F | 1 |  |  | 580 | 650 | 720 | 6 | 12 | 18 | 30 | 45 | 60 | 97.7 | 98.3 | 98.4 | 98.6 | 98.4 | 98.2 | 98.4 | 97.8 | 98.5 | 98.5 | 98.6 | 98.5 | 98.3 | 98.5 | 97.9 | 98.5 | 98.6 | 98.7 | 98.6 | 98.5 | 98.6 | Canadian Solar Incorporated60.086CSI-60KTL-GS [480V] [SI1] | 2018-02-01 | 2018-11-01
Canadian Solar Incorporated. | CSI-60KTL-GS-B [480V] | N | Y | Y | 60 kW, 480 Vac, Seperated Wiring Box, 3-phase Grid Support Utility Interactive Inverter, | 60.086 | 480 | 98.5 | [01/08/2018] | [19/01] | 2018-11-01 | N | N | Multiple Listing of Ningbo Ginlong Technologies Co., LTD Solis-60K-US-F-SW | 1 |  |  | 580 | 650 | 720 | 6 | 12 | 18 | 30 | 45 | 60 | 97.7251 | 98.3108 | 98.4189 | 98.5501 | 98.3711 | 98.2238 | 98.3782 | 97.8227 | 98.4496 | 98.5404 | 98.6262 | 98.499 | 98.3294 | 98.4926 | 97.8622 | 98.5252 | 98.5865 | 98.7 | 98.5526 | 98.4499 | 98.5535 | Canadian Solar Incorporated.60.086CSI-60KTL-GS-B [480V] [SI1] | 2018-02-01 | 2018-11-01
Canadian Solar Incorporated. | CSI-66KTL-GS [480V] | N | Y | Y | 66 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter. | 66.07 | 480 | 98.5 | [01/08/2018] | [19/01] | 2018-11-01 | N | N | Multiple Listing of Ningbo Ginlong Technologies Co., LTD Solis-66K-US-F | 1 |  |  | 580 | 650 | 720 | 6.6 | 13.2 | 19.8 | 33 | 49.5 | 66 | 97.6 | 98.4 | 98.5 | 98.6 | 98.4 | 98.3 | 98.4 | 97.7 | 98.5 | 98.6 | 98.7 | 98.5 | 98.4 | 98.5 | 97.8 | 98.7 | 98.7 | 98.8 | 98.6 | 98.5 | 98.6 | Canadian Solar Incorporated66.07CSI-66KTL-GS [480V] [SI1] | 2018-02-01 | 2018-11-01
Canadian Solar Incorporated. | CSI-66KTL-GS-B [480V] | N | Y | Y | 66 kW, 480 Vac, Seperated Wiring Box, 3-phase Grid Support Utility Interactive Inverter | 66.07 | 480 | 98.5 | [01/08/2018] | [19/01] | 2018-11-01 | N | N | Multiple Listing of Ningbo Ginlong Technologies Co., LTD Solis-66K-US-F-SW | 1 |  |  | 580 | 650 | 720 | 6.6 | 13.2 | 19.8 | 33 | 49.5 | 66 | 97.5717 | 98.3763 | 98.4763 | 98.5633 | 98.4214 | 98.3118 | 98.416 | 97.7441 | 98.5006 | 98.5537 | 98.7042 | 98.4989 | 98.3902 | 98.513 | 97.7721 | 98.6713 | 98.6538 | 98.7738 | 98.5561 | 98.4918 | 98.5847 | Canadian Solar Incorporated.66.07CSI-66KTL-GS-B [480V] [SI1] | 2018-02-01 | 2018-11-01
Carlo Gavazzi | ISGA 1 22 [240V] | Y | N | N | 2110 W, 240 Vac Utility Interactive Inverter | 2.11 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.21 | 0.42 | 0.63 | 1.06 | 1.58 | 2.11 | 85.3 | 91.6 | 92.9 | 94.3 | 94.6 | 94.5 | 93.8 | 82.1 | 91.9 | 94.2 | 95.6 | 96.1 | 96.4 | 95 | 82.2 | 91.5 | 93.8 | 95.6 | 96.1 | 96.3 | 95 | Carlo Gavazzi2.11ISGA 1 22 [240V]
Carlo Gavazzi | ISGA 1 33 [240V] | Y | N | N | 3180 W, 240 Vac Utility Interactive Inverter | 3.18 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.32 | 0.64 | 0.95 | 1.59 | 2.39 | 3.18 | 88.8 | 92.9 | 94.1 | 94.6 | 94.3 | 94 | 94 | 88.8 | 94.4 | 95.3 | 96.2 | 96.3 | 95.9 | 95.7 | 89.5 | 93.7 | 95.3 | 96.2 | 96.3 | 96.1 | 95.7 | Carlo Gavazzi3.18ISGA 1 33 [240V]
Carlo Gavazzi | ISGA 1 42 [240V] | Y | N | N | 4100 W, 240 Vac Utility Interactive Inverter | 4.16 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.42 | 0.83 | 1.25 | 2.08 | 3.12 | 4.16 | 90.6 | 93.8 | 94.5 | 94.8 | 94.6 | 94.2 | 94.4 | 91.4 | 95 | 95.7 | 96.1 | 96.2 | 95.9 | 95.9 | 90.7 | 94.7 | 95.5 | 96.1 | 96.1 | 95.9 | 95.7 | Carlo Gavazzi4.16ISGA 1 42 [240V]
Carlo Gavazzi | ISGA 1 53 [240V] | Y | N | N | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8 | Carlo Gavazzi5.24ISGA 1 53 [240V]
CFM Equipment Distributors | Green Power 1100 [120V] | Y | N | N | 1100 W, 120 Vac Utility Interactive Inverter | 1.1 | 120 | 90.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 182 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 81.8 | 89 | 90.9 | 92.1 | 92.4 | 92.5 | 91.6 | 79.9 | 88 | 90.1 | 91.7 | 92.2 | 92.3 | 91.1 | 74.8 | 84.7 | 87.8 | 90 | 90.8 | 91.1 | 89.3 | CFM Equipment Distributors1.1Green Power 1100 [120V]
CFM Equipment Distributors | Green Power 2000 [240V] | Y | N | N | 2000 W, 240 Vac Utility Interactive Inverter | 2 | 240 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 199 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.3 | 91.7 | 92.6 | 93.5 | 93.2 | 93 | 92.9 | 85.7 | 90.8 | 92.1 | 92.9 | 92.9 | 92.6 | 92.4 | 82.4 | 88.8 | 90.5 | 91.6 | 91.8 | 91.6 | 91.1 | CFM Equipment Distributors2Green Power 2000 [240V]
CFM Equipment Distributors | Green Power 2500 [240V] | Y | N | N | 2500 W, 240 Vac Utility Interactive Inverter | 2.5 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2 | CFM Equipment Distributors2.5Green Power 2500 [240V]
CFM Equipment Distributors | Green Power 3000 [240V] | Y | N | N | 3000 W, 240 Vac Utility Interactive Inverter | 3 | 240 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.63 |  |  | 100 | 222.5 | 380 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 88.9 | 92.9 | 93.8 | 94.3 | 94.2 | 93.9 | 93.9 | 87.9 | 92.5 | 93.5 | 94.1 | 94 | 93.8 | 93.7 | 84.9 | 90.9 | 92.4 | 93.3 | 93.2 | 93 | 92.7 | CFM Equipment Distributors3Green Power 3000 [240V]
CFM Equipment Distributors | Green Power 3500 [240V] | Y | N | N | 3500 W, 240 Vac Utility Interactive Inverter | 3.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.86 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5 | CFM Equipment Distributors3.5Green Power 3500 [240V]
CFM Equipment Distributors | Green Power 4600 [208V] | Y | N | N | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 |  |  | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95 | CFM Equipment Distributors4.6Green Power 4600 [208V]
CFM Equipment Distributors | Green Power 4800 [240V] | Y | N | N | 4800 W, 240 Vac Utility Interactive Inverter | 4.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.1 |  |  | 100 | 263 | 400 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 86.8 | 93.5 | 95.5 | 97 | 97.2 | 97.1 | 96.4 | 85.5 | 92.9 | 95 | 96.7 | 96.9 | 96.8 | 96 | 84.5 | 91.5 | 93.9 | 95.9 | 96.2 | 96.1 | 95.1 | CFM Equipment Distributors4.8Green Power 4800 [240V]
CFM Equipment Distributors | Green Power 5200 [240V] | Y | N | N | 5200 W, 240 Vac Utility Interactive Inverter | 5.2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 |  |  | 100 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5 | CFM Equipment Distributors5.2Green Power 5200 [240V]
Changzhou Nesl Solartech | DJ-230P-ST15 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | [33 empty] | Changzhou Nesl Solartech0.225DJ-230P-ST15 [240V]
Changzhou Nesl Solartech | DJ-235P-ST15 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | [33 empty] | Changzhou Nesl Solartech0.225DJ-235P-ST15 [240V]
Changzhou Nesl Solartech | DJ-240DA/C-ST15 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | [33 empty] | Changzhou Nesl Solartech0.225DJ-240DA/C-ST15 [240V]
Changzhou Nesl Solartech | DJ-240P-ST15 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | [33 empty] | Changzhou Nesl Solartech0.225DJ-240P-ST15 [240V]
Changzhou Nesl Solartech | DJ-245DA/C-ST15 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | [33 empty] | Changzhou Nesl Solartech0.225DJ-245DA/C-ST15 [240V]
Changzhou Nesl Solartech | DJ-250DA/C-ST15 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | [33 empty] | Changzhou Nesl Solartech0.225DJ-250DA/C-ST15 [240V]
Changzhou Nesl Solartech | DJ-255D/C-ST15 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N |  | This component is specific to ACPV modules and is not available as an individual unit. | [33 empty] | Changzhou Nesl Solartech0.225DJ-255D/C-ST15 [240V]
Chiconypower | MU300SAP2 [240V] | Y | N | N | 300 W, 240 Vac Utility Interactive Inverter | 0.29 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.1 |  |  | 26 | 31 | 43 | 0.03 | 0.06 | 0.09 | 0.14 | 0.22 | 0.29 | 92.1 | 94.4 | 95 | 95.7 | 96.3 | 95.9 | 95.7 | 91.6 | 95.1 | 94.8 | 96.5 | 96.5 | 96.5 | 96.1 | 89.9 | 94.3 | 95.3 | 96.3 | 96.2 | 96.2 | 95.8 | Chiconypower0.29MU300SAP2 [240V]
Chilicon Power LLC | CP-250-60-208/240-MC4 [208V] | Y | N | N | 250 W, 208 Vac Utility Interactive Inverter | 0.22 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 |  |  | 24 | 28 | 35 | 0.22 | 0.44 | 0.66 | 1.1 | 1.65 | 2.2 | 93 | 95.7 | 96.2 | 96.3 | 96 | 95.3 | 95.9 | 91.7 | 95.2 | 96.1 | 96.4 | 96.2 | 95.7 | 95.9 | 89 | 93.8 | 95.2 | 96.2 | 96.2 | 95.9 | 95.7 | Chilicon Power LLC0.22CP-250-60-208/240-MC4 [208V] |  | 2017-12-15
Chilicon Power LLC | CP-250-60-208/240-MC4 [240V] | Y | N | N | 250 W, 240 Vac Utility Interactive Inverter | 0.22 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.08 |  |  | 24 | 28 | 35 | 0.22 | 0.44 | 0.66 | 1.1 | 1.65 | 2.2 | 93.1 | 95.6 | 96.3 | 96.5 | 96.2 | 95.6 | 96.1 | 92 | 95.4 | 96.3 | 96.6 | 96.5 | 96.1 | 96.2 | 89.2 | 94 | 95.4 | 96.5 | 96.6 | 96.3 | 96 | Chilicon Power LLC0.22CP-250-60-208/240-MC4 [240V] |  | 2017-12-15
Chilicon Power LLC | CP-250E-60/72-208/240-MC4 [208V] | Y | Y | Y | 277 W, 208 Vac Grid Support Utility Interactive Inverter | 0.277 | 208 | 95.5 | [11/15/2017] | [3353] | 2018-10-15 | N | Y |  | 0.02 |  |  | 28 | 30 | 32 | 0.03 | 0.06 | 0.08 | 0.14 | 0.21 | 0.28 | 92 | 95.1 | 95.9 | 96 | 95.6 | 94.9 | 95.5 | 91.2 | 94.8 | 95.7 | 96 | 95.6 | 95.1 | 95.5 | 90.6 | 94.5 | 95.6 | 96 | 95.7 | 95.2 | 95.4 | Chilicon Power LLC0.277CP-250E-60/72-208/240-MC4 (208V) [SI1] | 2017-12-15 | 2018-10-15
Chilicon Power LLC | CP-250E-60/72-208/240-MC4 [240V] | Y | Y | Y | 289 W, 240 Vac Grid Support Utility Interactive Inverter | 0.289 | 240 | 96 | [11/15/2017] | [3353] | 2018-10-15 | N | Y |  | 0.06 |  |  | 28 | 30 | 32 | 0.03 | 0.06 | 0.09 | 0.14 | 0.22 | 0.29 | 92.3 | 95.4 | 96.1 | 96.2 | 95.9 | 95.2 | 95.8 | 91.6 | 95.2 | 96 | 96.3 | 96 | 95.4 | 95.8 | 91 | 95.1 | 95.9 | 96.3 | 96.1 | 95.6 | 95.8 | Chilicon Power LLC0.289CP-250E-60/72-208/240-MC4 (240V) [SI1] | 2017-12-15 | 2018-10-15
Chint Power Systems America | CPS SCA3KTL-O/US [208V] | Y | N | N | Utility Interactive Inverter | 2.86 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.29 | 0.57 | 0.86 | 1.43 | 2.15 | 2.86 | 91.1 | 94.1 | 95.1 | 95.6 | 95.6 | 95 | 95.3 | 93.4 | 95.7 | 96.7 | 97.1 | 97 | 96.6 | 96.8 | 93 | 95.4 | 96.4 | 96.9 | 96.8 | 96.4 | 96.6 | Chint Power Systems America2.86CPS SCA3KTL-O/US [208V]
Chint Power Systems America | CPS SCA3KTL-O/US [240V] | Y | N | N | Utility Interactive Inverter | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.3 | 0.6 | 0.9 | 1.5 | 2.3 | 3 | 91.5 | 94.5 | 95.5 | 96 | 96 | 95.6 | 95.7 | 94.1 | 96.2 | 97.1 | 97.5 | 97.4 | 97.1 | 97.2 | 93.8 | 95.8 | 96.8 | 97.3 | 97.3 | 97 | 97 | Chint Power Systems America3CPS SCA3KTL-O/US [240V]
Chint Power Systems America | CPS SCE4KTL-O US [208V] | Y | N | N | 3.7 kW, 208 Vac Utility Interactive Inverter | 3.69 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.21 |  |  | 100 | 360 | 470 | 0.37 | 0.74 | 1.11 | 1.85 | 2.77 | 3.69 | 94.7 | 96.6 | 97.3 | 97.7 | 97.6 | 97.4 | 97.4 | 94.1 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 92.5 | 95.5 | 96.6 | 97.2 | 97.2 | 97.2 | 96.9 | Chint Power Systems America3.69CPS SCE4KTL-O US [208V]
Chint Power Systems America | CPS SCA4KTL-O/US [208V] | Y | N | N | Utility Interactive Inverter | 3.81 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.381 | 0.762 | 1.143 | 1.905 | 2.858 | 3.81 | 91.4 | 94.6 | 95.4 | 96 | 95.8 | 95.2 | 95.5 | 93.7 | 96.2 | 97 | 97.3 | 97.2 | 96.8 | 97 | 93.1 | 95.6 | 96.5 | 97.1 | 97 | 96.6 | 96.7 | Chint Power Systems America3.81CPS SCA4KTL-O/US [208V]
Chint Power Systems America | CPS SCE4KTL-O US [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 3.98 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.16 |  |  | 100 | 360 | 450 | 0.4 | 0.8 | 1.19 | 1.99 | 2.99 | 3.98 | 92 | 95.1 | 96.3 | 97 | 97 | 96.9 | 96.6 | 94.1 | 96.5 | 97.4 | 97.3 | 97.1 | 97.7 | 97.1 | 92.3 | 95.8 | 96.9 | 97.5 | 97.6 | 97.6 | 97.2 | Chint Power Systems America3.98CPS SCE4KTL-O US [240V]
Chint Power Systems America | CPS SCE4KTL-O US [277V] | Y | N | N | 4 kW, 277 Vac Utility Interactive Inverter | 3.98 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 |  |  | 100 | 360 | 450 | 0.4 | 0.8 | 1.19 | 1.99 | 2.99 | 3.98 | 90.7 | 94.5 | 96 | 96.9 | 97 | 97 | 96.5 | 92.8 | 95.9 | 96.9 | 97.5 | 97.7 | 97.6 | 97.2 | 93 | 96 | 97.2 | 97.9 | 98 | 97.9 | 97.6 | Chint Power Systems America3.98CPS SCE4KTL-O US [277V]
Chint Power Systems America | CPS SCA4KTL-O/US [240V] | Y | N | N | Utility Interactive Inverter | 4.02 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.402 | 0.804 | 1.206 | 2.01 | 3.015 | 4.02 | 92.1 | 94.9 | 95.8 | 96.3 | 96.2 | 95.8 | 95.9 | 94.2 | 96.6 | 97.2 | 97.7 | 97.6 | 97.4 | 97.4 | 93.4 | 95.9 | 96.8 | 97.4 | 97.5 | 97.1 | 97.1 | Chint Power Systems America4.02CPS SCA4KTL-O/US [240V]
Chint Power Systems America | CPS SCE5KTL-O US [208V] | Y | N | N | 4.5 kW, 208 Vac Utility Interactive Inverter | 4.47 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 360 | 470 | 0.45 | 0.89 | 1.34 | 2.24 | 3.35 | 4.47 | 94.5 | 96.9 | 97.5 | 97.7 | 97.6 | 97.4 | 97.4 | 94 | 96.6 | 97.2 | 97.5 | 97.5 | 97.3 | 97.2 | 92.6 | 95.4 | 96.3 | 97.1 | 97.2 | 97.1 | 96.8 | Chint Power Systems America4.47CPS SCE5KTL-O US [208V]
Chint Power Systems America | CPS SCA5KTL-O US [208V] | Y | N | N | 4.8 kW, 208 Vac Utility Interactive Inverter | 4.61 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.7 |  |  | 100 | 390 | 470 | 0.46 | 0.92 | 1.38 | 2.31 | 3.46 | 4.61 | 93 | 95.3 | 95.9 | 96.1 | 95.7 | 95 | 95.7 | 94.8 | 96.8 | 97.3 | 97.5 | 97.2 | 96.6 | 97.1 | 94.6 | 96.6 | 97.1 | 97.3 | 97.1 | 96.5 | 97 | Chint Power Systems America4.61CPS SCA5KTL-O US [208V]
Chint Power Systems America | CPS SCE5KTL-O US [240V] | Y | N | N | 4.8 kW, 240 Vac Utility Interactive Inverter | 4.83 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.12 |  |  | 100 | 360 | 450 | 0.48 | 0.97 | 1.45 | 2.42 | 3.62 | 4.83 | 92.8 | 95.8 | 96.6 | 96.9 | 96.9 | 96.8 | 96.6 | 94.7 | 96.8 | 97.2 | 97.7 | 97.5 | 97.6 | 97.4 | 93.2 | 96.3 | 97 | 97.5 | 97.5 | 97.5 | 97.2 | Chint Power Systems America4.83CPS SCE5KTL-O US [240V]
Chint Power Systems America | CPS SCE5KTL-O US [277V] | Y | N | N | 4.8 kW, 277 Vac Utility Interactive Inverter | 4.83 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.09 |  |  | 100 | 360 | 450 | 0.48 | 0.97 | 1.45 | 2.42 | 3.62 | 4.83 | 91 | 94.4 | 95.7 | 96.6 | 96.9 | 96.9 | 96.3 | 93.3 | 96.3 | 97 | 97.5 | 97.6 | 97.6 | 97.3 | 94 | 96.7 | 97.3 | 97.8 | 97.9 | 97.9 | 97.6 | Chint Power Systems America4.83CPS SCE5KTL-O US [277V]
Chint Power Systems America | CPS SCA5KTL-O US [240V] | Y | N | N | Utility Interactive Inverter | 5 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.6 | 95.7 | 96.1 | 96.5 | 96.1 | 95.4 | 96 | 95.4 | 97.1 | 97.6 | 97.8 | 97.6 | 97.1 | 97.5 | 95 | 96.9 | 97.4 | 97.6 | 97.4 | 97.1 | 97.3 | Chint Power Systems America5CPS SCA5KTL-O US [240V]
Chint Power Systems America | CPS SCA6KTL-O US [208V] | Y | N | N | 5.5 kW, 208 Vac Utility Interactive Inverter. For outdoor use. | 5.5 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 380 | 470 | 0.55 | 1.1 | 1.65 | 2.75 | 4.125 | 5.5 | 92.1 | 94.8 | 95.5 | 96.1 | 96 | 95.5 | 95.7 | 93.6 | 96.1 | 96.8 | 97.3 | 97.2 | 96.8 | 97 | 93 | 95.7 | 96.5 | 97 | 96.9 | 96.6 | 96.7 | Chint Power Systems America5.5CPS SCA6KTL-O US [208V]
Chint Power Systems America | CPS SCE6KTL-O US [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter | 5.68 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 |  |  | 100 | 360 | 470 | 0.6 | 1.2 | 1.79 | 2.99 | 4.49 | 5.98 | 95.9 | 97.2 | 97.5 | 97.5 | 97.3 | 97 | 97.3 | 94.9 | 96.9 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93 | 96 | 96.6 | 97.1 | 97 | 96.8 | 96.7 | Chint Power Systems America5.68CPS SCE6KTL-O US [208V]
Chint Power Systems America | CPS SCA6KTL-O US [240V] | Y | N | N | 6.0 kW, 240 Vac Utility Interactive Inverter. For outdoor use. | 6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 380 | 470 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 95.3 | 95.9 | 96.5 | 96.4 | 95.9 | 96.1 | 94.3 | 96.6 | 97.3 | 97.7 | 97.6 | 97.3 | 97.4 | 93.7 | 96.1 | 96.9 | 97.4 | 97.4 | 97.2 | 97.1 | Chint Power Systems America6CPS SCA6KTL-O US [240V]
Chint Power Systems America | CPS SCE6KTL-O US [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 360 | 450 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 91.5 | 94.7 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | 93.3 | 96.2 | 96.9 | 97.4 | 97.4 | 97.4 | 97.1 | 94.3 | 96.7 | 97.3 | 97.9 | 97.8 | 97.7 | 97.6 | Chint Power Systems America6CPS SCE6KTL-O US [240V]
Chint Power Systems America | CPS SCE6KTL-O US [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter | 6.01 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 100 | 360 | 450 | 0.6 | 1.2 | 1.8 | 3.01 | 4.51 | 6.01 | 93.8 | 96.1 | 96.4 | 96.8 | 96.8 | 96.6 | 96.6 | 95.5 | 97.1 | 97.7 | 97.7 | 97.7 | 97.4 | 97.5 | 93.9 | 96.2 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | Chint Power Systems America6.01CPS SCE6KTL-O US [277V]
Chint Power Systems America | CPS SCE7KTL-O US [240V] | Y | N | N | 7 kW, 240 Vac Utility Interactive Inverter | 6.92 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.17 |  |  | 100 | 360 | 450 | 0.69 | 1.38 | 2.08 | 3.46 | 5.19 | 6.92 | 94.3 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | 96.6 | 95.5 | 97 | 97.5 | 97.6 | 97.5 | 97.3 | 97.4 | 94 | 96.2 | 96.9 | 97.3 | 97.3 | 97.2 | 97.1 | Chint Power Systems America6.92CPS SCE7KTL-O US [240V]
Chint Power Systems America | CPS SCE7KTL-O US [208V] | Y | N | N | 7 kW, 208 Vac Utility Interactive Inverter | 6.95 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.09 |  |  | 100 | 360 | 470 | 0.7 | 1.39 | 2.09 | 3.48 | 5.21 | 6.95 | 96.1 | 97.3 | 97.5 | 97.3 | 97 | 96.5 | 97.1 | 95.6 | 97 | 97.4 | 97.1 | 96.9 | 96.6 | 97 | 93.8 | 96 | 96.6 | 96.9 | 96.7 | 96.4 | 96.6 | Chint Power Systems America6.95CPS SCE7KTL-O US [208V]
Chint Power Systems America | CPS SCE7KTL-O US [277V] | Y | N | N | 7 kW, 277 Vac Utility Interactive Inverter | 7.01 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.02 |  |  | 100 | 360 | 450 | 0.7 | 1.4 | 2.1 | 3.51 | 5.26 | 7.01 | 93.4 | 95.9 | 96.5 | 96.8 | 96.6 | 96.4 | 96.5 | 94.8 | 96.6 | 97.2 | 97.5 | 97.1 | 97.1 | 97.1 | 94.9 | 96.9 | 97.4 | 97.7 | 97.6 | 97.4 | 97.5 | Chint Power Systems America7.01CPS SCE7KTL-O US [277V]
Chint Power Systems America | CPS SC14KTL-DO/xx-208 [208V] | Y | N | N | 14 kW, 208 Vac Utility Interactive Inverter with dual inputs (CA) | 14 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 |  |  | 300 | 385 | 540 | 1.4 | 2.8 | 4.2 | 7 | 10.5 | 14 | 94.9 | 95.4 | 95.6 | 95.6 | 95.2 | 94.7 | 95.3 | 95.7 | 96.5 | 96.9 | 96.8 | 96.5 | 96.1 | 96.6 | 93.7 | 96.8 | 95.9 | 96.2 | 96 | 95.6 | 96 | Chint Power Systems America14CPS SC14KTL-DO/xx-208 [208V]
Chint Power Systems America | CPS SC20KTL-DO/xx-480 [480V] | Y | N | N | 20 kW, 480 Vac Utility Interactive Inverter with dual inputs (CA) | 20 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2 |  |  | 300 | 480 | 550 | 2 | 4 | 6 | 10 | 15 | 20 | 94.9 | 96.2 | 96.4 | 96.6 | 96.2 | 95.7 | 96.2 | 95.2 | 96.7 | 97.1 | 97.2 | 97.1 | 96.9 | 97 | 95.3 | 96.8 | 97.2 | 97.4 | 97.3 | 97.2 | 97.2 | Chint Power Systems America20CPS SC20KTL-DO/xx-480 [480V]
Chint Power Systems America | CPS SCA23KTL-DO/US-480 [480V] | Y | N | N | 23 kVA, 3-phase, transformerless Utility Interactive Inverter | 23 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 480 | 720 | 800 | 2.3 | 4.6 | 6.9 | 11.5 | 17.25 | 23 | 95.8 | 97 | 97.2 | 97.4 | 97.4 | 97.3 | 97.3 | 97 | 98.2 | 98.4 | 98.6 | 98.5 | 98.4 | 98.4 | 96.6 | 98 | 98.2 | 98.4 | 98.4 | 98.3 | 98.3 | Chint Power Systems America23CPS SCA23KTL-DO/US-480 [480V]
Chint Power Systems America | CPS SCA28KTL-DO/US-480 [480V] | Y | N | N | 28 kVA 3-phase, transformerless Utility Interactive Inverter | 28 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 500 | 725 | 800 | 2.8 | 5.6 | 8.4 | 14 | 21 | 28 | 96.3 | 97.2 | 97.4 | 97.5 | 97.4 | 97.2 | 97.3 | 97.5 | 98.3 | 98.5 | 98.5 | 98.4 | 98.2 | 98.4 | 97.2 | 98.1 | 98.4 | 98.4 | 98.3 | 98.1 | 98.3 | Chint Power Systems America28CPS SCA28KTL-DO/US-480 [480V]
Chint Power Systems America | CPS SCA36KTL-DO/US [480V] | Y | Y | Y | 36 kVA, 480 Vac, 1000 Vdc, 3-phase, non-isolated Grid Support Utility Interactive Inverter | 36 | 480 | 98 | [7/31/2017] | [V0.60] | 2018-10-15 | Y | N | Multiple Listings: Solectria Renewables, LLC PVI 36TL-480 and Canadian Solar Inc CSI-36KTL-CT | 0 |  |  | 540 | 730 | 800 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 95.5 | 96.8 | 97.2 | 97.5 | 97.5 | 97.3 | 97.3 | 97.4 | 98.3 | 98.5 | 98.5 | 98.5 | 98.3 | 98.4 | 97.1 | 98 | 98.3 | 98.4 | 98.3 | 98.2 | 98.3 | Chint Power Systems America36CPS SCA36KTL-DO/US [480V] | 2017-09-01 | 2018-10-15
Chint Power Systems America | CPS SCA50KTL-DO/US-480 [480V] | Y | Y | Y | 50 kVA , 1000 Vdc, 480 Vac, 3-phase, non-isolated Grid Support Utility Interactive Inverter | 50 | 480 | 98.5 | [7/6/2017] | [V5.00] | 2018-10-15 | Y | N | Multiple Listings: Solectria Renewables, LLC PVI 50TL-480 and Canadian Solar Inc CSI-50KTL-CT | 0.88 |  |  | 480 | 730 | 850 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95.6 | 96.8 | 97.5 | 97.9 | 97.8 | 97.7 | 97.6 | 98 | 98.6 | 98.8 | 98.8 | 98.7 | 98.6 | 98.7 | 97.7 | 98.5 | 98.6 | 98.7 | 98.6 | 98.5 | 98.6 | Chint Power Systems America50CPS SCA50KTL-DO/US-480 [480V] | 2017-08-01 | 2018-10-15
Chint Power Systems America | CPS SCA60KTL-DO/US-480 [480V] | Y | Y | Y | 60 kVA , 1000 Vdc, 480 Vac, 3-phase, non-isolated Grid Support Utility Interactive Inverter | 60 | 480 | 98.5 | [7/6/2017] | [V5.00] | 2018-10-15 | Y | N | Multiple Listings: Solectria Renewables, LLC PVI 60TL-480 and Canadian Solar Inc CSI-60KTL-CT | 0.88 |  |  | 540 | 730 | 850 | 6 | 12 | 18 | 30 | 45 | 60 | 96.5 | 97.5 | 97.9 | 98.1 | 97.9 | 97.7 | 97.9 | 98.2 | 98.7 | 98.8 | 98.8 | 98.7 | 98.5 | 98.7 | 98 | 98.6 | 98.7 | 98.7 | 98.5 | 98.4 | 98.5 | Chint Power Systems America60CPS SCA60KTL-DO/US-480 [480V] | 2017-08-01 | 2018-10-15
Chint Power Systems America | CPS SC100KT-O/xx-480 [480V] | Y | N | N | 100 kW, 480 Vac Utility Interactive Inverter with dual inputs (US) | 100 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 34 |  |  | 330 | 430 | 500 | 10 | 20 | 30 | 50 | 75 | 100 | 94 | 96.2 | 96.6 | 96.8 | 96.6 | 96.2 | 96.5 | 92.7 | 95.7 | 96.1 | 96.5 | 96.3 | 95.9 | 96.1 | 92.2 | 95.2 | 95.8 | 96.3 | 96.1 | 95.7 | 95.9 | Chint Power Systems America100CPS SC100KT-O/xx-480 [480V]
Chint Power Systems America | CPS SCH100KTL-DO/US-600 [600V] | Y | Y | Y | 100 kVA , 1500Vdc, 600Vac, 3 Phase, Non-isolated Grid Support Utility Interactive Inverter | 100 | 600 | 98.5 | [06/08/2018] | [V2.00] | 2018-10-15 | N | N |  | 4.5 |  |  | 870 | 1000 | 1300 | 10 | 20 | 30 | 50 | 75 | 100 | 98.5519 | 98.9972 | 99.062 | 99.0008 | 98.8738 | 98.7452 | 98.9099 | 97.9026 | 98.4849 | 98.5322 | 98.5674 | 98.447 | 98.2811 | 98.4543 | 97.098 | 97.901 | 98.071 | 98.1053 | 98.08 | 97.9054 | 98.0273 | Chint Power Systems America100CPS SCH100KTL-DO/US-600 [600V] | 2018-08-01 | 2018-10-15
Chint Power Systems America | CPS SCH125KTL-DO/US-600 [600V] | Y | Y | Y | 125 kVA , 1500Vdc, 600Vac, 3 Phase, Non-isolated Grid Support Utility Interactive Inverter | 125 | 600 | 98.5 | [06/08/2018] | [V2.00] | 2018-10-15 | N | N |  | 4.9 |  |  | 870 | 1000 | 1300 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 98.7077 | 99.0329 | 99.0691 | 98.9523 | 98.7899 | 98.5613 | 98.8549 | 98.1008 | 98.563 | 98.5841 | 98.5384 | 98.352 | 98.0513 | 98.4045 | 97.4171 | 98.0383 | 98.14 | 98.1411 | 97.9782 | 97.6992 | 97.9985 | Chint Power Systems America125CPS SCH125KTL-DO/US-600 [600V] | 2018-08-01 | 2018-10-15
Chint Solar Zhejiang | CHPI3KTL-US [208V] | Y | N | N | Utility Interactive Inverter | 2.86 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.29 | 0.57 | 0.86 | 1.43 | 2.15 | 2.86 | 91.1 | 94.1 | 95.1 | 95.6 | 95.6 | 95 | 95.3 | 93.4 | 95.7 | 96.7 | 97.1 | 97 | 96.6 | 96.8 | 93 | 95.4 | 96.4 | 96.9 | 96.8 | 96.4 | 96.6 | Chint Solar Zhejiang2.86CHPI3KTL-US [208V]
Chint Solar Zhejiang | CHPI3KTL-US [240V] | Y | N | N | Utility Interactive Inverter | 3 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.3 | 0.6 | 0.9 | 1.5 | 2.3 | 3 | 91.5 | 94.5 | 95.5 | 96 | 96 | 95.6 | 95.7 | 94.1 | 96.2 | 97.1 | 97.5 | 97.4 | 97.1 | 97.2 | 93.8 | 95.8 | 96.8 | 97.3 | 97.3 | 97 | 97 | Chint Solar Zhejiang3CHPI3KTL-US [240V]
Chint Solar Zhejiang | CHPI4KTL-US [208V] | Y | N | N | Utility Interactive Inverter | 3.81 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.381 | 0.762 | 1.143 | 1.905 | 2.858 | 3.81 | 91.4 | 94.6 | 95.4 | 96 | 95.8 | 95.2 | 95.5 | 93.7 | 96.2 | 97 | 97.3 | 97.2 | 96.8 | 97 | 93.1 | 95.6 | 96.5 | 97.1 | 97 | 96.6 | 96.7 | Chint Solar Zhejiang3.81CHPI4KTL-US [208V]
Chint Solar Zhejiang | CHPI4KTL-US [240V] | Y | N | N | Utility Interactive Inverter | 4.02 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.402 | 0.804 | 1.206 | 2.01 | 3.015 | 4.02 | 92.1 | 94.9 | 95.8 | 96.3 | 96.2 | 95.8 | 95.9 | 94.2 | 96.6 | 97.2 | 97.7 | 97.6 | 97.4 | 97.4 | 93.4 | 95.9 | 96.8 | 97.4 | 97.5 | 97.1 | 97.1 | Chint Solar Zhejiang4.02CHPI4KTL-US [240V]
Chint Solar Zhejiang | CHPI5KTL-US [208V] | Y | N | N | Utility Interactive Inverter | 4.61 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.7 |  |  | 100 | 390 | 470 | 0.461 | 0.922 | 1.383 | 2.305 | 3.458 | 4.61 | 93 | 95.3 | 95.9 | 96.1 | 95.7 | 95 | 95.7 | 94.8 | 96.8 | 97.3 | 97.5 | 97.2 | 96.6 | 97.1 | 94.6 | 96.6 | 97.1 | 97.3 | 97.1 | 96.5 | 97 | Chint Solar Zhejiang4.61CHPI5KTL-US [208V]
Chint Solar Zhejiang | CHPI5KTL-US [240V] | Y | N | N | Utility Interactive Inverter | 5 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 390 | 470 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.6 | 95.7 | 96.1 | 96.5 | 96.1 | 95.4 | 96 | 95.4 | 97.1 | 97.6 | 97.8 | 97.6 | 97.1 | 97.5 | 95 | 96.9 | 97.4 | 97.6 | 97.4 | 97.1 | 97.3 | Chint Solar Zhejiang5CHPI5KTL-US [240V]
Chint Solar Zhejiang | CHPI 6KTL-US [208V] | Y | N | N | 5.5 kW, 208 Vac Utility Interactive Inverter | 5.5 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 380 | 470 | 0.55 | 1.1 | 1.65 | 2.75 | 4.125 | 5.5 | 92.1 | 94.8 | 95.5 | 96.1 | 96 | 95.5 | 95.7 | 93.6 | 96.1 | 96.8 | 97.3 | 97.2 | 96.8 | 97 | 93 | 95.7 | 96.5 | 97 | 96.9 | 96.6 | 96.7 | Chint Solar Zhejiang5.5CHPI 6KTL-US [208V]
Chint Solar Zhejiang | CHPI 6KTL-US [240V] | Y | N | N | 6.0 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 380 | 470 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 95.3 | 95.9 | 96.5 | 96.4 | 95.9 | 96.1 | 94.3 | 96.6 | 97.3 | 97.7 | 97.6 | 97.3 | 97.4 | 93.7 | 96.1 | 96.9 | 97.4 | 97.4 | 97.2 | 97.1 | Chint Solar Zhejiang6CHPI 6KTL-US [240V]
Chint Solar Zhejiang | CHPI14KTL-US | Y | N | N | Utility Interactive Inverter | 14 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 |  |  | 300 | 385 | 540 | 1.4 | 2.8 | 4.2 | 7 | 10.5 | 14 | 94.9 | 95.4 | 95.6 | 95.6 | 95.2 | 94.7 | 95.3 | 95.7 | 96.5 | 96.9 | 96.8 | 96.5 | 96.1 | 96.6 | 93.7 | 96.8 | 95.9 | 96.2 | 96 | 95.6 | 96 | Chint Solar Zhejiang14CHPI14KTL-US
Chint Solar Zhejiang | CHPI20KTL-US | Y | N | N | Utility Interactive Inverter | 20 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2 |  |  | 300 | 480 | 550 | 2 | 4 | 6 | 10 | 15 | 20 | 94.9 | 96.2 | 96.4 | 96.6 | 96.2 | 95.7 | 96.2 | 95.2 | 96.7 | 97.1 | 97.2 | 97.1 | 96.9 | 97 | 95.3 | 96.8 | 97.2 | 97.4 | 97.3 | 97.2 | 97.2 | Chint Solar Zhejiang20CHPI20KTL-US
Chint Solar Zhejiang | CHPI 23KTL-US | Y | N | N | 23 kVA, 3-phase, transformerless Utility Interactive Inverter | 23 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 480 | 720 | 800 | 2.3 | 4.6 | 6.9 | 11.5 | 17.25 | 23 | 95.8 | 97 | 97.2 | 97.4 | 97.4 | 97.3 | 97.3 | 97 | 98.2 | 98.4 | 98.6 | 98.5 | 98.4 | 98.4 | 96.6 | 98 | 98.2 | 98.4 | 98.4 | 98.3 | 98.3 | Chint Solar Zhejiang23CHPI 23KTL-US
Chint Solar Zhejiang | CHPI 28KTL-US | Y | N | N | 28 kVA, 3-phase, transformerless Utility Interactive Inverter | 28 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 500 | 725 | 800 | 2.8 | 5.6 | 8.4 | 14 | 21 | 28 | 96.3 | 97.2 | 97.4 | 97.5 | 97.4 | 97.2 | 97.3 | 97.5 | 98.3 | 98.5 | 98.5 | 98.4 | 98.2 | 98.4 | 97.2 | 98.1 | 98.4 | 98.4 | 98.3 | 98.1 | 98.3 | Chint Solar Zhejiang28CHPI 28KTL-US
Concept by US | Power Station PS247-05-180 [120V] | Y | N | N | 5 kW, 120 Vac Utility Interactive Inverter | 5.02 | 120 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0 |  |  | 210 | 310 | 420 | 0.502 | 1.004 | 1.506 | 2.51 | 3.765 | 5.02 | 96.5419 | 94.6876 | 93.4665 | 92.9563 | 93.3258 | 92.4851 | 93.4198 | 96.0637 | 96.782 | 96.7023 | 93.7118 | 94.6159 | 92.3483 | 94.7292 | 95.1281 | 93.4382 | 95.5797 | 94.4897 | 94.2959 | 92.9827 | 94.4154 | Concept by US5.02Power Station PS247-05-180 [120V]
Concept by US | Power Station PS247-10-180 [120V] | Y | N | N | 10 kW, 120 Vac Utility Interactive Inverter | 10.08 | 120 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0 |  |  | 210 | 310 | 420 | 1.01 | 2.02 | 3.02 | 5.04 | 7.56 | 10.08 | 96.9 | 94.3 | 93.9 | 93.1 | 92.3 | 91.4 | 92.9 | 97.2 | 96.1 | 95.4 | 93.8 | 94.9 | 92.6 | 94.8 | 96.4 | 94 | 93.9 | 95.2 | 93.7 | 93 | 94.1 | Concept by US10.08Power Station PS247-10-180 [120V]
Concept by US | Power Station PS247-15-180 [120V] | Y | N | N | 15 kW, 120 Vac Utility Interactive Inverter | 15.16 | 120 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0 |  |  | 210 | 310 | 420 | 1.52 | 3.03 | 4.55 | 7.58 | 11.37 | 15.16 | 95.4 | 94.3 | 94.4 | 93.2 | 92.4 | 92.1 | 93 | 96.9 | 96 | 95.8 | 94.2 | 94.8 | 93 | 94.8 | 96.4 | 95.4 | 94 | 94.7 | 93.9 | 93.7 | 94.2 | Concept by US15.16Power Station PS247-15-180 [120V]
Connect Renewable Energy | CE 4000 [240V] | Y | N | N | 3000 W Grid Tied, 240 Vac, Low DC Voltage Inverter | 3 | 240 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 7 | 3 | 7 | 54 | 62 | 77 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 85.3 | 92.8 | 93.8 | 94.4 | 94.3 | 93.4 | 93.8 | 85.6 | 91.7 | 93.1 | 94.4 | 93.6 | 92.6 | 93.3 | 82.8 | 89.3 | 91.1 | 93.8 | 93.3 | 93.2 | 92.5 | Connect Renewable Energy3CE 4000 [240V]
Danfoss | MLX 480V [480V] | Y | N | N | 60 kW, 480 Vac, Utility Interactive Inverter | 60 | 480 | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 8.16 |  |  | 685 | 710 | 800 | 6 | 12 | 18 | 30 | 45 | 60 | 97.7 | 98.5 | 98.7 | 98.8 | 98.6 | 98.5 | 98.6 | 97.5 | 98.4 | 98.7 | 98.7 | 98.6 | 98.4 | 98.6 | 96.9 | 98.1 | 98.4 | 98.4 | 98.3 | 98.1 | 98.3 | Danfoss60MLX 480V [480V]
Danfoss Solar | DLX 2.0 UL [208V] | Y | N | N | 2.0 kW, 208 Vac Utility Interactive Inverter | 2.01 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 100 | 365 | 490 | 0.2 | 0.4 | 0.6 | 1 | 1.51 | 2.01 | 91.7 | 95.1 | 95.6 | 96.5 | 96.6 | 96.3 | 96.2 | 92.9 | 95.4 | 96.2 | 96.8 | 96.9 | 96.7 | 96.6 | 91 | 94 | 95.3 | 96.3 | 96.6 | 96.6 | 96 | Danfoss Solar2.01DLX 2.0 UL [208V]
Danfoss Solar | DLX 2.0 UL [240V] | Y | N | N | 2.0 kW, 240 Vac Utility Interactive Inverter | 2.01 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.97 |  |  | 100 | 375 | 490 | 0.2 | 0.4 | 0.6 | 1.01 | 1.51 | 2.01 | 91.9 | 95.3 | 96.1 | 96.7 | 96.8 | 96.7 | 96.4 | 91.2 | 95.2 | 96.1 | 96.9 | 97.1 | 97.1 | 96.6 | 91 | 94.5 | 95.6 | 96.6 | 97 | 97.1 | 96.4 | Danfoss Solar2.01DLX 2.0 UL [240V]
Danfoss Solar | DLX 2.9 UL [240V] | Y | N | N | 2.9 kW, 240 Vac Utility Interactive Inverter | 2.9 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.98 |  |  | 100 | 375 | 490 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.9 | 93.4 | 95.9 | 96.5 | 96.8 | 96.5 | 96.1 | 96.4 | 93.3 | 96.1 | 96.8 | 97.2 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | Danfoss Solar2.9DLX 2.9 UL [240V]
Danfoss Solar | DLX 2.9 UL [208V] | Y | N | N | 2.9 kW, 208 Vac Utility Interactive Inverter | 2.91 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.92 |  |  | 100 | 365 | 490 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.91 | 93.7 | 95.9 | 96.2 | 96.5 | 96.3 | 95.6 | 96.2 | 93.9 | 96.1 | 96.6 | 96.8 | 96.6 | 96.3 | 96.5 | 91.9 | 95.1 | 96 | 96.5 | 96.5 | 96.3 | 96.2 | Danfoss Solar2.91DLX 2.9 UL [208V]
Danfoss Solar | DLX 3.8 UL [208V] | Y | N | N | 3.8 kW, 208 Vac Utility Interactive Inverter | 3.81 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.77 |  |  | 100 | 360 | 500 | 0.38 | 0.76 | 1.14 | 1.91 | 2.86 | 3.81 | 94.6 | 96.3 | 96.7 | 96.7 | 96.2 | 95.6 | 96.3 | 94.8 | 96.5 | 96.9 | 97 | 96.8 | 96.5 | 96.7 | 93.1 | 95.6 | 96.4 | 96.8 | 96.7 | 96.5 | 96.5 | Danfoss Solar3.81DLX 3.8 UL [208V]
Danfoss Solar | DLX 3.8 UL [240V] | Y | N | N | 3.8 kW, 240 Vac Utility Interactive Inverter | 3.81 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 100 | 370 | 500 | 0.38 | 0.76 | 1.14 | 1.91 | 2.86 | 3.81 | 94.8 | 96.6 | 96.9 | 96.9 | 96.5 | 96 | 96.6 | 94.6 | 96.6 | 97.1 | 97.3 | 97.2 | 96.8 | 97 | 93.3 | 95.8 | 96.6 | 97 | 97.1 | 96.9 | 96.8 | Danfoss Solar3.81DLX 3.8 UL [240V]
Danfoss Solar | DLX 4.4 UL [208V] | Y | N | N | 4.4 kW, 208 Vac Utility Interactive Inverter | 4.4 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.8 |  |  | 100 | 360 | 500 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 95.1 | 96.5 | 96.7 | 96.4 | 95.9 | 95.1 | 96 | 95.2 | 96.6 | 97 | 97 | 96.7 | 96.3 | 96.7 | 93.6 | 95.9 | 96.4 | 96.7 | 96.5 | 96.2 | 96.4 | Danfoss Solar4.4DLX 4.4 UL [208V]
Danfoss Solar | DLX 4.4 UL [240V] | Y | N | N | 4.4 kW, 240 Vac Utility Interactive Inverter | 4.4 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.97 |  |  | 100 | 370 | 500 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 95.3 | 96.8 | 96.9 | 96.8 | 96.4 | 95.6 | 96.5 | 95.2 | 96.8 | 97.2 | 97.2 | 97.1 | 96.7 | 97 | 93.9 | 96.2 | 96.7 | 97 | 97 | 96.7 | 96.8 | Danfoss Solar4.4DLX 4.4 UL [240V]
Danfoss Solar | MLX 400V [400V] | Y | N | N | 60 kW, 400 Vac, Utility Interactive Inverter | 59.86 | 400 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 7.1 |  |  | 570 | 630 | 800 | 5.99 | 11.97 | 17.96 | 29.93 | 44.89 | 59.86 | 97.9 | 98.6 | 98.7 | 98.6 | 98.4 | 98.1 | 98.4 | 97.5 | 98.3 | 98.4 | 98.3 | 98.1 | 97.9 | 98.2 | 96.5 | 97.7 | 98 | 98 | 97.7 | 97.5 | 97.8 | Danfoss Solar59.86MLX 400V [400V]
Darfon Electronics Corp. | MIG240UL00 [240V] | Y | N | N | 220 W, 240V Utility Interactive Inverter | 0.23 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.047 |  |  | 27 | 35 | 40 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 88.9 | 93.3 | 94.6 | 94.9 | 95.2 | 95.1 | 94.7 | 89 | 93 | 94.6 | 95.3 | 95.5 | 95.6 | 95 | 88.2 | 92.7 | 94.3 | 95.3 | 95.5 | 95.7 | 94.9 | Darfon Electronics Corp.0.23MIG240UL00 [240V]
Darfon Electronics Corp. | MIG300UL00 [240V] | Y | N | N | Utility Interactive Inverter | 0.25 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.089 |  |  | 30 | 36 | 40 | 0.025 | 0.051 | 0.076 | 0.127 | 0.19 | 0.254 | 90.3 | 93.7 | 95 | 95.3 | 95.5 | 95.4 | 95.1 | 89.9 | 93.5 | 94.9 | 95.2 | 95.7 | 95.7 | 95.1 | 89.8 | 93.3 | 94.7 | 95.2 | 95.7 | 95.8 | 95.1 | Darfon Electronics Corp.0.25MIG300UL00 [240V]
Darfon Electronics Corp. | G32xxxxxx [208V] | Y | N | N | 300 W, 208 Vac Utility Interactive Inverter, where x = 0-9, A-Z, or (blank) | 0.303 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.014 |  |  | 24 | 27.5 | 37 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 92.3 | 95.5 | 96 | 96.1 | 95.6 | 94.7 | 95.6 | 91.9 | 95.3 | 95.9 | 96 | 95.5 | 94.7 | 95.5 | 90.6 | 94.7 | 95.4 | 95.6 | 95.3 | 94.5 | 95.1 | Darfon Electronics Corp.0.303G32xxxxxx [208V] | 2017-03
Darfon Electronics Corp. | G32xxxxxx [240V] | Y | N | N | 300 W, 240 Vac Utility Interactive Inverter, where x = 0-9, A-Z, or (blank) | 0.305 | 240 | 96.3 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.065 |  |  | 24 | 27.5 | 37 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.31 | 91.9819 | 95.7436 | 96.4819 | 96.7075 | 96.4925 | 95.9914 | 96.2935 | 91.5101 | 95.3888 | 96.2557 | 96.5292 | 96.3443 | 95.8729 | 96.1078 | 89.9942 | 94.7422 | 95.7649 | 96.1578 | 96.0436 | 95.6311 | 95.7065 | Darfon Electronics Corp.0.305G32xxxxxx [240V]
Darfon Electronics Corp. | G32xxxxxx [277V] | Y | N | N | 300 W, 277 Vac Utility Interactive Inverter, where x = 0-9, A-Z ,or (Blank) | 0.305 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.065 |  |  | 24 | 27.5 | 37 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.31 | 92 | 95.7 | 96.5 | 96.7 | 96.5 | 96 | 96.3 | 91.5101 | 95.3888 | 96.2557 | 96.5292 | 96.3443 | 95.8729 | 96.1078 | 89.9942 | 94.7422 | 95.7649 | 96.1578 | 96.0436 | 95.6311 | 95.7065 | Darfon Electronics Corp.0.305G32xxxxxx [277V]
Darfon Electronics Corp. | H5000x [240V] | Y | Y | Y | 5000 W, 240 Vac Grid Support Utility Interactive Inverter, where x = 0-9, A-Z or blank, (0-9 for color; A-Z for customer) | 5.074 | 240 | 95.5 | [11/30/2017] | [INV DSP: INV 1.2, EEROM: EE 1.0] | 2018-10-15 | N | N |  | 0.43 |  |  | 300 | 360 | 380 | 0.508 | 1.016 | 1.524 | 2.54 | 3.81 | 5.076 | 89.2283 | 93.7363 | 94.9074 | 95.7518 | 95.8863 | 95.613 | 95.3531 | 89.4891 | 93.9486 | 95.2566 | 95.9139 | 96.0338 | 95.8858 | 95.5419 | 89.3177 | 94.0048 | 95.2025 | 95.9477 | 96.0161 | 95.9196 | 95.5308 | Darfon Electronics Corp.5.074H5000x [240V] | 2018-03-15 | 2018-10-15
DASS tech | DSP-M33250KUS | Y | N | N | Utility Interactive Inverter | 250 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 107.7 |  |  | 330 | 378 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 91.5 | 94.7 | 95.5 | 95.2 | 95.1 | 94.5 | 95 | 91.5 | 94.5 | 95.2 | 95.1 | 94.9 | 94.6 | 94.8 | 91.1 | 94.2 | 94.9 | 95 | 94.8 | 94.5 | 94.7 | DASS tech250DSP-M33250KUS
Delta Electronics | DDP-260AB XX | Y | N | N | Utility Interactive, transformer isolated PV Microinverter | 0.26 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.2 |  |  | 27.5 | 33.8 | 36 | 0.03 | 0.05 | 0.08 | 0.13 | 0.2 | 0.26 | 91.1 | 93.7 | 95 | 95.3 | 94.8 | 93.6 | 94.6 | 90.6 | 94.3 | 94.5 | 95.4 | 95.6 | 95 | 95.1 | 90.6 | 93.8 | 94.5 | 95.6 | 95.5 | 94.9 | 95.1 | Delta Electronics0.26DDP-260AB XX
Delta Electronics | SOLIVIA 3.8 NA G4 TL [208V] | Y | Y | Y | 3800W, 208Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type. | 3.32 | 208 | 97.5 | [4/10/2017] | [A: 02.04.01, B: 02.04.01, C: 02.04.01] | 2018-10-15 | Y | N |  | 1.14 |  |  | 100 | 380 | 500 | 0.33 | 0.66 | 1 | 1.66 | 2.49 | 3.32 | 94.6 | 96.1 | 97 | 97.3 | 97.1 | 96.8 | 97 | 96.3 | 96.9 | 97.8 | 97.9 | 98.1 | 97.5 | 97.8 | 95.9 | 95.8 | 96.9 | 97.4 | 97.4 | 97.1 | 97.2 | Delta Electronics3.32SOLIVIA 3.8 NA G4 TL [208V] [SI1] | 2017-10-16 | 2018-10-15
Delta Electronics | M4-TL-US [208V] | N | Y | Y | 3648 W, 208 Vac transformerless Grid Support Utility Interactive Inverter | 3.33 | 208 | 97 | [01/18/2018] | [1.4.1] | 2018-10-15 | Y | N |  | 1.92 |  |  | 180 | 380 | 480 | 0.3328 | 0.6656 | 0.9984 | 1.664 | 2.496 | 3.328 | 92 | 94.6 | 95.7 | 96.5 | 96.7 | 96.5 | 96.2 | 93 | 95.7 | 97.3 | 97.3 | 97.8 | 97.4 | 97.3 | 92.9 | 95.9 | 96.8 | 97.5 | 97.6 | 97.5 | 97.2 | Delta Electronics3.33M4-TL-US [208V] | 2018-03-01 | 2018-10-15
Delta Electronics | SOLIVIA 3.8 NA G4 TL [240V] | Y | Y | Y | 3800 W, 240 Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type. | 3.81 | 240 | 97.5 | [4/10/2017] | [A: 02.04.01, B: 02.04.01, C: 02.04.01] | 2018-10-15 | Y | N |  | 1.19 |  |  | 100 | 380 | 500 | 0.38 | 0.76 | 1.14 | 1.91 | 2.86 | 3.81 | 94.1 | 95.9 | 96.9 | 97.3 | 97.2 | 96.8 | 97 | 95.5 | 96.9 | 98 | 98.3 | 98.1 | 98 | 98 | 94.6 | 95.6 | 97.3 | 97.8 | 97.8 | 97.6 | 97.5 | Delta Electronics3.81SOLIVIA 3.8 NA G4 TL [240V] [SI1] | 2017-10-16 | 2018-10-15
Delta Electronics | M4-TL-US [240V] | N | Y | Y | 4000 W, 240 Vac transformerless Grid Support Utility Interactive Inverter | 3.84 | 240 | 97.5 | [01/18/2018] | [1.4.1] | 2018-10-15 | Y | N |  | 2.03 |  |  | 180 | 380 | 480 | 0.384 | 0.768 | 1.152 | 1.92 | 2.88 | 3.84 | 92.9 | 95.1 | 96.1 | 96.9 | 96.9 | 96.7 | 96.6 | 95.7 | 97.4 | 97.8 | 98.1 | 98.1 | 98 | 98 | 93.6 | 96.4 | 97.2 | 97.7 | 97.8 | 97.7 | 97.5 | Delta Electronics3.84M4-TL-US [240V] | 2018-03-01 | 2018-10-15
Delta Electronics | M5-TL-US [208V] | N | Y | Y | 4560 W, 208 Vac transformerless Grid Support Utility Interactive Inverter | 4.16 | 208 | 97.5 | [01/18/2018] | [1.4.1] | 2018-10-15 | Y | N |  | 1.24 |  |  | 220 | 380 | 480 | 0.416 | 0.832 | 1.248 | 2.08 | 3.12 | 4.16 | 94.5 | 96.1 | 96.9 | 97.3 | 97.2 | 96.9 | 97 | 95.8 | 97.3 | 97.8 | 98 | 97.8 | 97.6 | 97.7 | 95 | 96.8 | 97.4 | 97.7 | 97.7 | 97.4 | 97.5 | Delta Electronics4.16M5-TL-US [208V] [SI1] | 2018-03-01 | 2018-10-15
Delta Electronics | M5-TL-US [240V] | N | Y | Y | 5000 W, 240 Vac transformerless Grid Support Utility Interactive Inverter | 4.86 | 240 | 97.5 | [01/18/2018] | [1.4.1] | 2018-10-15 | Y | N |  | 1.26 |  |  | 220 | 380 | 480 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 94.3 | 96.1 | 96.9 | 97.3 | 97.2 | 96.9 | 97 | 96.3 | 97.6 | 98 | 98.2 | 98 | 97.8 | 97.9 | 95.6 | 97.2 | 97.7 | 98 | 97.9 | 97.7 | 97.8 | Delta Electronics4.858M5-TL-US [240V] [SI1] | 2018-03-01 | 2018-10-15
Delta Electronics | M6-TL-US [208V] | N | Y | Y | 5472 W, 208 Vac transformerless Grid Support Utility Interactive Inverter. | 4.99 | 208 | 97 | [01/18/2018] | [1.4.1] | 2018-10-15 | Y | N |  | 1.86 |  |  | 200 | 380 | 480 | 0.4992 | 0.9984 | 1.4976 | 2.496 | 3.744 | 4.992 | 94 | 95.6 | 96.5 | 97 | 97 | 96.7 | 96.7 | 95.7 | 97.2 | 97.7 | 97.8 | 97.7 | 97.3 | 97.6 | 94.6 | 96.5 | 97.2 | 97.5 | 97.5 | 97.2 | 97.3 | Delta Electronics4.992M6-TL-US [208V] [SI1] | 2018-03-01 | 2018-10-15
Delta Electronics | E6-TL-US [208V] | N | Y | Y | 4992 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter | 4.992 | 208 | 97 | [06/01/2018] | [1.4.1] | 2018-10-15 | Y | N |  | 1.86 |  |  | 200 | 380 | 480 | 0.4992 | 0.9984 | 1.4976 | 2.496 | 3.744 | 4.992 | 94.0016 | 95.6485 | 96.4705 | 97.0318 | 96.9884 | 96.6789 | 96.7334 | 95.696 | 97.2204 | 97.6522 | 97.8362 | 97.6671 | 97.3491 | 97.5837 | 94.6317 | 96.517 | 97.1735 | 97.5416 | 97.4711 | 97.1739 | 97.274 | Delta Electronics4.992E6-TL-US [208V] | 2018-08-01 | 2018-10-15
Delta Electronics | E6-TL-US(AC) [208V] | N | Y | Y | 5000 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Energy Storage Inverter | 5 | 208 | 98 | [06/01/2018] | [1.4.1] | 2018-10-15 | Y | N |  | 1.85 |  |  | 350 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 96.3576 | 97.7104 | 98.1201 | 98.2082 | 98.0337 | 97.6876 | 97.9802 | 95.6974 | 97.377 | 97.8682 | 98.0571 | 97.92 | 97.611 | 97.8111 | 94.7983 | 96.7769 | 97.4536 | 97.765 | 97.7211 | 97.431 | 97.5196 | Delta Electronics5E6-TL-US(AC) [208V] | 2018-08-01 | 2018-10-15
Delta Electronics | E6-TL-US(AC) [240V] | N | Y | Y | 5000 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Energy Storage Inverter | 5 | 240 | 98 | [06/01/2018] | [1.4.1] | 2018-10-15 | Y | N |  | 2.05 |  |  | 350 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 96.4809 | 97.5846 | 98.1167 | 98.4736 | 98.3238 | 97.9351 | 98.2003 | 95.8938 | 97.5508 | 98.0084 | 98.4507 | 98.3503 | 98.1238 | 98.1808 | 94.8718 | 96.9341 | 97.5858 | 98.1949 | 98.1673 | 97.9672 | 97.8998 | Delta Electronics5E6-TL-US(AC) [240V] | 2018-08-01 | 2018-10-15
Delta Electronics | SOLIVIA 5.2 NA G4 TL [208V] | Y | Y | Y | 5200W, 208Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type. | 5.2 | 208 | 97.5 | [4/10/2017] | [A: 02.04.01, B: 02.04.01, C: 02.04.01] | 2018-10-15 | Y | N |  | 1.31 |  |  | 100 | 380 | 500 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 93.6 | 95.6 | 96.3 | 97.2 | 97.1 | 96.8 | 96.8 | 95.2 | 96.6 | 97.5 | 98 | 98 | 97.7 | 97.7 | 93.6 | 96.3 | 97 | 97.7 | 97.7 | 97.5 | 97.4 | Delta Electronics5.2SOLIVIA 5.2 NA G4 TL [208V] [SI1] | 2017-10-16 | 2018-10-15
Delta Electronics | SOLIVIA 5.2 NA G4 TL [240V] | Y | Y | Y | 5200 W, 240Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type. | 5.2 | 240 | 97.5 | [4/10/2017] | [A: 02.04.01, B: 02.04.01, C: 02.04.01] | 2018-10-15 | Y | N |  | 1.42 |  |  | 100 | 380 | 500 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 94 | 95.8 | 96.4 | 97.3 | 97.4 | 97.1 | 97 | 95.2 | 97 | 97.5 | 98.2 | 98.3 | 98.1 | 98 | 93.8 | 96.6 | 97.2 | 97.9 | 98 | 98 | 97.7 | Delta Electronics5.2SOLIVIA 5.2 NA G4 TL [240V] [SI1] | 2017-10-16 | 2018-10-15
Delta Electronics | E6-TL-US [240V] | N | Y | Y | 5760 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter | 5.76 | 240 | 97.5 | [06/01/2018] | [1.4.1] | 2018-10-15 | Y | N |  | 2.25 |  |  | 200 | 380 | 480 | 0.576 | 1.152 | 1.728 | 2.88 | 4.32 | 5.76 | 93.9636 | 95.7324 | 96.5328 | 97.1183 | 97.0624 | 96.7746 | 96.8057 | 96.2574 | 97.615 | 97.9819 | 98.0814 | 97.6804 | 97.6267 | 97.738 | 95.2386 | 96.9825 | 97.5357 | 97.8342 | 97.7548 | 97.4585 | 97.5911 | Delta Electronics5.76E6-TL-US [240V] | 2018-08-01 | 2018-10-15
Delta Electronics | M6-TL-US [240V] | N | Y | Y | 6000 W, 240 Vac transformerless Grid Support Utility Interactive Inverter | 5.76 | 240 | 97.5 | [01/18/2018] | [1.4.1] | 2018-10-15 | Y | N |  | 2.25 |  |  | 200 | 380 | 480 | 0.576 | 1.152 | 1.728 | 2.88 | 4.32 | 5.76 | 94 | 95.7 | 96.5 | 97.1 | 97.1 | 96.8 | 96.8 | 96.3 | 97.6 | 98 | 98.1 | 97.7 | 97.6 | 97.7 | 95.2 | 97 | 97.5 | 97.8 | 97.8 | 97.5 | 97.6 | Delta Electronics5.76 M6-TL-US [240V] [SI1] | 2018-03-01 | 2018-10-15
Delta Electronics | RPI H7U [208V] | Y | N | N | 6 kW, 208 Vac transformerless Utility Interactive Inverter with arc detector | 5.99 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.087 |  |  | 280 | 370 | 400 | 0.6 | 1.2 | 1.8 | 3 | 4.49 | 5.99 | 96.1 | 96.8 | 97 | 97 | 96.7 | 96.3 | 96.8 | 95.8 | 97.4 | 97.6 | 97.5 | 97.3 | 96.9 | 97.3 | 95.7 | 97.3 | 97.5 | 97.5 | 97.3 | 96.9 | 97.3 | Delta Electronics5.99RPI H7U [208V]
Delta Electronics | RPI H7U [240V] [6kVa] | Y | N | N | 6 kW, 240 Vac transformerless Utility Interactive Inverter with arc detector | 6.06 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.181 |  |  | 280 | 370 | 400 | 0.61 | 1.21 | 1.82 | 3.03 | 4.55 | 6.06 | 96 | 96.1 | 96.6 | 96.7 | 96.7 | 96.4 | 96.6 | 96 | 97.7 | 97.9 | 97.9 | 97.7 | 97.5 | 97.7 | 95.8 | 97.6 | 97.8 | 97.9 | 97.7 | 97.5 | 97.6 | Delta Electronics6.06RPI H7U [240V] [6kVa]
Delta Electronics | E8-TL-US(AC) [240V] | N | Y | Y | 6500 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Energy Storage Inverter | 6.494 | 240 | 98 | [06/01/2018] | [1.4.1] | 2018-10-15 | Y | N |  | 2.1 |  |  | 350 | 400 | 480 | 0.65 | 1.3 | 1.95 | 3.25 | 4.875 | 6.5 | 96.564 | 97.9534 | 98.1731 | 98.3825 | 98.2962 | 98.0856 | 98.2026 | 95.9941 | 97.6828 | 98.1182 | 98.3712 | 98.3594 | 98.0923 | 98.1911 | 95.036 | 97.1456 | 97.7444 | 98.1155 | 98.1782 | 97.9141 | 97.9224 | Delta Electronics6.494E8-TL-US(AC) [240V] | 2018-08-01 | 2018-10-15
Delta Electronics | E8-TL-US(AC) [208V] | N | Y | Y | 6500 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Energy Storage Inverter | 6.5 | 208 | 98 | [06/01/2018] | [1.4.1] | 2018-10-15 | Y | N |  | 1.91 |  |  | 350 | 400 | 480 | 0.65 | 1.3 | 1.95 | 3.25 | 4.875 | 6.5 | 96.5268 | 97.8051 | 98.1607 | 98.2713 | 98.071 | 97.7448 | 98.0324 | 95.9938 | 97.5402 | 97.9409 | 98.1437 | 97.9732 | 97.6535 | 97.8883 | 95.0772 | 96.9768 | 97.5715 | 97.8841 | 97.7702 | 97.4644 | 97.6076 | Delta Electronics6.5E8-TL-US(AC) [208V] | 2018-08-01 | 2018-10-15
Delta Electronics | SOLIVIA 6.6 NA G4 TL [208V] | Y | Y | Y | 6600W, 208Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type. | 6.6 | 208 | 97.5 | [4/10/2017] | [A: 02.04.01, B: 02.04.01, C: 02.04.01] | 2018-10-15 | Y | N |  | 1.23 |  |  | 100 | 380 | 500 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.4 | 96.1 | 97 | 97.2 | 96.9 | 96.2 | 96.8 | 95.9 | 96.9 | 97.8 | 98 | 97.7 | 97.3 | 97.7 | 95 | 96.4 | 97.4 | 97.7 | 97.6 | 97.1 | 97.4 | Delta Electronics6.6SOLIVIA 6.6 NA G4 TL [208V] [SI1] | 2017-10-16 | 2018-10-15
Delta Electronics | SOLIVIA 6.6 NA G4 TL [240V] | Y | Y | Y | 6600W, 208Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type. | 6.6 | 240 | 97.5 | [4/10/2017] | [A: 02.04.01, B: 02.04.01, C: 02.04.01] | 2018-10-15 | Y | N |  | 1.45 |  |  | 100 | 380 | 500 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.3 | 96.2 | 96.9 | 97.4 | 97.2 | 96.8 | 97 | 96 | 97.3 | 97.9 | 98.3 | 98.2 | 97.9 | 98 | 95 | 96.8 | 97.6 | 98 | 98 | 97.7 | 97.7 | Delta Electronics6.6SOLIVIA 6.6 NA G4 TL [240V] [SI1] | 2017-10-16 | 2018-10-15
Delta Electronics | SOLIVIA 7.6 NA G4 TL [208V] | Y | Y | Y | 7600W, 208Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type. | 6.6 | 208 | 97.5 | [4/10/2017] | [A: 02.04.01, B: 02.04.01, C: 02.04.01] | 2018-10-15 | Y | N |  | 1.23 |  |  | 100 | 380 | 500 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.4 | 96.1 | 97 | 97.2 | 96.9 | 96.2 | 96.8 | 95.9 | 96.9 | 97.8 | 98 | 97.7 | 97.3 | 97.7 | 95 | 96.4 | 97.4 | 97.7 | 97.6 | 97.1 | 97.4 | Delta Electronics6.6SOLIVIA 7.6 NA G4 TL [208V] [SI1] | 2017-10-16 | 2018-10-15
Delta Electronics | E8-TL-US [208V] | N | Y | Y | 6656W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter | 6.656 | 208 | 97.5 | [06/01/2018] | [1.4.1] | 2018-10-15 | Y | N |  | 1.15 |  |  | 270 | 380 | 480 | 0.6656 | 1.3312 | 1.9968 | 3.328 | 4.992 | 6.656 | 95.2308 | 96.891 | 97.3835 | 97.6343 | 97.4276 | 97.0506 | 97.3322 | 95.9476 | 97.4104 | 97.7946 | 97.9487 | 97.6997 | 97.3918 | 97.6634 | 94.855 | 96.7763 | 97.3739 | 97.6604 | 97.5174 | 97.1621 | 97.3689 | Delta Electronics6.656E8-TL-US [208V] | 2018-08-01 | 2018-10-15
Delta Electronics | M8-TL-US [208V] | N | Y | Y | 7296 W, 208 Vac transformerless Grid Support Utility Interactive Inverter | 6.66 | 208 | 97.5 | [01/18/2018] | [1.4.1] | 2018-10-15 | Y | N |  | 1.15 |  |  | 270 | 380 | 480 | 0.6656 | 1.3312 | 1.9968 | 3.328 | 4.992 | 6.656 | 95.2 | 96.9 | 97.4 | 97.6 | 97.4 | 97.1 | 97.3 | 95.9 | 97.4 | 97.8 | 97.9 | 97.7 | 97.4 | 97.7 | 94.9 | 96.8 | 97.4 | 97.7 | 97.5 | 97.2 | 97.4 | Delta Electronics6.656M8-TL-US [208V] [SI1] | 2018-03-01 | 2018-10-15
Delta Electronics | RPI H7U [240V] [7kVa] | Y | N | N | 7 kW, 240 Vac transformerless Utility Interactive Inverter with arc detector | 7.014 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.169 |  |  | 280 | 370 | 400 | 0.7 | 1.4 | 2.1 | 3.51 | 5.26 | 7.01 | 96.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.2 | 96.6 | 96.9 | 97.8 | 97.9 | 97.9 | 97.6 | 97.3 | 97.7 | 96.7 | 97.7 | 97.9 | 97.9 | 97.6 | 97.4 | 97.7 | Delta Electronics7.014RPI H7U [240V] [7kVa]
Delta Electronics | SOLIVIA 7.6 NA G4 TL [240V] | Y | Y | Y | 7600W,240Vac transformerless Grid Support Utility Interactive Inverter. All the SOLIVIA models are same firmare version tested for Grid Support Utility Interactive type. | 7.6 | 240 | 97.5 | [4/10/2017] | [A: 02.04.01, B: 02.04.01, C: 02.04.01] | 2018-10-15 | Y | N |  | 1.43 |  |  | 100 | 380 | 500 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95 | 96.4 | 97.3 | 97.4 | 97 | 96.4 | 97 | 96.3 | 97.4 | 98.1 | 98.3 | 98 | 97.7 | 98 | 95.5 | 97.2 | 97.7 | 98 | 97.9 | 97.5 | 97.7 | Delta Electronics7.6SOLIVIA 7.6 NA G4 TL [240V] [SI1] | 2017-10-16 | 2018-10-15
Delta Electronics | E8-TL-US [240V] | N | Y | Y | 7680 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter | 7.68 | 240 | 97.5 | [06/01/2018] | [1.4.1] | 2018-10-15 | Y | N |  | 1.19 |  |  | 270 | 380 | 480 | 0.768 | 1.536 | 2.304 | 3.84 | 5.76 | 7.68 | 95.2202 | 96.7865 | 97.3605 | 97.6615 | 97.5147 | 97.0633 | 97.3763 | 96.5571 | 97.7682 | 98.0917 | 98.1644 | 97.9971 | 97.6404 | 97.9567 | 95.5533 | 97.2136 | 97.7339 | 97.9476 | 97.8481 | 97.5018 | 97.7144 | Delta Electronics7.68E8-TL-US [240V] | 2018-08-01 | 2018-10-15
Delta Electronics | M8-TL-US [240V] | N | Y | Y | 8000 W, 240 Vac transformerless Grid Support Utility Interactive Inverter | 7.68 | 240 | 97.5 | [01/18/2018] | [1.4.1] | 2018-10-15 | Y | N |  | 1.19 |  |  | 270 | 380 | 480 | 0.768 | 1.536 | 2.304 | 3.84 | 5.76 | 7.68 | 95.2 | 96.8 | 97.4 | 97.7 | 97.5 | 97.1 | 97.4 | 96.6 | 97.8 | 98.1 | 98.2 | 98 | 97.6 | 98 | 95.6 | 97.2 | 97.7 | 97.9 | 97.8 | 97.5 | 97.7 | Delta Electronics7.68M8-TL-US [240V] [SI1] | 2018-03-01 | 2018-10-15
Delta Electronics | Delta 15 TL | Y | N | N | 15 kW, 3-phase, transformerless Utility Interactive Inverter | 15.13 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.82 |  |  | 420 | 700 | 800 | 1.51 | 3.03 | 4.54 | 7.56 | 11.34 | 15.13 | 94.7 | 96.5 | 97 | 97.4 | 97.5 | 97.4 | 97.2 | 95.6 | 97.2 | 97.7 | 98.1 | 98.2 | 98.1 | 97.9 | 96.2 | 97.6 | 98.1 | 98.4 | 98.4 | 98.4 | 98.3 | Delta Electronics15.13Delta 15 TL
Delta Electronics | Delta 20 TL | Y | N | N | 20 kW, 3-phase, transformerless Utility Interactive Inverter | 20.2 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.82 |  |  | 500 | 720 | 800 | 2.02 | 4.04 | 6.06 | 10.1 | 15.15 | 20.2 | 95.5 | 96.8 | 97.3 | 97.6 | 97.7 | 97.6 | 97.5 | 97.3 | 98.2 | 98.5 | 98.6 | 98.6 | 98.5 | 98.5 | 96.9 | 97.9 | 98.3 | 98.4 | 98.4 | 98.4 | 98.3 | Delta Electronics20.2Delta 20 TL
Delta Electronics | M24U_XXX [480V] | Y | Y | Y | 26.4 kW, 480 Vac Grid Support Utility Interactive Inverter, where xxx = 120, 121, or 122 | 26.403 | 480 | 98 | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X ] | 2018-10-15 | N | N |  | 2.6 |  |  | 415 | 710 | 830 | 2.64 | 5.28 | 7.92 | 13.2 | 19.8 | 26.4 | 95.28 | 96.42 | 97.03 | 97.41 | 97.46 | 97.3 | 97.25 | 97.39 | 98.27 | 98.56 | 98.65 | 98.65 | 98.57 | 98.57 | 96.51 | 97.77 | 98.06 | 98.35 | 98.36 | 98.27 | 98.21 | Delta Electronics Inc26.403M60U_XXX [SI1] | 2017-12-15 | 2018-10-15
Delta Electronics | M28U_XXX [480V] | Y | Y | Y | 30.7 kW, 480 Vac Grid Support Utility Interactive Inverter, where xxx = 120, 121, or 122 | 30.709 | 480 | 98 | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X ] | 2018-10-15 | N | N |  | 2.4 |  |  | 485 | 710 | 830 | 3.07 | 6.14 | 9.21 | 15.35 | 23.03 | 30.71 | 95.98 | 97.06 | 97.64 | 97.78 | 97.74 | 97.52 | 97.62 | 97.67 | 98.38 | 98.6 | 98.65 | 98.6 | 98.49 | 98.56 | 96.9 | 97.95 | 98.21 | 98.35 | 98.32 | 98.18 | 98.23 | Delta Electronics Inc30.709M80U_XXX [SI1] | 2017-12-15 | 2018-10-15
Delta Electronics | M36U_XXX [480V] | Y | Y | Y | 39.7 kW, 480 Vac Grid Support Utility Interactive Inverter, where xxx = 120, 121, or 122 | 39.737 | 480 | 98 | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X ] | 2018-10-15 | N | N |  | 2.9 |  |  | 520 | 710 | 830 | 3.97 | 7.95 | 11.92 | 19.87 | 29.8 | 39.74 | 96.36 | 97.47 | 97.83 | 97.97 | 97.81 | 97.59 | 97.76 | 97.75 | 98.45 | 98.6 | 98.6 | 98.43 | 98.28 | 98.45 | 96.89 | 97.92 | 98.22 | 98.3 | 98.16 | 97.95 | 98.12 | Delta Electronics Inc39.737M24U_XXX [SI1] | 2017-12-15 | 2018-10-15
Delta Electronics | M42U_XXX [480V] | Y | Y | Y | 45.9 kW, 480 Vac Grid Support Utility Interactive Inverter, where xxx = 120, 121, or 122 | 45.972 | 480 | 98 | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X,V01.6X, V01.7X, V01.8X, V01.9X, V02.0X ] | 2018-10-15 | N | N |  | 2.9 |  |  | 545 | 710 | 830 | 4.6 | 9.19 | 13.79 | 22.99 | 34.48 | 45.97 | 96.83 | 97.76 | 97.97 | 98.02 | 97.8 | 97.54 | 97.81 | 97.98 | 98.53 | 98.6 | 98.55 | 98.35 | 98.16 | 98.41 | 97.21 | 98.04 | 98.26 | 98.26 | 98.07 | 97.86 | 98.09 | Delta Electronics Inc45.972M28U_XXX [SI1] | 2017-12-15 | 2018-10-15
Delta Electronics | M60U_XXX [480V] | Y | Y | Y | 65.47 kW, 480 Vac Grid Support Utility Interactive Inverter, where xxx = 120, 121, or 122 | 65.47 | 480 | 98.5 | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X ] | 2018-10-15 | N | N |  | 2.863 |  |  | 540 | 710 | 800 | 6.55 | 13.09 | 19.64 | 32.74 | 49.1 | 65.47 | 96.77 | 97.69 | 97.62 | 98.1 | 98.02 | 97.46 | 97.89 | 98.52 | 98.59 | 98.63 | 98.71 | 98.46 | 98.29 | 98.54 | 97.76 | 98.59 | 98.41 | 98.51 | 98.32 | 98.14 | 98.35 | Delta Electronics Inc65.47M36U_XXX [SI1] | 2017-12-15 | 2018-10-15
Delta Electronics | M80U_XXX [480V] | Y | Y | Y | 82.76 kW, 480 Vac Grid Support Utility Interactive Inverter, where xxx = 120, 121, or 122 | 82.764 | 480 | 98.5 | [10/27/2017] | [V01.0X, V01.1X, V01.2X, V01.3X, V01.4X, V01.5X ] | 2018-10-15 | N | N |  | 2.6 |  |  | 600 | 710 | 800 | 8.28 | 16.55 | 24.83 | 41.38 | 62.07 | 82.76 | 97.48 | 98.39 | 98.4 | 98.22 | 97.97 | 97.79 | 98.06 | 98.31 | 98.79 | 98.85 | 98.69 | 98.54 | 98.18 | 98.59 | 98.37 | 98.68 | 98.69 | 98.49 | 98.23 | 98.09 | 98.36 | Delta Electronics Inc82.764M42U_XXX [SI1] | 2017-12-15 | 2018-10-15
Delta Electronics | DES10JB125K01 [480V] | N | Y | Y | 125 kW, 480 Vac, 3-phase bi-directional Grid Support Utility Interactive Inverter | 125 | 480 | 97 | [7/20/2017] | [1.1.2.4, 1.1.2.4, 0.1.2.2] | 2018-10-15 | N | N |  | 22.4 |  |  | 750 | 900 | 1000 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 95.731 | 97.1982 | 97.5482 | 97.6472 | 97.4412 | 97.2142 | 97.4054 | 93.8046 | 96.324 | 96.9331 | 97.278 | 97.2686 | 97.1169 | 97.037 | 92.3112 | 95.6622 | 96.4776 | 96.9704 | 97.0348 | 96.8004 | 96.6851 | Delta Electronics, Inc125DES10JB125K01 | 2017-11-01 | 2018-10-15
Delta Energy Systems | SI 1800 US [208V] | Y | N | N | 1800 W, 208 Vac Grid-Tied Solar PV Inverter | 1.8 | 208 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 290 | 320 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 83.5 | 90 | 91.6 | 92.5 | 92.8 | 92.4 | 92 | 84 | 91.4 | 91.6 | 93.1 | 93.4 | 93.5 | 92.6 | 84.8 | 90.4 | 92.1 | 93.4 | 93.6 | 93.5 | 92.8 | Delta Energy Systems1.8SI 1800 US [208V]
Delta Energy Systems | SI 1800 US [240V] | Y | N | N | 1800 W, 240 Vac Grid-Tied Solar PV Inverter | 1.8 | 240 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 290 | 320 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 83.6 | 89.6 | 91.2 | 92.3 | 92.6 | 92.3 | 91.8 | 84.1 | 90.1 | 91.8 | 93.2 | 93.4 | 93.2 | 92.6 | 85 | 90.1 | 92.2 | 93.3 | 93.5 | 93.3 | 92.8 | Delta Energy Systems1.8SI 1800 US [240V]
Delta Energy Systems | SI 2500 US [208V] | Y | N | N | 2500 W, 208 Vac Grid-Tied Solar PV Inverter | 2.5 | 208 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 100 | 290 | 320 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 85.3 | 90.2 | 91.6 | 92.1 | 91.8 | 90.8 | 91.4 | 86.7 | 90.7 | 92.3 | 92.7 | 92.6 | 92.1 | 92.2 | 86.6 | 91 | 92.4 | 93 | 92.5 | 92 | 92.3 | Delta Energy Systems2.5SI 2500 US [208V]
Delta Energy Systems | SI 2500 US [240V] | Y | N | N | 2500 W, 240 Vac Grid-Tied Solar PV Inverter | 2.5 | 240 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 100 | 290 | 320 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 86.5 | 91.2 | 92.7 | 93.1 | 92.6 | 91.7 | 92.4 | 86.8 | 91.7 | 93.1 | 93.7 | 93.6 | 92.9 | 93.2 | 87.6 | 92.1 | 93.3 | 93.8 | 93.6 | 93 | 93.3 | Delta Energy Systems2.5SI 2500 US [240V]
Delta Energy Systems | SOLIVIA 2.5 NA G4 TR [240V] | Y | N | N | 2500 W, 240 Vac Grid-Tied Solar PV Inverter | 2.53 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.44 |  |  | 100 | 350 | 500 | 0.2525 | 0.505 | 0.7575 | 1.263 | 1.894 | 2.525 | 87.88 | 92.81 | 94.3 | 95.16 | 95.39 | 95.43 | 94.78 | 88.06 | 92.94 | 94.4 | 95.57 | 95.81 | 96.07 | 95.15 | 87.32 | 93.18 | 94.41 | 95.57 | 96.11 | 96.19 | 95.3 | Delta Energy Systems2.53SOLIVIA 2.5 NA G4 TR [240V]
Delta Energy Systems | SOLIVIA 2.5 NA G4 TR [208V] | Y | N | N | 2500 W, 208 Vac Grid-Tied Solar PV Inverter | 2.55 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.33 |  |  | 100 | 350 | 500 | 0.2554 | 0.5108 | 0.7662 | 1.277 | 1.916 | 2.554 | 87.8 | 92.51 | 93.67 | 94.83 | 95.11 | 95.18 | 94.46 | 87.84 | 92.59 | 93.98 | 95.14 | 95.44 | 95.71 | 94.77 | 87.07 | 92.88 | 94.1 | 95.22 | 95.67 | 95.82 | 94.91 | Delta Energy Systems2.55SOLIVIA 2.5 NA G4 TR [208V]
Delta Energy Systems | SOLIVIA 3.3 NA G4 TR [208V] | Y | N | N | 3300 W, 208 Vac Grid-Tied Solar PV Inverter | 3.33 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.33 |  |  | 100 | 350 | 500 | 0.3325 | 0.665 | 0.9975 | 1.663 | 2.494 | 3.325 | 89.6 | 93.39 | 94.38 | 95.06 | 95.1 | 94.9 | 94.69 | 89.95 | 93.65 | 94.73 | 95.42 | 95.74 | 95.36 | 95.19 | 89.44 | 93.75 | 94.91 | 95.65 | 95.82 | 95.59 | 95.3 | Delta Energy Systems3.33SOLIVIA 3.3 NA G4 TR [208V]
Delta Energy Systems | SOLIVIA 3.3 NA G4 TR [240V] | Y | N | N | 3300 W, 240 Vac Grid-Tied Solar PV Inverter | 3.34 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.44 |  |  | 100 | 350 | 500 | 0.3335 | 0.667 | 1.001 | 1.668 | 2.501 | 3.335 | 89.99 | 93.76 | 94.76 | 95.34 | 95.57 | 95.28 | 95.09 | 89.85 | 94.05 | 95 | 95.8 | 96.07 | 95.85 | 95.52 | 89.59 | 94.12 | 95.09 | 95.98 | 96.15 | 96 | 95.62 | Delta Energy Systems3.34SOLIVIA 3.3 NA G4 TR [240V]
Delta Energy Systems | SOLIVIA 4.4 NA G4 TR [208V] | Y | N | N | 4400 W, 208 Vac Grid-Tied Solar PV Inverter | 4.528 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.39 |  |  | 100 | 350 | 500 | 0.45 | 0.91 | 1.36 | 2.26 | 3.4 | 4.53 | 89.29 | 93.12 | 93.99 | 94.56 | 94.41 | 94.04 | 94.1 | 89.82 | 93.26 | 94.33 | 95.08 | 94.86 | 94.47 | 94.54 | 89.76 | 94.05 | 95 | 95.49 | 95.38 | 94.87 | 95.04 | Delta Energy Systems4.528SOLIVIA 4.4 NA G4 TR [208V]
Delta Energy Systems | SOLIVIA 4.4 NA G4 TR [240V] | Y | N | N | 4400 W, 240 Vac Grid-Tied Solar PV Inverter | 4.564 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.49 |  |  | 100 | 350 | 500 | 0.46 | 0.91 | 1.37 | 2.28 | 3.42 | 4.56 | 90 | 93.32 | 94.39 | 94.88 | 94.89 | 94.61 | 94.54 | 89.54 | 93.68 | 94.86 | 95.49 | 95.33 | 95.01 | 94.98 | 89.56 | 93.58 | 95.11 | 95.82 | 95.84 | 95.44 | 95.37 | Delta Energy Systems4.564SOLIVIA 4.4 NA G4 TR [240V]
Delta Energy Systems | SOLIVIA 5.0 NA G4 TR [208V] | Y | N | N | 5000 W, 208 Vac Grid-Tied Solar PV Inverter | 5.084 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.39 |  |  | 100 | 350 | 500 | 0.51 | 1.02 | 1.53 | 2.54 | 3.81 | 5.08 | 90.37 | 93.22 | 94.25 | 94.49 | 94.27 | 93.72 | 94.08 | 90.53 | 93.49 | 94.69 | 94.97 | 94.66 | 93.96 | 94.47 | 90.64 | 93.95 | 94.83 | 95.49 | 95.16 | 94.56 | 94.92 | Delta Energy Systems5.084SOLIVIA 5.0 NA G4 TR [208V]
Delta Energy Systems | SOLIVIA 5.0 NA G4 TR [240V] | Y | N | N | 5000 W, 240 Vac Grid-Tied Solar PV Inverter | 5.14 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.51 |  |  | 100 | 350 | 500 | 0.51 | 1.03 | 1.54 | 2.57 | 3.86 | 5.14 | 90.13 | 93.58 | 94.64 | 94.84 | 94.8 | 94.46 | 94.53 | 90.59 | 93.73 | 94.91 | 95.4 | 95.15 | 94.87 | 94.9 | 91.18 | 94.19 | 95.12 | 95.68 | 95.61 | 95.13 | 95.29 | Delta Energy Systems5.14SOLIVIA 5.0 NA G4 TR [240V]
Destin Power Inc. | SAVEEN1000-ES02H.US [440V] | Y | Y | N | 1000 kW, 440 Vac, Grid Support Utility Interactive Inverter ESS for Indoor ESS PCS | 1000 | 440 | 98 | [01/11/2018] | [1.00.4] | Not Applicable | N | N | Weighted Efficiency includes efficiency of 3000 kVA ABB Korea distribution transformer. | 149.25 |  |  | 740 | 830 | 900 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.9762 | 97.2102 | 97.9516 | 98.4084 | 98.507 | 98.421 | 98.2093 | 94.252 | 96.7644 | 97.5816 | 98.1856 | 98.3254 | 98.2608 | 97.9626 | 93.5872 | 96.4774 | 97.3838 | 98.0058 | 98.2088 | 98.1694 | 97.7938 | Destin Power Inc.1000SAVEEN1000-ES02H.US [440V] | 2018-11-01
Diehl AKO Stiftung | 4301 S-A [208V] | Y | N | N | 3.68 kW, 208 Vac Utility Interactive Inverter | 3.19 | 208 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.05 | 3.19 | 2.05 | 100 | 273 | 440 | 0.319 | 0.638 | 0.957 | 1.595 | 2.393 | 3.19 | 92.1 | 94.8 | 95.03 | 94.95 | 94.36 | 93.53 | 94.46 | 91.6 | 94.52 | 94.83 | 94.81 | 94.27 | 93.52 | 94.32 | 89.49 | 93.56 | 94.25 | 94.31 | 93.85 | 93.26 | 93.78 | Diehl AKO Stiftung3.194301 S-A [208V]
Diehl AKO Stiftung | 4301 S-A [240V] | Y | N | N | 3.68 kW, 240 Vac Utility Interactive Inverter | 3.68 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.22 | 3.68 | 2.22 | 100 | 298 | 440 | 0.368 | 0.736 | 1.104 | 1.84 | 2.76 | 3.68 | 91.69 | 94.79 | 95.17 | 95.3 | 94.92 | 94.17 | 94.86 | 91.29 | 94.51 | 94.98 | 95.1 | 94.98 | 94.13 | 94.79 | 89.47 | 93.58 | 94.4 | 94.69 | 94.42 | 93.91 | 94.21 | Diehl AKO Stiftung3.684301 S-A [240V]
Diehl AKO Stiftung | Platinum 100 CS-A [208V] | Y | N | N | 100 kW, 208 Vac 3-phase Utility Interactive Inverter | 100 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.82 | 94.01 | 94.82 | 95.34 | 95.08 | 93.88 | 94.82 | 90.27 | 93.75 | 94.58 | 95.15 | 95.04 | 93.75 | 94.69 | 89.04 | 92.9 | 93.9 | 94.75 | 94.31 | 93.33 | 94.02 | Diehl AKO Stiftung100Platinum 100 CS-A [208V]
Diehl AKO Stiftung | Platinum 100 CS-A [480V] | Y | N | N | 100 kW, 480 Vac 3-phase Utility Interactive Inverter | 100 | 480 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3 |  |  | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.85 | 94.14 | 94.86 | 95.17 | 95.09 | 93.98 | 94.81 | 90.33 | 93.83 | 94.68 | 95.05 | 94.99 | 93.86 | 94.66 | 88.99 | 92.99 | 93.99 | 94.61 | 94.41 | 93.54 | 94.07 | Diehl AKO Stiftung100Platinum 100 CS-A [480V]
Diehl AKO Stiftung | Platinum 100 CS-A HE [208V] | Y | N | N | 100 kW, 208 Vac 3-phase Utility Interactive Inverter | 100 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 100 | 1 | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.53 | 94.8 | 95.45 | 95.79 | 95.69 | 94.57 | 95.41 | 91.06 | 94.55 | 95.25 | 95.65 | 95.55 | 94.67 | 95.26 | 89.83 | 93.76 | 94.6 | 95.2 | 95.16 | 94.4 | 94.78 | Diehl AKO Stiftung100Platinum 100 CS-A HE [208V]
Diehl AKO Stiftung | Platinum 100 CS-A HE [480V] | Y | N | N | 100 kW, 480 Vac 3-phase Utility Interactive Inverter | 100 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2 | 100 | 2 | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.91 | 95.03 | 95.69 | 95.95 | 95.84 | 94.83 | 95.6 | 91.44 | 94.7 | 95.5 | 95.81 | 95.71 | 94.7 | 95.43 | 90.22 | 94 | 94.91 | 95.38 | 95.33 | 94.33 | 94.97 | Diehl AKO Stiftung100Platinum 100 CS-A HE [480V]
Direct Grid Technologies | DGM-460 [208V] | Y | N | N | 415W, 208 Vac Utility Interactive Inverter | 0.415 | 208 | 92 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.27 |  |  | 55 | 60 | 65 | 0.0415 | 0.083 | 0.1245 | 0.2075 | 0.3113 | 0.415 | 82.9 | 89.6 | 91.4 | 92.9 | 93.3 | 93.1 | 92.4 | 82.5 | 89.3 | 91 | 92.6 | 93.1 | 93.1 | 92.2 | 82.3 | 88.8 | 90.7 | 92.3 | 92.9 | 92.9 | 91.9 | Direct Grid Technologies0.415DGM-460 [208V]
Direct Grid Technologies | DGM-S460 [240V] | Y | N | N | 479W, 240 Vac Utility Interactive Inverter | 0.479 | 240 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.38 |  |  | 55 | 60 | 65 | 0.0479 | 0.0958 | 0.1437 | 0.2395 | 0.3593 | 0.479 | 84.3 | 91.1 | 92.4 | 93.4 | 93.7 | 93.5 | 93 | 83.9 | 90.8 | 92.1 | 93.1 | 93.5 | 93.5 | 92.7 | 83.6 | 90.7 | 91.8 | 92.9 | 93.3 | 93.3 | 92.5 | Direct Grid Technologies0.479DGM-S460 [240V]
Dow Chemical | 362589 (3.5 kW 2-string) [240V] | Y | N | N | Powerhouse 240 Vac, 2-string, 3.5 kW Utility Interactive Inverter | 3.504 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 1.39 |  |  | 100 | 300 | 420 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 86.8 | 91.5 | 93.5 | 94.1 | 95 | 94.7 | 94.1 | 87.2 | 92.3 | 93.9 | 95.1 | 95.4 | 95.3 | 94.7 | 86.1 | 90.6 | 94 | 95.3 | 95.6 | 95.6 | 94.7 | Dow Chemical3.504362589 (3.5 kW 2-string) [240V]
Dow Chemical | 362590 (3.5 kW 3-string) [240V] | Y | N | N | Powerhouse 240 Vac, 3-string, 3.5 kW Utility Interactive Inverter | 3.53 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 1.42 |  |  | 100 | 300 | 420 | 0.35 | 0.71 | 1.06 | 1.77 | 2.65 | 3.53 | 85.6 | 90.8 | 92.7 | 94.1 | 94.2 | 94 | 93.5 | 86.3 | 91.6 | 93.3 | 94.7 | 95.1 | 95.1 | 94.3 | 87 | 91.9 | 93.6 | 95 | 95.6 | 95.7 | 94.7 | Dow Chemical3.53362590 (3.5 kW 3-string) [240V]
Dow Chemical | 362591 (3.5 kW 4-string) [240V] | Y | N | N | Powerhouse 240 Vac, 4-string, 3.5 kW Utility Interactive Inverter | 3.54 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 1.14 |  |  | 100 | 300 | 420 | 0.35 | 0.71 | 1.06 | 1.77 | 2.65 | 3.54 | 84.1 | 90.3 | 92.2 | 93.8 | 94.2 | 94.1 | 93.3 | 86.9 | 91.7 | 93.2 | 94.5 | 95 | 95 | 94.2 | 86.6 | 91.5 | 93.3 | 94.8 | 95.2 | 95.3 | 94.4 | Dow Chemical3.54362591 (3.5 kW 4-string) [240V]
Dow Chemical | 362592 (5.0 kW 2-string) [240V] | Y | N | N | Powerhouse 240 Vac, 2-string, 5.0 kW Utility Interactive Inverter | 4.95 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 1.26 |  |  | 100 | 360 | 475 | 0.5 | 0.99 | 1.49 | 2.48 | 3.72 | 4.95 | 89.17 | 93.99 | 94.92 | 95.31 | 94.86 | 94.24 | 94.7 | 90.43 | 94.42 | 95.25 | 95.69 | 95.46 | 94.24 | 95.2 | 89.11 | 93.51 | 94.69 | 95.31 | 95.15 | 94.67 | 94.8 | Dow Chemical4.95362592 (5.0 kW 2-string) [240V]
DYNAPOWER COMPANY LLC | MPS-100 [480] | N | Y | N | 100 kVA, 3-phase, 4-quadrant, bidirectional, 350-600VDC, 422-528VAC Grid Support Utility Interactive Inverter with optional standalone mode. Inclusive of internal isolation transformer. | 98.861 | 480 | 93 | [12/06/2017] | [251.25] | Not Applicable | N | N |  | 803.97 |  |  | 350 | 475 | 600 | 9.8861 | 19.7722 | 29.6583 | 49.4305 | 74.1458 | 98.861 | 81.5497 | 89.9745 | 92.7648 | 95.0554 | 95.9538 | 96.2674 | 94.523 | 76.874 | 87.5246 | 90.7261 | 93.6858 | 95.0811 | 95.5789 | 93.1843 | 73.018 | 84.9646 | 89.0409 | 92.3812 | 94.007 | 94.6159 | 91.8084 | DYNAPOWER COMPANY LLC98.861MPS-100 [480] | 2018-06-15
DYNAPOWER COMPANY LLC | MPS-250 [480V] | N | Y | Y | 250 kVA, 3-phase, 4-quadrant, bidirectional, 350-600 VDC, 422-528 VAC Grid Support Utility Interactive Inverter with optional standalone mode. Inclusive of internal isolation transformer. | 248.91 | 480 | 95 | [12/06/2017];[12/06/2017] | [V251.125];[251.25] | 2018-10-15 | N | N |  | 1638.5 |  |  | 350 | 475 | 600 | 24.891 | 49.7812 | 74.6718 | 124.453 | 186.68 | 248.906 | 89.1 | 93.5 | 95 | 95.9 | 96 | 95.8 | 95.4 | 87.1 | 92.3 | 94.1 | 95.3 | 95.6 | 95.3 | 94.8 | 85.6 | 91.1 | 93 | 94.5 | 94.9 | 94.6 | 94 | DYNAPOWER COMPANY LLC248.91MPS-250 [480V] | 2018-02-15 | 2018-10-15
DYNAPOWER COMPANY LLC | MPS-250HV [480V] | N | Y | N | 250 kVA, 3-phase, 4-quadrant, bidirectional, 580-835VDC, 422-528VAC Grid Support Utility Interactive Inverter with optional standalone mode. Inclusive of internal isolation transformer. | 249.619 | 480 | 95.5 | [12/06/2017] | [252.01] | Not Applicable | N | N |  | 437.7 |  |  | 580 | 705 | 830 | 24.9619 | 49.9238 | 74.8857 | 124.8095 | 187.2142 | 249.619 | 89.1625 | 93.2778 | 94.9436 | 96.6352 | 96.5073 | 96.4981 | 95.8908 | 87.1443 | 92.741 | 94.1606 | 95.6894 | 96.3244 | 96.1982 | 95.3787 | 86.2167 | 91.8394 | 93.7002 | 95.0852 | 95.7877 | 95.8819 | 94.8141 | DYNAPOWER COMPANY LLC249.619MPS-250HV [480V] | 2018-06-15
Eaton | PV238 [208V] | Y | N | N | 3.7 kW, 208 Vac Utility Interactive Inverter | 3.69 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.21 |  |  | 100 | 360 | 470 | 0.37 | 0.74 | 1.11 | 1.85 | 2.77 | 3.69 | 94.7 | 96.6 | 97.3 | 97.7 | 97.6 | 97.4 | 97.4 | 94.1 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 92.5 | 95.5 | 96.6 | 97.2 | 97.2 | 97.2 | 96.9 | Eaton3.69PV238 [208V]
Eaton | PV240 [208V] | Y | N | N | 3.7 kW, 208 Vac Utility Interactive Inverter | 3.69 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.21 |  |  | 100 | 360 | 470 | 0.37 | 0.74 | 1.11 | 1.85 | 2.77 | 3.69 | 94.7 | 96.6 | 97.3 | 97.7 | 97.6 | 97.4 | 97.4 | 94.1 | 96.4 | 97.2 | 97.6 | 97.5 | 97.4 | 97.3 | 92.5 | 95.5 | 96.6 | 97.2 | 97.2 | 97.2 | 96.9 | Eaton3.69PV240 [208V]
Eaton | PV238 [240V] | Y | N | N | 3.7 kW, 240 Vac Utility Interactive Inverter | 3.71 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.06 |  |  | 100 | 360 | 450 | 0.37 | 0.74 | 1.11 | 1.86 | 2.78 | 3.71 | 92 | 95.1 | 96.3 | 97 | 97 | 96.9 | 96.6 | 94.1 | 96.5 | 97.4 | 97.3 | 97.1 | 97.7 | 97.1 | 92.3 | 95.8 | 96.9 | 97.5 | 97.6 | 97.6 | 97.2 | Eaton3.71PV238 [240V]
Eaton | PV238 [277V] | Y | N | N | 3.7 kW, 277 Vac Utility Interactive Inverter | 3.71 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 360 | 450 | 0.37 | 0.74 | 1.11 | 1.86 | 2.78 | 3.71 | 90.8 | 94.6 | 95.9 | 96.8 | 97 | 97 | 96.5 | 92.9 | 95.9 | 96.8 | 97.6 | 97.6 | 97.6 | 97.2 | 93.4 | 96.3 | 97.2 | 97.8 | 97.9 | 97.9 | 97.5 | Eaton3.71PV238 [277V]
Eaton | PV240 [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 3.98 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.16 |  |  | 100 | 360 | 450 | 0.4 | 0.8 | 1.19 | 1.99 | 2.99 | 3.98 | 92 | 95.1 | 96.3 | 97 | 97 | 96.9 | 96.6 | 94.1 | 96.5 | 97.4 | 97.3 | 97.1 | 97.7 | 97.1 | 92.3 | 95.8 | 96.9 | 97.5 | 97.6 | 97.6 | 97.2 | Eaton3.98PV240 [240V]
Eaton | PV240 [277V] | Y | N | N | 4 kW, 277 Vac Utility Interactive Inverter | 3.98 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 |  |  | 100 | 360 | 450 | 0.4 | 0.8 | 1.19 | 1.99 | 2.99 | 3.98 | 90.7 | 94.5 | 96 | 96.9 | 97 | 97 | 96.5 | 92.8 | 95.9 | 96.9 | 97.5 | 97.7 | 97.6 | 97.2 | 93 | 96 | 97.2 | 97.9 | 98 | 97.9 | 97.6 | Eaton3.98PV240 [277V]
Eaton | PV250 [208V] | Y | N | N | 4.5 kW, 208 Vac Utility Interactive Inverter | 4.47 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 360 | 470 | 0.45 | 0.89 | 1.34 | 2.24 | 3.35 | 4.47 | 94.5 | 96.9 | 97.5 | 97.7 | 97.6 | 97.4 | 97.4 | 94 | 96.6 | 97.2 | 97.5 | 97.5 | 97.3 | 97.2 | 92.6 | 95.4 | 96.3 | 97.1 | 97.2 | 97.1 | 96.8 | Eaton4.47PV250 [208V]
Eaton | PV250 [240V] | Y | N | N | 4.8 kW, 240 Vac Utility Interactive Inverter | 4.83 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.12 |  |  | 100 | 360 | 450 | 0.48 | 0.97 | 1.45 | 2.42 | 3.62 | 4.83 | 92.8 | 95.8 | 96.6 | 96.9 | 96.9 | 96.8 | 96.6 | 94.7 | 96.8 | 97.2 | 97.7 | 97.5 | 97.6 | 97.4 | 93.2 | 96.3 | 97 | 97.5 | 97.5 | 97.5 | 97.2 | Eaton4.83PV250 [240V]
Eaton | PV250 [277V] | Y | N | N | 4.8 kW, 277 Vac Utility Interactive Inverter | 4.83 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.09 |  |  | 100 | 360 | 450 | 0.48 | 0.97 | 1.45 | 2.42 | 3.62 | 4.83 | 91 | 94.4 | 95.7 | 96.6 | 96.9 | 96.9 | 96.3 | 93.3 | 96.3 | 97 | 97.5 | 97.6 | 97.6 | 97.3 | 94 | 96.7 | 97.3 | 97.8 | 97.9 | 97.9 | 97.6 | Eaton4.83PV250 [277V]
Eaton | PV260 [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter | 5.98 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 |  |  | 100 | 360 | 470 | 0.6 | 1.2 | 1.79 | 2.99 | 4.49 | 5.98 | 95.9 | 97.2 | 97.5 | 97.5 | 97.3 | 97 | 97.3 | 94.9 | 96.9 | 97.4 | 97.4 | 97.3 | 97 | 97.2 | 93 | 96 | 96.6 | 97.1 | 97 | 96.8 | 96.7 | Eaton5.98PV260 [208V]
Eaton | PV260 [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 360 | 450 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 91.5 | 94.7 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | 93.3 | 96.2 | 96.9 | 97.4 | 97.4 | 97.4 | 97.1 | 94.3 | 96.7 | 97.3 | 97.9 | 97.8 | 97.7 | 97.6 | Eaton6PV260 [277V]
Eaton | PV260 [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter | 6.01 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 100 | 360 | 450 | 0.6 | 1.2 | 1.8 | 3.01 | 4.51 | 6.01 | 93.8 | 96.1 | 96.4 | 96.8 | 96.8 | 96.6 | 96.6 | 95.5 | 97.1 | 97.7 | 97.7 | 97.7 | 97.4 | 97.5 | 93.9 | 96.2 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | Eaton6.01PV260 [240V]
Eaton | PV270 [240V] | Y | N | N | 7 kW, 208 Vac Utility Interactive Inverter | 6.92 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.17 |  |  | 100 | 360 | 450 | 0.69 | 1.38 | 2.08 | 3.46 | 5.19 | 6.92 | 94.3 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | 96.6 | 95.5 | 97 | 97.5 | 97.6 | 97.5 | 97.3 | 97.4 | 94 | 96.2 | 96.9 | 97.3 | 97.3 | 97.2 | 97.1 | Eaton6.92PV270 [240V]
Eaton | PV270 [208V] | Y | N | N | 7 kW, 240 Vac Utility Interactive Inverter | 6.95 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.09 |  |  | 100 | 360 | 470 | 0.7 | 1.39 | 2.09 | 3.48 | 5.21 | 6.95 | 96.1 | 97.3 | 97.5 | 97.3 | 97 | 96.5 | 97.1 | 95.6 | 97 | 97.4 | 97.1 | 96.9 | 96.6 | 97 | 93.8 | 96 | 96.6 | 96.9 | 96.7 | 96.4 | 96.6 | Eaton6.95PV270 [208V]
Eaton | PV270 [277V] | Y | N | N | 7 kW, 277 Vac Utility Interactive Inverter | 7.01 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.02 |  |  | 100 | 360 | 450 | 0.7 | 1.4 | 2.1 | 3.51 | 5.26 | 7.01 | 93.4 | 95.9 | 96.5 | 96.8 | 96.6 | 96.4 | 96.5 | 94.8 | 96.6 | 97.2 | 97.5 | 97.1 | 97.1 | 97.1 | 94.9 | 96.9 | 97.4 | 97.7 | 97.6 | 97.4 | 97.5 | Eaton7.01PV270 [277V]
Eaton | S-Max 250KW [480V] | Y | N | N | S-Max™ Series 250 kW, 480 Vac ,3-phase Utility Interactive Inverter, 300-600 Vdc input | 250 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 69.32 |  |  | 300 | 345 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 93.2 | 95.7 | 96.3 | 96.5 | 96.7 | 96.5 | 96.4 | 92.7 | 95.3 | 96 | 96.1 | 96.3 | 96.1 | 96 | 91.4 | 94.6 | 95.4 | 95.5 | 95.7 | 95.6 | 95.4 | Eaton250S-Max 250KW [480V]
Eaton | Xpert1500 | Y | N | N | 3-phase Utility Interactive Inverter | 1501 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 332.5 |  |  | 500 | 575 | 800 | 150.1 | 300.2 | 450.3 | 750.5 | 1126 | 1501 | 96.7 | 98.2 | 98.5 | 98.6 | 98.5 | 98.5 | 98.4 | 96.3 | 98 | 98.3 | 98.5 | 98.3 | 98.4 | 98.3 | 95.1 | 97.4 | 97.9 | 98.2 | 98 | 98.2 | 97.9 | Eaton1501Xpert1500
Eaton | Xpert1670 | Y | N | N | 3-phase Utility Interactive Inverter | 1671 |  | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 334.4 |  |  | 550 | 613 | 800 | 167.2 | 334.3 | 501.4 | 835.7 | 1254 | 1671 | 96.8 | 98.2 | 98.5 | 98.7 | 98.5 | 98.6 | 98.5 | 96.4 | 98 | 98.4 | 98.6 | 98.5 | 98.6 | 98.4 | 95.4 | 97.6 | 98.1 | 98.3 | 98.2 | 98.4 | 98.1 | Eaton1671Xpert1670
Elettronica Santerno | TG100NA208Y [208V] | Y | N | N | 100 kW, 208 Vac, Utility Interactive Inverter | 100 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 27.4 |  |  | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.1 | 94.5 | 95.8 | 96.5 | 96.5 | 96.5 | 96.1 | 89.5 | 94.3 | 95.7 | 96.4 | 96.5 | 96.4 | 96 | 88.6 | 93.5 | 95.2 | 96.1 | 96.2 | 96.2 | 95.6 | Elettronica Santerno100TG100NA208Y [208V]
Elettronica Santerno | TG100NA480Y [480V] | Y | N | N | 125 kW, 480 Vac, Utility Interactive Inverter | 100 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 25.3 |  |  | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.9 | 95 | 96 | 96.6 | 96.7 | 96.5 | 96.3 | 90.5 | 94.8 | 95.9 | 96.5 | 96.6 | 96.5 | 96.1 | 89.3 | 94 | 95.4 | 96.2 | 96.3 | 96.2 | 95.8 | Elettronica Santerno100TG100NA480Y [480V]
Elettronica Santerno | TG125NA208Y [208V] | Y | N | N | 125 kW, 208 Vac, Utility Interactive Inverter | 125 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 26.9 |  |  | 315 | 365 | 480 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 91.7 | 95.2 | 96.1 | 96.7 | 96.7 | 96.5 | 96.3 | 91.5 | 95 | 95.9 | 96.6 | 96.6 | 96.4 | 96.2 | 90.6 | 94.5 | 95.6 | 96.3 | 96.4 | 96.4 | 95.9 | Elettronica Santerno125TG125NA208Y [208V]
Elettronica Santerno | TG125NA480Y [480V] | Y | N | N | 125 kW, 480 Vac, Utility Interactive Inverter | 125 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 17 |  |  | 315 | 365 | 480 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 92.1 | 95.6 | 96.4 | 96.7 | 96.9 | 96.7 | 96.5 | 91.7 | 95.3 | 96.2 | 96.8 | 96.8 | 96.6 | 96.4 | 90.5 | 94.7 | 95.8 | 96.5 | 96.6 | 96.4 | 96.1 | Elettronica Santerno125TG125NA480Y [480V]
Eltek | Theia 2.0He-t UL [208V] | Y | N | N | 2.0 kW, 208 Vac Utility Interactive Inverter | 2.01 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 100 | 365 | 490 | 0.2 | 0.4 | 0.6 | 1 | 1.51 | 2.01 | 91.7 | 95.1 | 95.6 | 96.5 | 96.6 | 96.3 | 96.2 | 92.9 | 95.4 | 96.2 | 96.8 | 96.9 | 96.7 | 96.6 | 91 | 94 | 95.3 | 96.3 | 96.6 | 96.6 | 96 | Eltek2.01Theia 2.0He-t UL [208V]
Eltek | Theia 2.0He-t UL [240V] | Y | N | N | 2.0 kW, 240 Vac Utility Interactive Inverter | 2.01 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.97 |  |  | 100 | 375 | 490 | 0.2 | 0.4 | 0.6 | 1.01 | 1.51 | 2.01 | 91.9 | 95.3 | 96.1 | 96.7 | 96.8 | 96.7 | 96.4 | 91.2 | 95.2 | 96.1 | 96.9 | 97.1 | 97.1 | 96.6 | 91 | 94.5 | 95.6 | 96.6 | 97 | 97.1 | 96.4 | Eltek2.01Theia 2.0He-t UL [240V]
Eltek | Theia 2.9He-t UL [240V] | Y | N | N | 2.9 kW, 240 Vac Utility Interactive Inverter | 2.9 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.98 |  |  | 100 | 375 | 490 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.9 | 93.4 | 95.9 | 96.5 | 96.8 | 96.5 | 96.1 | 96.4 | 93.3 | 96.1 | 96.8 | 97.2 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | Eltek2.9Theia 2.9He-t UL [240V]
Eltek | Theia 2.9He-t UL [208V] | Y | N | N | 2.9 kW, 208 Vac Utility Interactive Inverter | 2.91 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.92 |  |  | 100 | 365 | 490 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.91 | 93.7 | 95.9 | 96.2 | 96.5 | 96.3 | 95.6 | 96.2 | 93.9 | 96.1 | 96.6 | 96.8 | 96.6 | 96.3 | 96.5 | 91.9 | 95.1 | 96 | 96.5 | 96.5 | 96.3 | 96.2 | Eltek2.91Theia 2.9He-t UL [208V]
Eltek | Theia 3.8He-t UL [208V] | Y | N | N | 3.8 kW, 208 Vac Utility Interactive Inverter | 3.81 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.77 |  |  | 100 | 360 | 500 | 0.381 | 0.762 | 1.143 | 1.905 | 2.858 | 3.81 | 94.62 | 96.34 | 96.7 | 96.68 | 96.21 | 95.57 | 96.28 | 94.76 | 96.49 | 96.91 | 97.03 | 96.77 | 96.53 | 96.74 | 93.09 | 95.63 | 96.36 | 96.79 | 96.73 | 96.51 | 96.49 | Eltek3.81Theia 3.8He-t UL [208V]
Eltek | Theia 3.8He-t UL [240V] | Y | N | N | 3.8 kW, 240 Vac Utility Interactive Inverter | 3.81 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 100 | 370 | 500 | 0.381 | 0.762 | 1.143 | 1.905 | 2.858 | 3.81 | 94.77 | 96.6 | 96.9 | 96.88 | 96.53 | 95.99 | 96.55 | 94.57 | 96.59 | 97.08 | 97.27 | 97.17 | 96.84 | 97.03 | 93.25 | 95.84 | 96.59 | 97.02 | 97.06 | 96.92 | 96.78 | Eltek3.81Theia 3.8He-t UL [240V]
Eltek | Theia 4.4He-t UL [208V] | Y | N | N | 4.4 kW, 208 Vac Utility Interactive Inverter | 4.4 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.8 |  |  | 100 | 360 | 500 | 0.4402 | 0.8804 | 1.321 | 2.201 | 3.302 | 4.402 | 95.08 | 96.51 | 96.69 | 96.45 | 95.87 | 95.09 | 96.05 | 95.24 | 96.64 | 96.98 | 96.99 | 96.71 | 96.25 | 96.71 | 93.55 | 95.89 | 96.43 | 96.74 | 96.52 | 96.17 | 96.38 | Eltek4.4Theia 4.4He-t UL [208V]
Eltek | Theia 4.4He-t UL [240V] | Y | N | N | 4.4 kW, 240 Vac Utility Interactive Inverter | 4.4 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.97 |  |  | 100 | 370 | 500 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 95.3 | 96.75 | 96.95 | 96.75 | 96.4 | 95.59 | 96.47 | 95.22 | 96.8 | 97.18 | 97.24 | 97.09 | 96.74 | 97.02 | 93.92 | 96.15 | 96.69 | 97.02 | 96.98 | 96.73 | 96.78 | Eltek4.4Theia 4.4He-t UL [240V]
Emerson Network Power | SPV-4.0AIUSO [240V] | Y | N | N | 4 kW, 240 Vac, 1-phase Utility Interactive Inverter | 4 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 1.26 |  |  | 100 | 360 | 475 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 88.5 | 93.2 | 94.5 | 95.2 | 95.2 | 94.8 | 94.7 | 88.7 | 93.7 | 94.8 | 95.6 | 95.6 | 94.8 | 95.1 | 87.3 | 92.6 | 94.1 | 95.2 | 95.3 | 95.1 | 94.7 | Emerson Network Power4SPV-4.0AIUSO [240V]
Emerson Network Power | SPV-4.5AIUSO [240V] | Y | N | N | 4.5 kW, 240 Vac, 1-phase Utility Interactive Inverter | 4.49 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 1.26 |  |  | 100 | 360 | 475 | 0.45 | 0.9 | 1.35 | 2.24 | 3.36 | 4.49 | 88.88 | 93.68 | 94.71 | 95.29 | 95.06 | 94.49 | 94.7 | 89.9 | 94.07 | 95.07 | 95.66 | 95.57 | 94.49 | 95.2 | 88.73 | 93.09 | 94.42 | 95.25 | 95.27 | 94.89 | 94.8 | Emerson Network Power4.49SPV-4.5AIUSO [240V]
Emerson Network Power | SPV-5.0AIUSO [240V] | Y | N | N | 5 kW, 240 Vac, 1-phase Utility Interactive Inverter | 4.95 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 1.26 |  |  | 100 | 360 | 475 | 0.5 | 0.99 | 1.49 | 2.48 | 3.72 | 4.95 | 89.17 | 93.99 | 94.92 | 95.31 | 94.86 | 94.24 | 94.7 | 90.43 | 94.42 | 95.25 | 95.69 | 95.46 | 94.24 | 95.2 | 89.11 | 93.51 | 94.69 | 95.31 | 95.15 | 94.67 | 94.8 | Emerson Network Power4.95SPV-5.0AIUSO [240V]
Enecsys | SMI-220 | Y | N | N | 1-phase Microinverter with built-in monitoring system | 0.22 |  | 93 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.06 |  |  | 30 | 34 | 42 | 0.022 | 0.044 | 0.066 | 0.11 | 0.165 | 0.22 | 84.9 | 91.38 | 93.21 | 94.16 | 94.17 | 93.59 | 93.51 | 82.55 | 90.46 | 92.55 | 93.97 | 94.18 | 93.75 | 93.27 | 78.52 | 88.13 | 90.82 | 92.99 | 93.85 | 93.93 | 92.41 | Enecsys0.22SMI-220
Enecsys | SMI-240-60 | Y | N | N | 1-phase Microinverter with built-in monitoring system | 0.225 |  | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 |  |  | 23 | 29 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 84.63 | 90.56 | 93.22 | 94.73 | 94.78 | 94.36 | 93.94 | 80.74 | 88.03 | 91.68 | 94.05 | 94.82 | 94.68 | 93.37 | 77.8 | 86.84 | 89.61 | 92.98 | 94.34 | 94.56 | 92.46 | Enecsys0.225SMI-240-60
Enecsys | 240-60-xx | Y | N | N | 1-phase Microinverter, where xx = MP, MM, or MM-S | 0.24 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 |  |  | 24 | 29 | 35 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 92.6 | 95 | 95.6 | 96.4 | 96.3 | 95.9 | 96 | 90.7 | 94.3 | 95.3 | 96.1 | 96.4 | 96.2 | 95.8 | 89.6 | 93.5 | 94.7 | 95.6 | 96.2 | 96.2 | 95.5 | Enecsys0.24240-60-xx
Enecsys | 250NL | Y | N | N | 0.25 kW, 1-phase Utility Interactive Microinverter | 0.25 |  | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.08 |  |  | 24 | 29 | 35 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 92.4 | 95.2 | 96 | 96 | 95.4 | 94.5 | 95.4 | 90.5 | 94.1 | 95.4 | 96 | 95.7 | 95.2 | 95.4 | 89.4 | 93.4 | 94.8 | 95.7 | 95.8 | 95.4 | 95.3 | Enecsys0.25250NL
Enecsys | 260-60-xx | Y | N | N | 1-phase Microinverter, where xx = MP, MM, or MM-S | 0.26 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 |  |  | 24 | 29 | 35 | 0.03 | 0.05 | 0.08 | 0.13 | 0.2 | 0.26 | 93 | 95.2 | 95.6 | 96.4 | 96.2 | 95.7 | 96 | 91.2 | 94.6 | 95.3 | 96.2 | 96.3 | 96 | 95.9 | 90.2 | 93.6 | 94.8 | 95.7 | 96.2 | 96.1 | 95.5 | Enecsys0.26260-60-xx
Enecsys | SMI-280-72 | Y | N | N | 1-phase Microinverter with built-in monitoring system | 0.265 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 |  |  | 30 | 34 | 42 | 0.0265 | 0.053 | 0.0795 | 0.1325 | 0.1988 | 0.265 | 85.57 | 92.75 | 94.36 | 95.41 | 95.29 | 94.87 | 94.67 | 82.99 | 91.53 | 93.74 | 95.17 | 95.35 | 95.08 | 94.42 | 80.03 | 89.45 | 92.28 | 94.42 | 95.1 | 95.12 | 93.73 | Enecsys0.265SMI-280-72
Enecsys | 280-60-xx | Y | N | N | 1-phase Microinverter, where xx = MP, MM, or MM-S | 0.28 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 |  |  | 24 | 29 | 35 | 0.03 | 0.06 | 0.08 | 0.14 | 0.21 | 0.28 | 93.3 | 95.3 | 95.6 | 96.4 | 96.1 | 95.5 | 95.9 | 91.4 | 94.7 | 95.4 | 96.4 | 96.3 | 95.9 | 95.9 | 90.5 | 93.9 | 94.8 | 95.8 | 96.1 | 96 | 95.6 | Enecsys0.28280-60-xx
Enecsys | 300-60-xx | Y | N | N | 1-phase Microinverter, where xx = MP, MM, or MM-S | 0.3 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 |  |  | 24 | 29 | 35 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 93.6 | 95.4 | 95.7 | 96.4 | 95.9 | 95.3 | 95.9 | 91.9 | 94.8 | 95.4 | 96.4 | 96.2 | 95.8 | 95.9 | 91.1 | 94.1 | 95 | 96 | 96.1 | 96 | 95.7 | Enecsys0.3300-60-xx
Enecsys | SMI-360-72 | Y | N | N | 1-phase Microinverter with built-in monitoring system | 0.34 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 |  |  | 30 | 34 | 42 | 0.034 | 0.068 | 0.102 | 0.17 | 0.255 | 0.34 | 89.15 | 93.97 | 94.95 | 95.41 | 95 | 94.49 | 94.77 | 87.1 | 93.07 | 94.48 | 95.4 | 95.14 | 94.58 | 94.66 | 83.7 | 91.1 | 93.35 | 94.94 | 95.13 | 94.95 | 94.21 | Enecsys0.34SMI-360-72
Enecsys | SMI-480-60 | Y | N | N | 1-phase Microinverter with built-in monitoring system | 0.455 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.05 |  |  | 24 | 29 | 35 | 0.0455 | 0.091 | 0.1365 | 0.2275 | 0.3413 | 0.455 | 91.9 | 94.3 | 95.1 | 95 | 94.4 | 93.8 | 94.5 | 90.5 | 93 | 94.3 | 95.1 | 95 | 94.4 | 94.6 | 89.2 | 91.3 | 93.1 | 94 | 94.6 | 94.4 | 93.9 | Enecsys0.455SMI-480-60
EnluxSolar | EL-300 | Y | N | N | 300 W Utility Interactive Inverter | 0.3 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.064 |  |  | 25 | 30 | 35 | 0.0305 | 0.061 | 0.0915 | 0.1525 | 0.2288 | 0.305 | 92.8 | 95.8 | 96.5 | 96.6 | 96.1 | 95.5 | 96.1 | 92.4 | 95.6 | 96.4 | 96.6 | 96.2 | 95.5 | 96.1 | 92 | 95.5 | 96.3 | 96.5 | 96.2 | 95.6 | 96 | EnluxSolar0.3EL-300 | 2017-03
Enphase Energy Inc. | M175-24-208-Sxx [208V] | Y | N | N | 175 W, 24 Vdc, 208 Vac, Utility Interactive modular Inverter, where xx = 01 or 02. | 0.175 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.56 | 0.175 | 0.56 | 25 | 32.5 | 40 | 0.0175 | 0.035 | 0.0525 | 0.0875 | 0.1313 | 0.175 | 91.9 | 93.5 | 94.2 | 94.6 | 94.5 | 94.1 | 94.3 | 91.6 | 92.9 | 94 | 94.6 | 94.9 | 94.7 | 94.5 | 91.3 | 92.3 | 93.3 | 94.3 | 94.9 | 94.9 | 94.3 | Enphase Energy Inc.0.175M175-24-208-Sxx [208V]
Enphase Energy Inc. | M175-24-208-Sxx-NA [208V] | Y | N | N | 175 W, 24 Vdc, 208 Vac Inverter, xx = connector types, -NA if North American | 0.175 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.56 | 0.175 | 0.56 | 25 | 32.5 | 40 | 0.0175 | 0.035 | 0.0525 | 0.0875 | 0.1313 | 0.175 | 91.9 | 93.5 | 94.2 | 94.6 | 94.5 | 94.1 | 94.3 | 91.6 | 92.9 | 94 | 94.6 | 94.9 | 94.7 | 94.5 | 91.3 | 92.3 | 93.3 | 94.3 | 94.9 | 94.9 | 94.3 | Enphase Energy Inc.0.175M175-24-208-Sxx-NA [208V]
Enphase Energy Inc. | M175-24-240-Sxx [240V] | Y | N | N | 175 W, 24 Vdc, 240 Vac, Utility Interactive modular Inverter, where xx = 01 or 02. | 0.175 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.58 | 0.175 | 0.58 | 25 | 32.5 | 40 | 0.0175 | 0.035 | 0.0525 | 0.0875 | 0.1313 | 0.175 | 91.2 | 93 | 94.1 | 94.6 | 94.6 | 94.3 | 94.3 | 90.7 | 92.6 | 93.8 | 94.4 | 94.9 | 94.9 | 94.4 | 90.2 | 91.9 | 93.1 | 94 | 94.7 | 94.9 | 94.1 | Enphase Energy Inc.0.175M175-24-240-Sxx [240V]
Enphase Energy Inc. | M175-24-240-Sxx-NA [240V] | Y | N | N | 175 W, 24 Vdc, 240 Vac Inverter, xx = connector types, -NA if North American | 0.175 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.58 | 0.175 | 0.58 | 25 | 32.5 | 40 | 0.0175 | 0.035 | 0.0525 | 0.0875 | 0.1313 | 0.175 | 91.2 | 93 | 94.1 | 94.6 | 94.6 | 94.3 | 94.3 | 90.7 | 92.6 | 93.8 | 94.4 | 94.9 | 94.9 | 94.4 | 90.2 | 91.9 | 93.1 | 94 | 94.7 | 94.9 | 94.1 | Enphase Energy Inc.0.175M175-24-240-Sxx-NA [240V]
Enphase Energy Inc. | M190-72-208-Sxx [208V] | Y | N | N | 190 W, 32Vdc, 208 Vac, Utility Interactive modular Inverter, where xx = 11, 12, or 13. | 0.19 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Enphase Energy Inc.0.19M190-72-208-Sxx [208V]
Enphase Energy Inc. | M190-72-208-Sxx-NA [208V] | Y | N | N | 190 W, 24 Vdc, 208 Vac Inverter, xx = connector types, -NA if North American | 0.19 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Enphase Energy Inc.0.19M190-72-208-Sxx-NA [208V]
Enphase Energy Inc. | M190-72-240-Sxx [240V] | Y | N | N | 175 W, 24 Vdc, 240 Vac Inverter, xx = connector types, -NA if North American | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Enphase Energy Inc.0.19M190-72-240-Sxx [240V]
Enphase Energy Inc. | M190-72-240-Sxx-NA [240V] | Y | N | N | 190 W, 24 Vdc, 240 Vac Inverter, xx = connector types, -NA if North American | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Enphase Energy Inc.0.19M190-72-240-Sxx-NA [240V]
Enphase Energy Inc. | M200-32-208-Sxx [240V] | Y | N | N | 175 W, 24 Vdc, 240 Vac Inverter, xx = connector types, -NA if North American | 0.2 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.56 | 0.2 | 0.56 | 44 | 54.5 | 65 | 0.02 | 0.04 | 0.06 | 0.1 | 0.15 | 0.2 | 92.5 | 94.2 | 94.6 | 95.2 | 95.3 | 95.1 | 95 | 92.4 | 94.3 | 94.5 | 95 | 95.4 | 95.3 | 95 | 91.9 | 94.1 | 94.2 | 94.6 | 95.2 | 95.3 | 94.8 | Enphase Energy Inc.0.2M200-32-208-Sxx [240V]
Enphase Energy Inc. | M200-32-208-Sxx-NA [208V] | Y | N | N | 200 W, 52.5 Vdc, 208 Vac, xx = connector types, -NA if North American | 0.2 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.56 | 0.2 | 0.56 | 44 | 54.5 | 65 | 0.02 | 0.04 | 0.06 | 0.1 | 0.15 | 0.2 | 92.5 | 94.2 | 94.6 | 95.2 | 95.3 | 95.1 | 95 | 92.4 | 94.3 | 94.5 | 95 | 95.4 | 95.3 | 95 | 91.9 | 94.1 | 94.2 | 94.6 | 95.2 | 95.3 | 94.8 | Enphase Energy Inc.0.2M200-32-208-Sxx-NA [208V]
Enphase Energy Inc. | M200-32-240-Sxx [240V] | Y | N | N | 200 W, 52.5 Vdc, 240 Vac, Utility Interactive modular Inverter, where xx = 01 or 02. | 0.2 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.48 | 0.2 | 0.48 | 44 | 54.5 | 65 | 0.02 | 0.04 | 0.06 | 0.1 | 0.15 | 0.2 | 92.5 | 94.2 | 94.6 | 95.2 | 95.3 | 95.1 | 95 | 92.4 | 94.3 | 94.5 | 95 | 95.4 | 95.3 | 95 | 91.9 | 94.1 | 94.2 | 94.6 | 95.2 | 95.3 | 94.8 | Enphase Energy Inc.0.2M200-32-240-Sxx [240V]
Enphase Energy Inc. | M200-32-240-Sxx-NA [240V] | Y | N | N | 200 W, 52.5 Vdc, 240 Vac, xx = connector types, -NA if North American | 0.2 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.48 | 0.2 | 0.48 | 44 | 54.5 | 65 | 0.02 | 0.04 | 0.06 | 0.1 | 0.15 | 0.2 | 92.5 | 94.2 | 94.6 | 95.2 | 95.3 | 95.1 | 95 | 92.4 | 94.3 | 94.5 | 95 | 95.4 | 95.3 | 95 | 91.9 | 94.1 | 94.2 | 94.6 | 95.2 | 95.3 | 94.8 | Enphase Energy Inc.0.2M200-32-240-Sxx-NA [240V]
Enphase Energy Inc. | M210-84-208-Sxx [208V] | Y | N | N | 210 W, 40.5 Vdc, 208 Vac, Utility Interactive modular Inverter, where xx = 11, 12, or 13. | 0.21 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0 | 0.21 | 0 | 31 | 40.5 | 50 | 0.021 | 0.042 | 0.063 | 0.105 | 0.1575 | 0.21 | 94 | 95.3 | 95.5 | 95.8 | 95.3 | 94.6 | 95.3 | 94.1 | 95.3 | 95.5 | 95.9 | 95.8 | 95.3 | 95.6 | 94 | 95 | 95.5 | 95.8 | 95.9 | 95.6 | 95.7 | Enphase Energy Inc.0.21M210-84-208-Sxx [208V]
Enphase Energy Inc. | M210-84-208-Sxx-NA [208V] | Y | N | N | 210 W, 40.5 Vdc, 208 Vac Inverter, xx = connector types, -NA if North American | 0.21 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0 | 0.21 | 0 | 31 | 40.5 | 50 | 0.021 | 0.042 | 0.063 | 0.105 | 0.1575 | 0.21 | 94 | 95.3 | 95.5 | 95.8 | 95.3 | 94.6 | 95.3 | 94.1 | 95.3 | 95.5 | 95.9 | 95.8 | 95.3 | 95.6 | 94 | 95 | 95.5 | 95.8 | 95.9 | 95.6 | 95.7 | Enphase Energy Inc.0.21M210-84-208-Sxx-NA [208V]
Enphase Energy Inc. | M210-84-240-Sxx [240V] | Y | N | N | 210 W, 40.5 Vdc, 240 Vac, Utility Interactive modular Inverter, where xx = 11, 12, or 13. | 0.21 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.01 | 0.21 | 0.01 | 31 | 40.5 | 50 | 0.021 | 0.042 | 0.063 | 0.105 | 0.1575 | 0.21 | 94 | 95.3 | 95.4 | 95.8 | 95.5 | 94.8 | 95.4 | 94.2 | 95.3 | 95.6 | 95.9 | 95.8 | 95.4 | 95.7 | 94.2 | 95.2 | 95.5 | 95.8 | 95.9 | 95.7 | 95.7 | Enphase Energy Inc.0.21M210-84-240-Sxx [240V]
Enphase Energy Inc. | M210-84-240-Sxx-NA [240V] | Y | N | N | 210 W, 40.5 Vdc, 240 Vac Inverter, xx = connector types, -NA if North American | 0.21 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.01 | 0.21 | 0.01 | 31 | 40.5 | 50 | 0.021 | 0.042 | 0.063 | 0.105 | 0.1575 | 0.21 | 94 | 95.3 | 95.4 | 95.8 | 95.5 | 94.8 | 95.4 | 94.2 | 95.3 | 95.6 | 95.9 | 95.8 | 95.4 | 95.7 | 94.2 | 95.2 | 95.5 | 95.8 | 95.9 | 95.7 | 95.7 | Enphase Energy Inc.0.21M210-84-240-Sxx-NA [240V]
Enphase Energy Inc. | M215-60-2LL-S2x [208V] | Y | N | N | 215 W, 208 Vac Inverter, S2x are connector types | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Enphase Energy Inc.0.215M215-60-2LL-S2x [208V]
Enphase Energy Inc. | M215-60-2LL-S2x [240V] | Y | N | N | 215 W, 240 Vac Inverter, S2x are connector types | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Enphase Energy Inc.0.215M215-60-2LL-S2x [240V]
Enphase Energy Inc. | M215-60-2LL-S2x-IG [208V] | Y | N | N | 208 Vac Microinverter for use with ungrounded arrays, where x = 1, 2, 3, 4, or 5 | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.05 | 0.215 | 0.05 | 22 | 29 | 36 | 0.0215 | 0.043 | 0.0645 | 0.1075 | 0.1613 | 0.215 | 94.64 | 95.53 | 95.86 | 95.92 | 95.53 | 94.79 | 95.58 | 94.64 | 95.62 | 95.92 | 96.11 | 96.01 | 95.61 | 95.93 | 94.6 | 95.53 | 95.83 | 96.1 | 96.15 | 95.94 | 96 | Enphase Energy Inc.0.215M215-60-2LL-S2x-IG [208V]
Enphase Energy Inc. | M215-60-2LL-S2x-IG [240V] | Y | N | N | 240 Vac Microinverter for use with ungrounded arrays, where x = 1, 2, 3, 4, or 5 | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.05 | 0.215 | 0.05 | 22 | 29 | 36 | 0.0215 | 0.043 | 0.0645 | 0.1075 | 0.1613 | 0.215 | 94.66 | 95.6 | 95.99 | 96.13 | 95.89 | 95.3 | 95.86 | 94.69 | 95.68 | 96.05 | 96.26 | 96.27 | 96 | 96.13 | 94.62 | 95.6 | 95.97 | 96.27 | 96.34 | 96.24 | 96.17 | Enphase Energy Inc.0.215M215-60-2LL-S2x-IG [240V]
Enphase Energy Inc. | M215-60-2LL-S2x-IG-NA [208V] | Y | N | N | 215 W, 208 Vac Inverter, where S2x are connector types | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.05 | 0.215 | 0.05 | 22 | 29 | 36 | 0.0215 | 0.043 | 0.0645 | 0.1075 | 0.1613 | 0.215 | 94.64 | 95.53 | 95.86 | 95.92 | 95.53 | 94.79 | 95.58 | 94.64 | 95.62 | 95.92 | 96.11 | 96.01 | 95.61 | 95.93 | 94.6 | 95.53 | 95.83 | 96.1 | 96.15 | 95.94 | 96 | Enphase Energy Inc.0.215M215-60-2LL-S2x-IG-NA [208V]
Enphase Energy Inc. | M215-60-2LL-S2x-IG-NA [240V] | Y | N | N | 215 W, 240 Vac Inverter, where S2x are connector types | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.05 | 0.215 | 0.05 | 22 | 29 | 36 | 0.0215 | 0.043 | 0.0645 | 0.1075 | 0.1613 | 0.215 | 94.66 | 95.6 | 95.99 | 96.13 | 95.89 | 95.3 | 95.86 | 94.69 | 95.68 | 96.05 | 96.26 | 96.27 | 96 | 96.13 | 94.62 | 95.6 | 95.97 | 96.27 | 96.34 | 96.24 | 96.17 | Enphase Energy Inc.0.215M215-60-2LL-S2x-IG-NA [240V]
Enphase Energy Inc. | M215-60-2LL-S2x-IG-ZC [208V] | Y | N | N | 215 W, 208 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.05 | 0.215 | 0.05 | 22 | 29 | 36 | 0.0215 | 0.043 | 0.0645 | 0.1075 | 0.1613 | 0.215 | 94.64 | 95.53 | 95.86 | 95.92 | 95.53 | 94.79 | 95.58 | 94.64 | 95.62 | 95.92 | 96.11 | 96.01 | 95.61 | 95.93 | 94.6 | 95.53 | 95.83 | 96.1 | 96.15 | 95.94 | 96 | Enphase Energy Inc.0.215M215-60-2LL-S2x-IG-ZC [208V]
Enphase Energy Inc. | M215-60-2LL-S2x-IG-ZC [240V] | Y | N | N | 215 W, 240 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.05 | 0.215 | 0.05 | 22 | 29 | 36 | 0.0215 | 0.043 | 0.0645 | 0.1075 | 0.1613 | 0.215 | 94.66 | 95.6 | 95.99 | 96.13 | 95.89 | 95.3 | 95.86 | 94.69 | 95.68 | 96.05 | 96.26 | 96.27 | 96 | 96.13 | 94.62 | 95.6 | 95.97 | 96.27 | 96.34 | 96.24 | 96.17 | Enphase Energy Inc.0.215M215-60-2LL-S2x-IG-ZC [240V]
Enphase Energy Inc. | M215-60-2LL-S2x-IG-ZC-NA [208V] | Y | N | N | 215 W, 208 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.05 | 0.215 | 0.05 | 22 | 29 | 36 | 0.0215 | 0.043 | 0.0645 | 0.1075 | 0.1613 | 0.215 | 94.64 | 95.53 | 95.86 | 95.92 | 95.53 | 94.79 | 95.58 | 94.64 | 95.62 | 95.92 | 96.11 | 96.01 | 95.61 | 95.93 | 94.6 | 95.53 | 95.83 | 96.1 | 96.15 | 95.94 | 96 | Enphase Energy Inc.0.215M215-60-2LL-S2x-IG-ZC-NA [208V]
Enphase Energy Inc. | M215-60-2LL-S2x-IG-ZC-NA [240V] | Y | N | N | 215 W, 240 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.05 | 0.215 | 0.05 | 22 | 29 | 36 | 0.0215 | 0.043 | 0.0645 | 0.1075 | 0.1613 | 0.215 | 94.66 | 95.6 | 95.99 | 96.13 | 95.89 | 95.3 | 95.86 | 94.69 | 95.68 | 96.05 | 96.26 | 96.27 | 96 | 96.13 | 94.62 | 95.6 | 95.97 | 96.27 | 96.34 | 96.24 | 96.17 | Enphase Energy Inc.0.215M215-60-2LL-S2x-IG-ZC-NA [240V]
Enphase Energy Inc. | M215-60-2LL-S2x-NA [208V] | Y | N | N | 215 W, 208 Vac Inverter, where S2x are connector types | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Enphase Energy Inc.0.215M215-60-2LL-S2x-NA [208V]
Enphase Energy Inc. | M215-60-2LL-S2x-NA [240V] | Y | N | N | 215 W, 240 Vac Inverter, where S2x are connector types | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | [34 empty] | Enphase Energy Inc.0.215M215-60-2LL-S2x-NA [240V]
Enphase Energy Inc. | M215-60-2LL-S2x-ZC [240V] | Y | N | N | 215 W, 240 Vac Inverter, where S2x are connector types | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Enphase Energy Inc.0.215M215-60-2LL-S2x-ZC [240V]
Enphase Energy Inc. | M215-60-2LL-S2x-ZC-NA [208V] | Y | N | N | 215 W, 208 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Enphase Energy Inc.0.215M215-60-2LL-S2x-ZC-NA [208V]
Enphase Energy Inc. | M215-60-2LL-S2x-ZC-NA [240V] | Y | N | N | 215 W, 240 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Enphase Energy Inc.0.215M215-60-2LL-S2x-ZC-NA [240V]
Enphase Energy Inc. | M215-60-SIE-S2x [208V] | Y | N | N | 215 W, 208 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Enphase Energy Inc.0.215M215-60-SIE-S2x [208V]
Enphase Energy Inc. | M215-60-SIE-S2x [240V] | Y | N | N | 215 W, 240 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Enphase Energy Inc.0.215M215-60-SIE-S2x [240V]
Enphase Energy Inc. | M215-60-SIE-S2x-NA [208V] | Y | N | N | 215 W, 208 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Enphase Energy Inc.0.215M215-60-SIE-S2x-NA [208V]
Enphase Energy Inc. | M215-60-SIE-S2x-NA [240V] | Y | N | N | 215 W, 240 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Enphase Energy Inc.0.215M215-60-SIE-S2x-NA [240V]
Enphase Energy Inc. | M215-60-SIE-S2x-ZC [208V] | Y | N | N | 215 W, 208 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Enphase Energy Inc.0.215M215-60-SIE-S2x-ZC [208V]
Enphase Energy Inc. | M215-60-SIE-S2x-ZC [240V] | Y | N | N | 215 W, 240 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Enphase Energy Inc.0.215M215-60-SIE-S2x-ZC [240V]
Enphase Energy Inc. | M215-60-SIE-S2x-ZC-NA [208V] | Y | N | N | 215 W, 208 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Enphase Energy Inc.0.215M215-60-SIE-S2x-ZC-NA [208V]
Enphase Energy Inc. | M215-60-SIE-S2x-ZC-NA [240V] | Y | N | N | 215 W, 240 Vac Inverter, where S2x are connector types, and ZC is mount | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Enphase Energy Inc.0.215M215-60-SIE-S2x-ZC-NA [240V]
Enphase Energy Inc. | S230-60-LL-x [208V] | Y | Y | Y | 230 W, 240 Vac, Grid Support Utility Interactive Microinverter, where x = 2, 3, 4, or 5 and may be followed by -US | 0.22 | 208 | 97 | [8/14/2017] | [v00.36.01] | 2018-10-15 | N | Y |  | 0.051 |  |  | 27 | 32 | 37 | 0.02 | 0.04 | 0.07 | 0.11 | 0.17 | 0.22 | 94.9 | 96.5 | 96.4 | 97.2 | 97.2 | 96.9 | 97 | 94.9 | 96.4 | 96.1 | 97.1 | 97.1 | 96.8 | 96.8 | 94.8 | 96.3 | 95.8 | 96.9 | 97 | 96.7 | 96.7 | Enphase Energy Inc.0.22S230-60-LL-x [208V] | 2017-10-16 | 2018-10-15
Enphase Energy Inc. | S230-60-LL-x [240V] | Y | Y | Y | 230 W, 240 Vac, Grid Support Utility Interactive Microinverter, where x = 2, 3, 4, or 5 and may be followed by -US | 0.22 | 240 | 97 | [8/14/2017] | [v00.36.01] | 2018-10-15 | N | Y |  | 0.051 |  |  | 27 | 32 | 37 | 0.02 | 0.04 | 0.07 | 0.11 | 0.17 | 0.22 | 95 | 96.4 | 96.2 | 97.4 | 97.5 | 97.4 | 97.2 | 95 | 96.5 | 95.8 | 97.2 | 97.3 | 97.2 | 97 | 94.9 | 96.4 | 95.4 | 96.9 | 97.2 | 97.2 | 96.8 | Enphase Energy Inc.0.22S230-60-LL-x [240V] | 2017-10-16 | 2018-10-15
Enphase Energy Inc. | IQ6-60-ACM-US [208V] | Y | Y | Y | 230 W, 208 Vac Grid Support Utility Interactive Microinverter for ACPV Module applications | 0.23 | 208 | 97 | [6/29/2017];[12/28/2017] | [V01.06.03];[V02.12.00] | 2018-10-15 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.1975 | 95.7125 | 96.3485 | 97.2626 | 97.2603 | 96.9175 | 96.9343 | 94.4525 | 95.865 | 96.241 | 97.1193 | 97.1982 | 96.9745 | 96.8791 | 94.1798 | 95.6904 | 96.0834 | 96.9677 | 97.0876 | 96.9175 | 96.7472 | Enphase Energy Inc.0.23IQ6-60-ACM-US [208V] [SI1] | 2017-08-01 | 2018-10-15
Enphase Energy Inc. | IQ6-60-ACM-US [240V] | Y | Y | Y | 230W, 240 Vac Grid Support Utility Interactive Microinverter for ACPV Module applications | 0.23 | 240 | 97 | [6/29/2017];[12/28/2017] | [V01.06.03];[V02.12.00] | 2018-10-15 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | Enphase Energy Inc.0.23IQ6-60-ACM-US [240V] [SI1] | 2017-08-01 | 2018-10-15
Enphase Energy Inc. | IQ6-60-x-US [208V] | Y | Y | Y | 230 W, 208 Vac Grid Support Utility Interactive Microinverter where x = DC Connector type = 2 or 5 | 0.23 | 208 | 97 | [6/29/2017];[12/28/2017] | [V01.06.03];[V02.12.00] | 2018-10-15 | N | Y |  | 0.02 |  |  | 27 | 32 | 37 | 23 | 46 | 69 | 115 | 172.5 | 230 | 94.1975 | 95.7125 | 96.3485 | 97.2626 | 97.2603 | 96.9175 | 96.9343 | 94.4525 | 95.865 | 96.241 | 97.1193 | 97.1982 | 96.9745 | 96.8791 | 94.1798 | 95.6904 | 96.0834 | 96.9677 | 97.0876 | 96.9175 | 96.7472 | Enphase Energy Inc.0.23IQ6-60-x-US [208V] [SI1] | 2017-08-01 | 2018-10-15
Enphase Energy Inc. | IQ6-60-x-US [240V] | Y | Y | Y | 230 W, 240 Vac Grid Support Utility Interactive Microinverter where x = DC Connector type = 2 or 5 | 0.23 | 240 | 97 | [6/29/2017];[12/28/2017] | [V01.06.03];[V02.12.00] | 2018-10-15 | N | Y |  | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2748 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.111 | Enphase Energy Inc.0.23IQ6-60-x-US [240V] [SI1] | 2017-08-01 | 2018-10-15
Enphase Energy Inc. | IQ7-60-x-ACM-US [208V] | Y | Y | Y | 240 VA, 208 Vac Grid Support Utility Interactive Microinverter for use in ACPV Module applications where x = DC Connector type = B or blank | 0.24 | 208 | 97 | [10/30/2017];[05/25/2018];[06/26/2018] | [V02.10.00];[V02.12.00];[V02.14.02] | 2018-10-15 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | Enphase Energy Inc.0.24IQ7-60-ACM-US [208V] [SI1] | 2017-12-15 | 2018-10-15
Enphase Energy Inc. | IQ7-60-x-ACM-US [240V] | Y | Y | Y | 240 VA, 240 Vac Grid Support Utility Interactive Microinverter for use in ACPV Module applications where x = DC Connector type = B or blank | 0.24 | 240 | 97 | [10/30/2017];[05/25/2018];[06/26/2018] | [V02.10.00];[V02.12.00];[V02.14.03] | 2018-10-15 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | Enphase Energy Inc.0.24IQ7-60-ACM-US [240V] [SI1] | 2017-12-15 | 2018-10-15
Enphase Energy Inc. | IQ7-60-x-US [208V] | Y | Y | Y | 240 VA, 208 Vac Grid Support Utility Interactive Microinverter where x = DC Connector type = 2, 5, or B | 0.24 | 208 | 97 | [10/30/2017];[05/25/2018];[06/26/2018] | [V02.10.00];[V02.12.00];[V02.14.02] | 2018-10-15 | N | Y |  | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 94.2043 | 96.2264 | 97.0215 | 97.5539 | 97.4142 | 96.9598 | 97.1859 | 93.3248 | 95.7344 | 96.7563 | 97.4639 | 97.4153 | 97.0564 | 97.0808 | 92.4192 | 95.0959 | 96.5384 | 97.3538 | 97.3374 | 97.0253 | 96.9205 | Enphase Energy Inc.0.24IQ7-60-x-US [208V] [SI1] | 2017-12-15 | 2018-10-15
Enphase Energy Inc. | IQ7-60-x-US [240V] | Y | Y | Y | 240 VA, 240 Vac Grid Support Utility Interactive Microinverter where x = DC Connector type = 2, 5, or B | 0.24 | 240 | 97 | [10/30/2017];[05/25/2018];[06/26/2018] | [V02.10.00];[V02.12.00];[V02.14.03] | 2018-10-15 | N | Y |  | 0.025 |  |  | 27 | 32 | 37 | 0.024 | 0.048 | 0.072 | 0.12 | 0.18 | 0.24 | 93.9453 | 96.08 | 96.8145 | 97.4746 | 97.4192 | 97.0288 | 97.1328 | 92.9907 | 95.6588 | 96.5049 | 97.5523 | 97.615 | 97.4087 | 97.1755 | 92.0062 | 95.0264 | 96.2309 | 97.3813 | 97.5438 | 97.4107 | 96.9981 | Enphase Energy Inc.0.24IQ7-60-x-US [240V] [SI1] | 2017-12-15 | 2018-10-15
Enphase Energy Inc. | M250-60-2LL-S2x (-ZC) (-NA) [208V] | Y | N | N | 240 W, 208 Vac Inverter, where S2x are connector types, ZC is mount, and NA is for North American | 0.24 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 |  |  | 27 | 32 | 38 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 94.7 | 95.7 | 96.1 | 96.3 | 96 | 95.5 | 96 | 94.7 | 95.7 | 96 | 96.3 | 96.2 | 95.8 | 96.1 | 94.5 | 95.5 | 95.8 | 96.1 | 96.2 | 96 | 96 | Enphase Energy Inc.0.24M250-60-2LL-S2x (-ZC) (-NA) [208V]
Enphase Energy Inc. | M250-60-2LL-S2x (-ZC) (-NA) [240V] | Y | N | N | 240 W, 240 Vac Inverter, where S2x are connector types, ZC is mount, and NA is for North American | 0.24 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.05 |  |  | 27 | 32 | 38 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 95.6 | 96 | 96.3 | 96.5 | 96.4 | 96.1 | 96.4 | 95 | 96 | 96.2 | 96.5 | 96.6 | 96.4 | 96.4 | 94.9 | 96 | 96 | 96.4 | 96.5 | 96.5 | 96.4 | Enphase Energy Inc.0.24M250-60-2LL-S2x (-ZC) (-NA) [240V]
Enphase Energy Inc. | M250-72-2LL-S2x [208V] | Y | N | N | 240 W, 208 Vac Microinverter, where x = 2, 3, 4, or 5 and may be followed by -US | 0.24 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 |  |  | 27 | 37 | 48 | 24 | 48 | 72 | 120 | 180 | 240 | 95.6 | 96.4 | 96.6 | 96.6 | 96.3 | 95.6 | 96.3 | 95.4 | 96.2 | 96.4 | 96.6 | 96.6 | 96.2 | 96.5 | 95.1 | 95.8 | 96 | 96.4 | 96.5 | 96.3 | 96.3 | Enphase Energy Inc.0.24M250-72-2LL-S2x [208V]
Enphase Energy Inc. | M250-72-2LL-S2x [240V] | Y | N | N | 240 W, 240 Vac Microinverter, where x = 2, 3, 4 ,or 5 and may be followed by -US | 0.24 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 |  |  | 27 | 37 | 48 | 24 | 48 | 72 | 120 | 180 | 240 | 95.7 | 96.4 | 96.6 | 96.6 | 96.3 | 95.8 | 96.4 | 95.5 | 96.3 | 96.5 | 96.7 | 96.6 | 96.3 | 96.5 | 95.3 | 96 | 96.2 | 96.5 | 96.5 | 96.4 | 96.4 | Enphase Energy Inc.0.24M250-72-2LL-S2x [240V]
Enphase Energy Inc. | C250-72-2LN-S2 | Y | N | N | 0.247 kW Utility Interactive Microinverter | 0.247 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.071 |  |  | 27.5 | 39 | 47.5 | 0.02 | 0.05 | 0.07 | 0.12 | 0.19 | 0.25 | 95.6 | 96.2 | 96.4 | 96.6 | 96.4 | 95.9 | 96.4 | 95.1 | 96.1 | 96.4 | 96.6 | 96.6 | 96.5 | 96.5 | 94.9 | 96 | 96.1 | 96.5 | 96.6 | 96.6 | 96.4 | Enphase Energy Inc.0.247C250-72-2LN-S2
Enphase Energy Inc. | IQ6PLUS-ACB-LL [240V] | Y | Y | Y | 270 VA, 240 Vac Grid Support Utility Interactive Microinverter | 0.27 | 240 | 95.5 | [12/28/2017] | [v02.12.00] | 2018-10-15 | N | Y |  | 0.07 |  |  | 23 | 25 | 28 | 0.027 | 0.054 | 0.081 | 0.135 | 0.2025 | 0.27 | 85.8903 | 93.6164 | 95.4627 | 95.9769 | 95.5783 | 94.8032 | 95.1238 | 85.8003 | 93.4691 | 95.4058 | 96.1485 | 95.8765 | 95.2295 | 95.3213 | 85.5189 | 93.1183 | 95.1904 | 96.1928 | 96.0669 | 95.5951 | 95.3952 | Enphase Energy Inc.0.27IQ6PLUS-ACB-LL [240V] | 2018-05-15 | 2018-10-15
Enphase Energy Inc. | S280-60-LL-x [208V] | Y | Y | Y | 270 W, 208 Vac, Grid Support Utility Interactive Microinverter, where x = 2, 3, 4 , or 5 and may be followed by -US | 0.27 | 208 | 96.5 | [8/14/2017] | [v00.36.01] | 2018-10-15 | N | Y |  | 0.051 |  |  | 27 | 32 | 37 | 0.03 | 0.05 | 0.08 | 0.14 | 0.2 | 0.27 | 95 | 96.1 | 96.5 | 96.9 | 96.7 | 96.2 | 96.6 | 95 | 96.1 | 96.1 | 96.7 | 96.6 | 96.2 | 96.5 | 94.9 | 95.7 | 95.8 | 96.6 | 96.5 | 96.1 | 96.3 | Enphase Energy Inc.0.27S280-60-LL-x [208V] | 2017-10-16 | 2018-10-15
Enphase Energy Inc. | S280-60-LL-x [240V] | Y | Y | Y | 270 W, 240 Vac, Grid Support Utility Interactive Microinverter, where x = 2, 3, 4, or 5 and may be followed by -US | 0.27 | 240 | 97 | [8/14/2017] | [v00.36.01] | 2018-10-15 | N | Y |  | 0.062 |  |  | 27 | 32 | 37 | 0.03 | 0.05 | 0.08 | 0.14 | 0.2 | 0.27 | 95.2 | 96.5 | 96.9 | 97.3 | 97.3 | 97 | 97.1 | 95.3 | 96.5 | 96.7 | 97.1 | 97.2 | 96.9 | 97 | 95.1 | 96.1 | 96 | 96.9 | 97.1 | 96.9 | 96.8 | Enphase Energy Inc.0.27S280-60-LL-x [240V] | 2017-10-16 | 2018-10-15
Enphase Energy Inc. | IQ6PLUS-72-ACM-US [208V] | Y | Y | Y | 280 W, 208 Vac Grid Support Utility Interactive Microinverter for ACPV Module applications | 0.28 | 208 | 97 | [6/29/2017];[12/28/2017] | [V01.06.03];[V02.12.00] | 2018-10-15 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules including LG Electronics Inc. LGxxxE1K-A5 and LGxxxE1C-A5, where xxx = 315, 320, 325, 330, or 335. | 0.02 |  |  | 27 | 36 | 45 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | Enphase Energy Inc.0.28IQ6PLUS-72-ACM-US [208V] [SI1] | 2017-08-15 | 2018-10-15
Enphase Energy Inc. | IQ6PLUS-72-ACM-US [240V] | Y | Y | Y | 280 W, 240 Vac Grid Support Utility Interactive Microinverter for ACPV Module applications | 0.28 | 240 | 97 | [6/29/2017];[12/28/2017] | [V01.06.03];[V02.12.00] | 2018-10-15 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules including LG Electronics Inc. LGxxxE1K-A5 and LGxxxE1C-A5, where xxx = 315, 320, 325, 330, or 335. | 0.02 |  |  | 27 | 36 | 45 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | Enphase Energy Inc.0.28IQ6PLUS-72-ACM-US [240V] [SI1] | 2017-08-15 | 2018-10-15
Enphase Energy Inc. | IQ6PLUS-72-x-US [208V] | Y | Y | Y | 280 W, 208 Vac Grid Support Utility Interactive Microinverter where x = DC Connector type = 2 or 5 | 0.28 | 208 | 97 | [6/29/2017];[12/28/2017] | [V01.06.03];[V02.12.00] | 2018-10-15 | N | Y |  | 0.02 |  |  | 27 | 36 | 45 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | Enphase Energy Inc.0.28IQ6PLUS-72-x-US [208V] [SI1] | 2017-08-01 | 2018-10-15
Enphase Energy Inc. | IQ6PLUS-72-x-US [240V] | Y | Y | Y | 280 W, 240 Vac Grid Support Utility Interactive Microinverter where x = DC Connector type = 2 or 5 | 0.28 | 240 | 97 | [6/29/2017];[12/28/2017] | [V01.06.03];[V02.12.00] | 2018-10-15 | N | Y |  | 0.02 |  |  | 27 | 36 | 45 | 0.028 | 0.056 | 0.084 | 0.14 | 0.21 | 0.28 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | Enphase Energy Inc.0.28IQ6PLUS-72-x-US [240V] [SI1] | 2017-08-01 | 2018-10-15
Enphase Energy Inc. | IQ7PLUS-72-x-ACM-US [208V] | Y | Y | Y | 290 VA, 208 Vac Grid Support Utility Interactive Microinverter for use in ACPV Module applications where x = DC Connector type = B or blank | 0.29 | 208 | 96.5 | [10/30/2017];[05/25/2018];[06/26/2018] | [V02.10.00];[V02.12.00];[V02.14.04] | 2018-10-15 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 36 | 45 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 96.8699 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 96.7446 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734 | 96.542 | Enphase Energy Inc.0.29IQ7PLUS-72-ACM-US [208V] [SI1] | 2017-12-15 | 2018-10-15
Enphase Energy Inc. | IQ7PLUS-72-x-ACM-US [240V] | Y | Y | Y | 290 VA, 240 Vac Grid Support Utility Interactive Microinverter for use in ACPV Module applications where x = DC Connector type = B or blank | 0.29 | 240 | 97 | [10/30/2017];[05/25/2018];[06/26/2018] | [V02.10.00];[V02.12.00];[V02.14.05] | 2018-10-15 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 36 | 45 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | Enphase Energy Inc.0.29IQ7PLUS-72-ACM-US [240V] [SI1] | 2017-12-15 | 2018-10-15
Enphase Energy Inc. | IQ7PLUS-72-x-US [208V] | Y | Y | Y | 290 VA, 208 Vac Grid Support Utility Interactive Microinverter where x = DC Connector type = 2, 5, or B | 0.29 | 208 | 96.5 | [10/30/2017];[05/25/2018];[06/26/2018] | [V02.10.00];[V02.12.00];[V02.14.04] | 2018-10-15 | N | Y |  | 0.025 |  |  | 27 | 36 | 45 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 94.9112 | 96.2467 | 97.1081 | 97.2516 | 96.9257 | 96.2942 | 96.8699 | 93.9563 | 95.3145 | 96.7282 | 97.1587 | 96.9578 | 96.445 | 96.7446 | 93.1479 | 94.59 | 96.3899 | 96.9798 | 96.8592 | 96.3734 | 96.542 | Enphase Energy Inc.0.29IQ7PLUS-72-x-US [208V] [SI1] | 2017-12-15 | 2018-10-15
Enphase Energy Inc. | IQ7PLUS-72-x-US [240V] | Y | Y | Y | 290 VA, 240 Vac Grid Support Utility Interactive Microinverter where x = DC Connector type = 2, 5, or B | 0.29 | 240 | 97 | [10/30/2017];[05/25/2018];[06/26/2018] | [V02.10.00];[V02.12.00];[V02.14.05] | 2018-10-15 | N | Y |  | 0.025 |  |  | 27 | 36 | 45 | 0.029 | 0.058 | 0.087 | 0.145 | 0.2175 | 0.29 | 95.0036 | 96.2457 | 97.1477 | 97.4291 | 97.1641 | 96.6039 | 97.0574 | 94.162 | 95.5752 | 96.7802 | 97.4953 | 97.4428 | 97.1569 | 97.1354 | 93.3214 | 94.8059 | 96.394 | 97.2732 | 97.3095 | 97.0757 | 96.8956 | Enphase Energy Inc.0.29IQ7PLUS-72-x-US [240V] [SI1] | 2017-12-15 | 2018-10-15
Enphase Energy Inc. | IQ7X-96-x-ACM-US [208V] | Y | Y | Y | 315 VA, 208 Vac Grid Support Utility Interactive microinverter for ACPV Module applications where x = DC Connector type = B or blank | 0.315 | 208 | 97 | [10/30/2017];[05/25/2018];[06/26/2018] | [V02.10.00];[V02.12.00];[V02.14.06] | 2018-10-15 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 97.151 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 97.2587 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197 | 97.2095 | Enphase Energy Inc.0.315IQ7X-96-x-ACM-US [208V] | 2018-06-01 | 2018-10-15
Enphase Energy Inc. | IQ7X-96-x-ACM-US [240V] | Y | Y | Y | 315 VA, 240 Vac Grid Support Utility Interactive microinverter for ACPV Module applications where x = DC Connector type = B or blank | 0.315 | 240 | 97.5 | [10/30/2017];[05/25/2018];[06/26/2018] | [V02.10.00];[V02.12.00];[V02.14.07] | 2018-10-15 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | Enphase Energy Inc.0.315IQ7X-96-x-ACM-US [240V] | 2018-06-01 | 2018-10-15
Enphase Energy Inc. | IQ7X-96-x-US [208V] | Y | Y | Y | 315 VA, 208 Vac Grid Support Utility Interactive Microinverter where x = DC Connector type = 2, 5, or B | 0.315 | 208 | 97 | [10/30/2017];[05/25/2018];[06/26/2018] | [V02.10.00];[V02.12.00];[V02.14.06] | 2018-10-15 | N | Y |  | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 97.151 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 97.2587 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197 | 97.2095 | Enphase Energy Inc.0.315IQ7X-96-x-US [208V] | 2018-06-01 | 2018-10-15
Enphase Energy Inc. | IQ7X-96-x-US [240V] | Y | Y | Y | 315 VA, 240 Vac Grid Support Utility Interactive Microinverter where x = DC Connector type = 2, 5, or B | 0.315 | 240 | 97.5 | [10/30/2017];[05/25/2018];[06/26/2018] | [V02.10.00];[V02.12.00];[V02.14.07] | 2018-10-15 | N | Y |  | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | Enphase Energy Inc.0.315IQ7X-96-x-US [240V] | 2018-06-01 | 2018-10-15
Enphase Energy Inc. | IQ7XS-96-y-ACM-z [208V] | Y | Y | Y | 315 VA, 208 Vac Grid Support Utility Interactive microinverter for ACPV Module applications, where y = DC Connector type = B or blank, and z = US or blank | 0.315 | 208 | 97 | [08/29/2018] | [V04.14.05] | 2018-10-15 | N | Y | This component is specific to SunPower ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 90.4836 | 96.6628 | 97.0999 | 97.6357 | 97.5242 | 97.1035 | 97.151 | 95.4142 | 96.4654 | 96.9008 | 97.542 | 97.4613 | 97.05 | 97.2587 | 95.2705 | 96.3335 | 96.8135 | 97.5025 | 97.4299 | 97.0197 | 97.2095 | Enphase Energy Inc.0.315IQ7XS-96-y-ACM-z [208V] | 2018-10-01 | 2018-10-15
Enphase Energy Inc. | IQ7XS-96-y-ACM-z [240V] | Y | Y | Y | 315 VA, 240 Vac Grid Support Utility Interactive microinverter for ACPV Module applications, where y = DC Connector type = B or blank, and z = US or blank | 0.315 | 240 | 97.5 | [08/29/2018] | [V04.14.05] | 2018-10-15 | N | Y | This component is specific to SunPower ACPV modules and is not available as an individual unit. | 0.021 |  |  | 53 | 60 | 64 | 0.0315 | 0.063 | 0.0945 | 0.1575 | 0.23625 | 0.315 | 95.7348 | 96.8402 | 96.9962 | 97.7627 | 97.7558 | 97.4686 | 97.5251 | 95.6103 | 96.6782 | 96.7549 | 97.6667 | 97.7392 | 97.5137 | 97.4564 | 95.4365 | 96.4979 | 96.6571 | 97.6038 | 97.7001 | 97.4825 | 97.3932 | Enphase Energy Inc.0.315IQ7XS-96-y-ACM-z [240V] | 2018-10-01 | 2018-10-15
Enphase Energy Inc. | D380-72-208-S1x [208V] | Y | N | N | 380 W, 208 Vac, Utility Interactive modular Inverter, 1x = connector types | 0.38 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.5 | 0.38 | 0.5 | 22 | 32 | 40 | 0.038 | 0.076 | 0.114 | 0.19 | 0.285 | 0.38 | 93.7 | 94.9 | 95.2 | 95.2 | 94.7 | 93.6 | 94.8 | 93.6 | 95 | 95.1 | 95.6 | 95.4 | 94.9 | 95.3 | 93.5 | 94.7 | 95.1 | 95.4 | 95.5 | 95.3 | 95.3 | Enphase Energy Inc.0.38D380-72-208-S1x [208V]
Enphase Energy Inc. | D380-72-240-S1x [240V] | Y | N | N | 380 W, 240 Vac, Utility Interactive modular Inverter, 1x are connector types | 0.38 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.5 | 0.38 | 0.5 | 22 | 32 | 40 | 0.038 | 0.076 | 0.114 | 0.19 | 0.285 | 0.38 | 93.8 | 94.9 | 95.1 | 95.3 | 94.8 | 93.8 | 94.9 | 93.7 | 94.9 | 95.2 | 95.6 | 95.5 | 95.1 | 95.3 | 93.7 | 94.9 | 95 | 95.4 | 95.6 | 95.4 | 95.4 | Enphase Energy Inc.0.38D380-72-240-S1x [240V]
Enphase Energy Inc. | D380-72-2LL-S1x [208V] | Y | N | N | 380 W, 208 Vac Inverter, x = connector types, -NA if North American | 0.38 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.05 | 0.38 | 0.05 | 22 | 32 | 40 | 0.038 | 0.076 | 0.114 | 0.19 | 0.285 | 0.38 | 93.71 | 94.91 | 95.17 | 95.18 | 94.7 | 93.58 | 94.77 | 93.65 | 95.03 | 95.13 | 95.55 | 95.37 | 94.93 | 95.27 | 93.45 | 94.74 | 95.07 | 95.39 | 95.54 | 95.29 | 95.31 | Enphase Energy Inc.0.38D380-72-2LL-S1x [208V]
Enphase Energy Inc. | D380-72-2LL-S1x [240V] | Y | N | N | 380 W, 240 Vac Inverter, x = connector types, -NA if North American | 0.38 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.05 | 0.38 | 0.05 | 22 | 32 | 40 | 0.038 | 0.076 | 0.114 | 0.19 | 0.285 | 0.38 | 93.71 | 94.91 | 95.17 | 95.18 | 94.7 | 93.58 | 94.77 | 93.65 | 95.03 | 95.13 | 95.55 | 95.37 | 94.93 | 95.27 | 93.45 | 94.74 | 95.07 | 95.39 | 95.54 | 95.29 | 95.31 | Enphase Energy Inc.0.38D380-72-2LL-S1x [240V]
Enphase Energy Inc. | D380-72-2LL-S1x-NA [208V] | Y | N | N | 380 W, 208 Vac Inverter, x = connector types, -NA if North American | 0.38 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.05 | 0.38 | 0.05 | 22 | 32 | 40 | 0.038 | 0.076 | 0.114 | 0.19 | 0.285 | 0.38 | 93.71 | 94.91 | 95.17 | 95.18 | 94.7 | 93.58 | 94.77 | 93.65 | 95.03 | 95.13 | 95.55 | 95.37 | 94.93 | 95.27 | 93.45 | 94.74 | 95.07 | 95.39 | 95.54 | 95.29 | 95.31 | Enphase Energy Inc.0.38D380-72-2LL-S1x-NA [208V]
Enphase Energy Inc. | D380-72-2LL-S1x-NA [240V] | Y | N | N | 380 W, 208 Vac Inverter, x = connector types, -NA if North American | 0.38 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | [34 empty] | Enphase Energy Inc.0.38D380-72-2LL-S1x-NA [240V]
Eoplly New Energy Technology | EP156M/60-230S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156M/60-230S AC [208V]
Eoplly New Energy Technology | EP156M/60-230S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156M/60-230S AC [240V]
Eoplly New Energy Technology | EP156M/60-235S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156M/60-235S AC [208V]
Eoplly New Energy Technology | EP156M/60-235S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156M/60-235S AC [240V]
Eoplly New Energy Technology | EP156M/60-240S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156M/60-240S AC [208V]
Eoplly New Energy Technology | EP156M/60-240S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156M/60-240S AC [240V]
Eoplly New Energy Technology | EP156M/60-245S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156M/60-245S AC [208V]
Eoplly New Energy Technology | EP156M/60-245S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156M/60-245S AC [240V]
Eoplly New Energy Technology | EP156M/60-250S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156M/60-250S AC [208V]
Eoplly New Energy Technology | EP156M/60-250S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156M/60-250S AC [240V]
Eoplly New Energy Technology | EP156M/60-255S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156M/60-255S AC [208V]
Eoplly New Energy Technology | EP156M/60-255S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156M/60-255S AC [240V]
Eoplly New Energy Technology | EP156M/60-260S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156M/60-260S AC [208V]
Eoplly New Energy Technology | EP156M/60-260S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156M/60-260S AC [240V]
Eoplly New Energy Technology | EP156MB/60-230S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156MB/60-230S AC [208V]
Eoplly New Energy Technology | EP156MB/60-230S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156MB/60-230S AC [240V]
Eoplly New Energy Technology | EP156MB/60-235S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156MB/60-235S AC [208V]
Eoplly New Energy Technology | EP156MB/60-235S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156MB/60-235S AC [240V]
Eoplly New Energy Technology | EP156MB/60-240S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156MB/60-240S AC [208V]
Eoplly New Energy Technology | EP156MB/60-240S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156MB/60-240S AC [240V]
Eoplly New Energy Technology | EP156MB/60-245S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156MB/60-245S AC [208V]
Eoplly New Energy Technology | EP156MB/60-245S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156MB/60-245S AC [240V]
Eoplly New Energy Technology | EP156MB/60-250S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156MB/60-250S AC [208V]
Eoplly New Energy Technology | EP156MB/60-250S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156MB/60-250S AC [240V]
Eoplly New Energy Technology | EP156P/60-225S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156P/60-225S AC [208V]
Eoplly New Energy Technology | EP156P/60-225S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156P/60-225S AC [240V]
Eoplly New Energy Technology | EP156P/60-230S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156P/60-230S AC [208V]
Eoplly New Energy Technology | EP156P/60-230S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156P/60-230S AC [240V]
Eoplly New Energy Technology | EP156P/60-235S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156P/60-235S AC [208V]
Eoplly New Energy Technology | EP156P/60-235S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156P/60-235S AC [240V]
Eoplly New Energy Technology | EP156P/60-240S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156P/60-240S AC [208V]
Eoplly New Energy Technology | EP156P/60-240S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156P/60-240S AC [240V]
Eoplly New Energy Technology | EP156P/60-245S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156P/60-245S AC [208V]
Eoplly New Energy Technology | EP156P/60-245S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156P/60-245S AC [240V]
Eoplly New Energy Technology | EP156P/60-250S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156P/60-250S AC [208V]
Eoplly New Energy Technology | EP156P/60-250S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156P/60-250S AC [240V]
Eoplly New Energy Technology | EP156P/60-255S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156P/60-255S AC [208V]
Eoplly New Energy Technology | EP156P/60-255S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156P/60-255S AC [240V]
Eoplly New Energy Technology | EP156P/60-260S AC [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156P/60-260S AC [208V]
Eoplly New Energy Technology | EP156P/60-260S AC [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Eoplly New Energy Technology0.215EP156P/60-260S AC [240V]
Eoplly New Energy Technology | EP156M/60-250 AC [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Eoplly New Energy Technology0.24EP156M/60-250 AC [208V]
Eoplly New Energy Technology | EP156M/60-250 AC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Eoplly New Energy Technology0.24EP156M/60-250 AC [240V]
Eoplly New Energy Technology | EP156M/60-255 AC [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Eoplly New Energy Technology0.24EP156M/60-255 AC [208V]
Eoplly New Energy Technology | EP156M/60-255 AC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Eoplly New Energy Technology0.24EP156M/60-255 AC [240V]
Eoplly New Energy Technology | EP156M/60-260 AC [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Eoplly New Energy Technology0.24EP156M/60-260 AC [208V]
Eoplly New Energy Technology | EP156M/60-260 AC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Eoplly New Energy Technology0.24EP156M/60-260 AC [240V]
Eoplly New Energy Technology | EP156MB/60-240 AC [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Eoplly New Energy Technology0.24EP156MB/60-240 AC [208V]
Eoplly New Energy Technology | EP156MB/60-240 AC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Eoplly New Energy Technology0.24EP156MB/60-240 AC [240V]
Eoplly New Energy Technology | EP156MB/60-245 AC [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Eoplly New Energy Technology0.24EP156MB/60-245 AC [208V]
Eoplly New Energy Technology | EP156MB/60-245 AC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Eoplly New Energy Technology0.24EP156MB/60-245 AC [240V]
Eoplly New Energy Technology | EP156P/60-240 AC [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Eoplly New Energy Technology0.24EP156P/60-240 AC [208V]
Eoplly New Energy Technology | EP156P/60-240 AC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Eoplly New Energy Technology0.24EP156P/60-240 AC [240V]
Eoplly New Energy Technology | EP156P/60-245 AC [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Eoplly New Energy Technology0.24EP156P/60-245 AC [208V]
Eoplly New Energy Technology | EP156P/60-245 AC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Eoplly New Energy Technology0.24EP156P/60-245 AC [240V]
ET Solar Industry | ET-P660245BAC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | ET Solar Industry0.24ET-P660245BAC [240V]
ET Solar Industry | ET-P660245BBAC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | ET Solar Industry0.24ET-P660245BBAC [240V]
ET Solar Industry | ET-P660245BBZAC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | ET Solar Industry0.24ET-P660245BBZAC [240V]
ET Solar Industry | ET-P660245WBZAC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | ET Solar Industry0.24ET-P660245WBZAC [240V]
ET Solar Industry | ET-P660250 WBAC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.22 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | ET Solar Industry0.24ET-P660250 WBAC [240V]
ET Solar Industry | ET-P660250 WBZAC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | ET Solar Industry0.24ET-P660250 WBZAC [240V]
ET Solar Industry | ET-P660250BAC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | ET Solar Industry0.24ET-P660250BAC [240V]
ET Solar Industry | ET-P660250BBAC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | ET Solar Industry0.24ET-P660250BBAC [240V]
ET Solar Industry | ET-P660250BBZAC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | ET Solar Industry0.24ET-P660250BBZAC [240V]
ET Solar Industry | ET-P660255BBAC | Y | N | N | 240 W, 1-phase Microinverter | 0.24 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | ET Solar Industry0.24ET-P660255BBAC
ET Solar Industry | ET-P660255BBZAC | Y | N | N | 240 W, 1-phase Microinverter | 0.24 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | ET Solar Industry0.24ET-P660255BBZAC
ET Solar Industry | ET-P660255WBAC | Y | N | N | 240 W, 1-phase Microinverter | 0.24 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | ET Solar Industry0.24ET-P660255WBAC
ET Solar Industry | ET-P660255WBZAC | Y | N | N | 240 W, 1-phase Microinverter | 0.24 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | ET Solar Industry0.24ET-P660255WBZAC
ET Solar Industry | ET-P660255WWAC | Y | N | N | 240 W, 1-phase Microinverter | 0.24 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | ET Solar Industry0.24ET-P660255WWAC
ET Solar Industry | ET-P660255WWZAC | Y | N | N | 240 W, 1-phase Microinverter | 0.24 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | ET Solar Industry0.24ET-P660255WWZAC
ET Solar Industry | ET-P660260WBAC | Y | N | N | 240 W, 1-phase Microinverter | 0.24 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | ET Solar Industry0.24ET-P660260WBAC
ET Solar Industry | ET-P660260WBZAC | Y | N | N | 240 W, 1-phase Microinverter | 0.24 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | ET Solar Industry0.24ET-P660260WBZAC
ET Solar Industry | ET-P660260WWAC | Y | N | N | 240 W, 1-phase Microinverter | 0.24 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | ET Solar Industry0.24ET-P660260WWAC
ET Solar Industry | ET-P660260WWZAC | Y | N | N | 240 W, 1-phase Microinverter | 0.24 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | ET Solar Industry0.24ET-P660260WWZAC
ETM Electromatic | 290-480-60 | Y | N | N | Utility Interactive Bi-Directional Inverter | 279.3 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 900 |  |  | 372 | 451 | 546 | 27.93 | 55.86 | 83.79 | 139.6 | 209.5 | 279.3 | 98.1 | 98.1 | 97.8 | 97.1 | 96.2 | 95.7 | 96.7 | 98.6 | 98.3 | 97.9 | 97.1 | 96.2 | 95.4 | 96.7 | 98.9 | 98.4 | 98 | 97.1 | 96.2 | 95.3 | 96.8 | ETM Electromatic279.3290-480-60
E-Village Solar | EVS1100EVR [120V] | Y | N | N | 1100W, 120 Vac Utility Interactive Inverter | 1.1 | 120 | 90.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 182 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 81.8 | 89 | 90.9 | 92.1 | 92.4 | 92.5 | 91.6 | 79.9 | 88 | 90.1 | 91.7 | 92.2 | 92.3 | 91.1 | 74.8 | 84.7 | 87.8 | 90 | 90.8 | 91.1 | 89.3 | E-Village Solar1.1EVS1100EVR [120V]
E-Village Solar | EVS2000EVR [240V] | Y | N | N | 2000 W, 240 Vac Utility Interactive Inverter | 2 | 240 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 199 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.3 | 91.7 | 92.6 | 93.5 | 93.2 | 93 | 92.9 | 85.7 | 90.8 | 92.1 | 92.9 | 92.9 | 92.6 | 92.4 | 82.4 | 88.8 | 90.5 | 91.6 | 91.8 | 91.6 | 91.1 | E-Village Solar2EVS2000EVR [240V]
E-Village Solar | EVS2500 [240V] | Y | N | N | 2500 W, 240 Vac Utility Interactive Inverter | 2.5 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2 | E-Village Solar2.5EVS2500 [240V]
E-Village Solar | EVS3000 [240V] | Y | N | N | 3000 W, 240 Vac Utility Interactive Inverter | 3 | 240 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.63 |  |  | 100 | 222.5 | 380 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 88.9 | 92.9 | 93.8 | 94.3 | 94.2 | 93.9 | 93.9 | 87.9 | 92.5 | 93.5 | 94.1 | 94 | 93.8 | 93.7 | 84.9 | 90.9 | 92.4 | 93.3 | 93.2 | 93 | 92.7 | E-Village Solar3EVS3000 [240V]
E-Village Solar | EVS3500 [240V] | Y | N | N | 3500 W, 240 Vac Utility Interactive Inverter | 3.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.86 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5 | E-Village Solar3.5EVS3500 [240V]
E-Village Solar | EVS4600 [208V] | Y | N | N | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 |  |  | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95 | E-Village Solar4.6EVS4600 [208V]
E-Village Solar | EVS4800 [240V] | Y | N | N | 4800 W, 240 Vac Utility Interactive Inverter | 4.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.1 |  |  | 100 | 263 | 400 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 86.8 | 93.5 | 95.5 | 97 | 97.2 | 97.1 | 96.4 | 85.5 | 92.9 | 95 | 96.7 | 96.9 | 96.8 | 96 | 84.5 | 91.5 | 93.9 | 95.9 | 96.2 | 96.1 | 95.1 | E-Village Solar4.8EVS4800 [240V]
E-Village Solar | EVS5200 [208V] | Y | N | N | 5200 W, 240 Vac Utility Interactive Inverter | 5.2 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 |  |  | 100 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5 | E-Village Solar5.2EVS5200 [208V]
Exeltech | AC2-1-2-6-5-XX [120V] | Y | N | N | 212 W, 120 Vac Inverter, where xx is connection option | 0.212 | 120 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16 | Exeltech0.212AC2-1-2-6-5-XX [120V]
Exeltech | AC2-1-B-6-5-XX [120V] | Y | N | N | 212 W, 120 Vac Inverter, where xx is connection option | 0.212 | 120 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16 | Exeltech0.212AC2-1-B-6-5-XX [120V]
Exeltech | AC2-1-C-6-5-XX [120V] | Y | N | N | 212 W, 120 Vac Inverter, where xx is connection option | 0.212 | 120 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16 | Exeltech0.212AC2-1-C-6-5-XX [120V]
Exeltech | AC2-1-L-6-5-XX [120V] | Y | N | N | 212 W, 120 Vac Inverter, where xx is connection option | 0.212 | 120 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16 | Exeltech0.212AC2-1-L-6-5-XX [120V]
Exeltech | AM24-1-B-6-0-00 [120V] | Y | N | N | 212W, 120 Vac Inverter | 0.212 | 120 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16 | Exeltech0.212AM24-1-B-6-0-00 [120V]
Exeltech | XLGT18A60 [120V] | Y | N | N | 1.8 kW, 120 Vac Utility Interactive Inverter | 1.8 | 120 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.16 |  |  | 100 | 290 | 450 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 96.55 | 97.49 | 97.81 | 97.53 | 96.98 | 96.13 | 97.16 | 96.09 | 97.25 | 97.43 | 97.29 | 96.75 | 95.98 | 96.9 | 93.81 | 96.04 | 96.48 | 94.73 | 94.95 | 95.09 | 95.11 | Exeltech1.8XLGT18A60 [120V]
Exeltech | XLGT18A60-01 [120V] | Y | N | N | 1.8 kW, 120 Vac Utility Interactive Inverter (-01 for disconnect) | 1.8 | 120 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.16 |  |  | 100 | 290 | 450 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 96.55 | 97.49 | 97.81 | 97.53 | 96.98 | 96.13 | 97.16 | 96.09 | 97.25 | 97.43 | 97.29 | 96.75 | 95.98 | 96.9 | 93.81 | 96.04 | 96.48 | 94.73 | 94.95 | 95.09 | 95.11 | Exeltech1.8XLGT18A60-01 [120V]
Flextronics Industrial | FLV-IA-6.0S1UA | Y | N | N | 6.0 kW, transformerless Utility Interactive Inverter | 6 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 6 |  |  | 200 | 380 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.9 | 96.1 | 96.8 | 97.3 | 97.3 | 96.5 | 97.1 | 95.5 | 97 | 97.4 | 97.4 | 97.4 | 98 | 97.3 | 95.3 | 96.9 | 97.5 | 97.6 | 97.6 | 97.6 | 97.4 | Flextronics Industrial6FLV-IA-6.0S1UA | 2017-05
Flextronics Industrial | FLV-IA-7.0S1UA | Y | N | N | 7.0 kW, transformerless Utility Interactive Inverter | 7 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 7 |  |  | 250 | 380 | 500 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 95 | 96.2 | 96.8 | 97.4 | 97.4 | 96.5 | 97.1 | 95.6 | 97 | 97.4 | 97.5 | 97.5 | 97 | 97.4 | 95.3 | 97 | 97.5 | 97.7 | 97.6 | 97.6 | 97.5 | Flextronics Industrial7FLV-IA-7.0S1UA | 2017-05
Flextronics Industrial | FLV-IA-7.6S1UA | Y | N | N | 7.6 kW, transformerless Utility Interactive Inverter | 7.6 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 7 |  |  | 200 | 380 | 500 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.1 | 96.2 | 96.9 | 97.3 | 97.1 | 96.6 | 97 | 95.6 | 97.2 | 97.5 | 97.8 | 97.3 | 97.9 | 97.4 | 95.4 | 96.8 | 97.6 | 97.8 | 97.9 | 97.7 | 97.7 | Flextronics Industrial7.6FLV-IA-7.6S1UA | 2017-05
Flextronics Industrial | FLV-IA-8.0S1UA | Y | N | N | 8.0 kW, transformerless Utility Interactive Inverter | 8 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 6 |  |  | 250 | 380 | 500 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.1 | 96.2 | 96.9 | 97.4 | 97.2 | 96.6 | 97 | 95.7 | 97.2 | 97.4 | 97.5 | 97.7 | 97 | 97.5 | 95.4 | 96.7 | 97.6 | 97.8 | 97.9 | 97.7 | 97.7 | Flextronics Industrial8FLV-IA-8.0S1UA | 2017-05
Flextronics Industrial | FLV-IA-9.0S1UA | Y | N | N | 9.0 kW, transformerless Utility Interactive Inverter | 9 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 7 |  |  | 250 | 380 | 500 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 95.1 | 96.8 | 97 | 97.5 | 97.4 | 97 | 97.2 | 95.7 | 97.3 | 97.4 | 97.6 | 97.8 | 97.1 | 97.5 | 95.6 | 96.7 | 97.7 | 97.8 | 97.8 | 97.7 | 97.7 | Flextronics Industrial9FLV-IA-9.0S1UA | 2017-05
Flextronics Industrial | FLV-IA-10.0S1UA | Y | N | N | 10.0 kW, transformerless Utility Interactive Inverter | 10 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 7 |  |  | 250 | 380 | 500 | 1 | 2 | 3 | 5 | 7.5 | 10 | 95.2 | 96.8 | 97.1 | 97.5 | 97.6 | 97.1 | 97.4 | 95.3 | 96.3 | 97.6 | 97.7 | 97.7 | 97.2 | 97.5 | 95.6 | 96.8 | 97.7 | 97.8 | 97.8 | 97.7 | 97.6 | Flextronics Industrial10FLV-IA-10.0S1UA | 2017-05
Friem | RECon 30L-100-US | Y | N | N | 100 kW 3-phase Utility Interactive Inverter | 100 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 59.63 |  |  | 325 | 487 | 650 | 10 | 20 | 30 | 50 | 75 | 100 | 96.5 | 98.1 | 98.4 | 98 | 97.3 | 96.9 | 97.5 | 95.3 | 97.8 | 98.3 | 98.2 | 98.1 | 97.9 | 98 | 96 | 98.2 | 98.8 | 98.7 | 98.3 | 97.7 | 98.3 | Friem100RECon 30L-100-US
Friem | RECon 30H-150-US [300V] | Y | N | N | 150 kW 3-phase output 300Vac/LV/MV Utility Interactive Inverter | 150 | 300 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 62.53 |  |  | 480 | 615 | 750 | 15 | 30 | 45 | 75 | 112.5 | 150 | 93.6 | 96.3 | 97 | 97.5 | 97.4 | 97.7 | 97.2 | 95.6 | 97.6 | 98.4 | 98.3 | 98 | 98 | 98 | 94.1 | 96.7 | 97.7 | 97.9 | 97.8 | 97.6 | 97.6 | Friem150RECon 30H-150-US [300V]
Fronius International GmbH | Fronius Primo 3.8-1 208-240 [208V] | N | Y | Y | 3800 W, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 3.8 | 208 | 96 | [7/7/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 0.41 |  |  | 100 | 650 | 800 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 87.3 | 92.4 | 93.9 | 95.2 | 95.6 | 95.7 | 94.8 | 90.7 | 95.2 | 96.4 | 97.2 | 97.5 | 97.6 | 96.9 | 85.7 | 93.4 | 95.2 | 96.6 | 97.1 | 97.3 | 96.1 | Fronius International GmbH3.8Fronius Primo 3.8-1 208-240 [208V] | 2017-08-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 3.8-1 208-240 [240V] | N | Y | Y | 3800 W, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 3.8 | 240 | 95.5 | [7/7/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 0.55 |  |  | 100 | 650 | 800 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 85.5 | 91.5 | 93.3 | 94.8 | 95.4 | 95.6 | 94.4 | 87.2 | 93.4 | 95 | 96.4 | 96.9 | 97.2 | 96 | 87 | 93.7 | 95.5 | 96.9 | 97.4 | 97.6 | 96.5 | Fronius International GmbH3.8Fronius Primo 3.8-1 208-240 [240V] | 2017-08-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 5.0-1 208-240 [208V] | N | Y | Y | 5000 W, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 5 | 208 | 96.5 | [7/7/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 0.41 |  |  | 100 | 650 | 800 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 89.4 | 93.8 | 94.8 | 95.8 | 96 | 96 | 95.4 | 92.5 | 96 | 96.8 | 97.5 | 97.6 | 97.6 | 97.2 | 89.3 | 94.6 | 96 | 97 | 97.3 | 97.4 | 96.6 | Fronius International GmbH5Fronius Primo 5.0-1 208-240 [208V] | 2017-08-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 5.0-1 208-240 [240V] | N | Y | Y | 5000 W, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 5 | 240 | 96.5 | [7/7/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 0.55 |  |  | 100 | 660 | 800 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 89 | 93.2 | 94.6 | 95.6 | 95.9 | 96 | 95.3 | 91.6 | 95.4 | 96.4 | 97.1 | 97.4 | 97.4 | 96.9 | 92.3 | 96 | 97 | 97.7 | 97.9 | 97.9 | 97.4 | Fronius International GmbH5Fronius Primo 5.0-1 208-240 [240V] | 2017-08-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 6.0-1 208-240 [208V] | N | Y | Y | 6000 W, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 6 | 208 | 96.5 | [7/7/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 0.41 |  |  | 100 | 660 | 800 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 90.7 | 94.4 | 95.2 | 95.9 | 96 | 95.9 | 95.6 | 93.5 | 96.5 | 97.1 | 97.6 | 97.6 | 97.6 | 97.3 | 91 | 95.4 | 96.4 | 97.2 | 97.3 | 97.4 | 96.8 | Fronius International GmbH6Fronius Primo 6.0-1 208-240 [208V] | 2017-08-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 6.0-1 208-240 [240V] | N | Y | Y | 6000 W, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 6 | 240 | 96.5 | [7/7/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 0.55 |  |  | 100 | 660 | 800 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 89.8 | 93.6 | 94.9 | 95.8 | 96 | 96 | 95.4 | 91.4 | 95.3 | 96.3 | 97 | 97.3 | 97.3 | 96.8 | 91.7 | 95.7 | 96.7 | 97.5 | 97.7 | 97.7 | 97.2 | Fronius International GmbH6Fronius Primo 6.0-1 208-240 [240V] | 2017-08-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 7.6-1 208-240 [208V] | N | Y | Y | 7600 W, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 7.6 | 208 | 97 | [7/7/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 0.41 |  |  | 100 | 660 | 800 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.7 | 95.1 | 95.8 | 96.1 | 96.1 | 95.8 | 95.8 | 96 | 97.4 | 97.7 | 97.8 | 97.7 | 97.6 | 97.7 | 94.1 | 96.7 | 97.3 | 97.6 | 97.5 | 97.4 | 97.3 | Fronius International GmbH7.6Fronius Primo 7.6-1 208-240 [208V] | 2017-08-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 7.6-1 208-240 [240V] | N | Y | Y | 7600 W, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 7.6 | 240 | 97 | [7/7/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 0.55 |  |  | 100 | 660 | 800 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 91.6 | 94.8 | 95.5 | 96 | 96.1 | 95.9 | 95.7 | 94 | 96.4 | 97 | 97.4 | 97.5 | 97.4 | 97.2 | 94.6 | 97 | 97.6 | 97.9 | 97.9 | 97.8 | 97.7 | Fronius International GmbH7.6Fronius Primo 7.6-1 208-240 [240V] | 2017-08-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 8.2-1 208-240 [208V] | N | Y | Y | 7900 W, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 7.9 | 208 | 97 | [7/7/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 0.41 |  |  | 100 | 660 | 800 | 0.79 | 1.58 | 2.37 | 3.95 | 5.93 | 7.9 | 93 | 95.3 | 95.9 | 96.2 | 96.2 | 95.9 | 96 | 95.8 | 97.3 | 97.7 | 97.8 | 97.8 | 97.5 | 97.7 | 94 | 96.7 | 97.3 | 97.6 | 97.6 | 97.4 | 97.3 | Fronius International GmbH7.9Fronius Primo 8.2-1 208-240 [208V] | 2017-08-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 8.2-1 208-240 [240V] | N | Y | Y | 8200 W, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 8.2 | 240 | 97 | [7/7/2017] | [ReCerbo V0.3.14.7, Roach V0.26.9.0, Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 0.55 |  |  | 100 | 660 | 800 | 0.82 | 1.64 | 2.46 | 4.1 | 6.15 | 8.2 | 92.1 | 94.9 | 95.7 | 96.2 | 96.2 | 96.1 | 95.9 | 94.2 | 96.6 | 97.1 | 97.4 | 97.4 | 97.4 | 97.2 | 94.7 | 97.1 | 97.6 | 97.9 | 97.9 | 97.8 | 97.7 | Fronius International GmbH8.2Fronius Primo 8.2-1 208-240 [240V] | 2017-08-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 10.0-1 [208V] | N | Y | Y | 9995 W, 208 Vac, Grid Support Utility Interactive Inverter with arc detector and meter | 9.995 | 208 | 96.5 | [9/22/2017] | [ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.7.0] | 2018-10-15 | Y | N |  | 0.24 |  |  | 100 | 660 | 800 | 1 | 2 | 3 | 5 | 7.5 | 10 | 92 | 94.7 | 95.1 | 95.6 | 95.6 | 95.5 | 95.3 | 94.5 | 97.4 | 96.8 | 97.3 | 97.3 | 97.4 | 97.1 | 93.3 | 97.1 | 96.5 | 97 | 97.3 | 97.3 | 97 | Fronius International GmbH9.995Fronius Primo 10.0-1 (208) [SI1] | 2017-11-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 10.0-1 [240V] | N | Y | Y | 9995 W, 240 Vac, Grid Support Utility Interactive Inverter with arc detector and meter | 9.995 | 240 | 96.5 | [9/22/2017] | [ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.7.0] | 2018-10-15 | Y | N |  | 0.32 |  |  | 100 | 655 | 800 | 1 | 2 | 3 | 5 | 7.5 | 10 | 91.4 | 94.3 | 94.8 | 95.4 | 95.6 | 95.6 | 95.2 | 93.5 | 95.8 | 96.3 | 96.9 | 97.1 | 97 | 96.7 | 95.6 | 97 | 97.2 | 97.6 | 97.7 | 97.5 | 97.5 | Fronius International GmbH9.995Fronius Primo 10.0-1 (240) [SI1] | 2017-11-01 | 2018-10-15
Fronius International GmbH | Fronius Symo 10.0-3 208-240 [208V] | N | Y | Y | Grid Support Utility Interactive Inverter with arc detector | 9.995 | 208 | 96.5 | [10/16/2017] | [ReCerbo V0.3.14.8 Roach V0.26.18.0 Guard V0.10.7.0] | 2018-10-15 | Y | N |  | 0.81 |  |  | 100 | 370 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94 | 95.6 | 96.1 | 96.2 | 96.2 | 96 | 96.1 | 95.4 | 96.8 | 97 | 97.1 | 97.1 | 96.9 | 97 | 94.8 | 96.4 | 96.7 | 96.9 | 96.9 | 96.7 | 96.7 | Fronius International GmbH9.995Fronius Symo 10.0-3 208-240 (208) [SI1] | 2017-12-01 | 2018-10-15
Fronius International GmbH | Fronius Symo 10.0-3 208-240 [240V] | N | Y | Y | Grid Support Utility Interactive Inverter with arc detector | 9.995 | 240 | 96.5 | [10/16/2017] | [ReCerbo V0.3.14.8 Roach V0.26.18.0 Guard V0.10.7.0] | 2018-10-15 | Y | N |  | 0.8 |  |  | 100 | 370 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94 | 95.6 | 96.1 | 96.2 | 96.2 | 96 | 96.1 | 95.4 | 96.8 | 97 | 97.1 | 97.1 | 96.9 | 97 | 94.8 | 96.4 | 96.7 | 96.9 | 96.9 | 96.7 | 96.7 | Fronius International GmbH9.995Fronius Symo 10.0-3 208-240 (240) [SI1] | 2017-12-01 | 2018-10-15
Fronius International GmbH | Fronius Symo 10.0-3 480 [480V] | N | Y | Y | 9.995 kW, 480 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 9.995 | 480 | 96.5 | [7/27/2017] | [ReCerbo V0.3.14.7 , Roach V0.26.9.0 , Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 0.86 |  |  | 100 | 670 | 800 | 1 | 2 | 3 | 5 | 7.5 | 10 | 89.6 | 93.7 | 94.8 | 95.3 | 96 | 96.2 | 95.3 | 91.8 | 95.2 | 96.1 | 96.7 | 97.2 | 97.3 | 96.6 | 92.9 | 96.1 | 96.9 | 97.3 | 97.7 | 97.8 | 97.2 | Fronius International GmbH9.995Fronius Symo 10.0-3 480 [480V] | 2017-08-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 11.4-1 [208V] | N | Y | Y | 11,400 W, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 11.4 | 208 | 96.5 | [9/22/2017] | [ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.7.0] | 2018-10-15 | Y | N |  | 0.24 |  |  | 240 | 660 | 800 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 93 | 94.9 | 95.4 | 95.8 | 95.8 | 95.7 | 95.6 | 95.4 | 97 | 97.3 | 97.4 | 97.4 | 97.4 | 97.3 | 94.5 | 96.4 | 96.9 | 97.2 | 97.2 | 97.3 | 97.1 | Fronius International GmbH11.4Fronius Primo 11.4-1 (208) [SI1] | 2017-11-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 11.4-1 [240V] | N | Y | Y | 11,400 W, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 11.4 | 240 | 96.5 | [9/22/2017] | [ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.7.0] | 2018-10-15 | Y | N |  | 0.32 |  |  | 240 | 660 | 800 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 92.1 | 94.8 | 95.3 | 95.8 | 95.9 | 95.8 | 95.6 | 93.7 | 96.1 | 96.6 | 97 | 97.1 | 97.1 | 96.9 | 94.8 | 96.9 | 97.4 | 97.6 | 97.6 | 97.6 | 97.4 | Fronius International GmbH11.4Fronius Primo 11.4-1 (240) [SI1] | 2017-11-01 | 2018-10-15
Fronius International GmbH | Fronius Symo 12.0-3 208-240 [208V] | N | Y | Y | Grid Support Utility Interactive Inverter with arc detector | 12 | 208 | 96.5 | [10/16/2017] | [ReCerbo V0.3.14.8 Roach V0.26.18.0 Guard V0.10.7.0] | 2018-10-15 | Y | N |  | 0.61 |  |  | 300 | 350 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 95.4 | 96.2 | 96.3 | 96.2 | 95.9 | 95.4 | 95.9 | 96.3 | 96.9 | 96.9 | 96.8 | 96.5 | 96.2 | 96.6 | 94.7 | 96.1 | 96.4 | 96.4 | 96.3 | 96 | 96.2 | Fronius International GmbH12Fronius Symo 12.0-3 208-240 (208) [SI1] | 2017-12-01 | 2018-10-15
Fronius International GmbH | Fronius Symo 12.0-3 208-240 [240V] | N | Y | Y | Grid Support Utility Interactive Inverter with arc detector | 12 | 240 | 96.5 | [10/16/2017] | [ReCerbo V0.3.14.8 Roach V0.26.18.0 Guard V0.10.7.0] | 2018-10-15 | Y | N |  | 0.81 |  |  | 300 | 370 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 94.4 | 95.9 | 96.2 | 96.3 | 96.1 | 95.8 | 96.1 | 96 | 96.9 | 97.1 | 97.1 | 97 | 96.8 | 97 | 95.2 | 96.6 | 96.8 | 96.9 | 96.8 | 96.6 | 96.7 | Fronius International GmbH12Fronius Symo 12.0-3 208-240 (240) [SI1] | 2017-12-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 12.5-1 [208V] | N | Y | Y | 12,500 W, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 12.5 | 208 | 96.5 | [9/22/2017] | [ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.7.0] | 2018-10-15 | Y | N |  | 0.24 |  |  | 260 | 665 | 800 | 1.25 | 2.5 | 3.75 | 6.25 | 9.38 | 12.5 | 92.5 | 95.1 | 95.5 | 95.9 | 95.9 | 95.6 | 95.6 | 95.3 | 96.9 | 97.3 | 97.5 | 97.3 | 97.3 | 97.2 | 94.5 | 96.6 | 97 | 97.2 | 97.1 | 97.2 | 97 | Fronius International GmbH12.5Fronius Primo 12.5-1 (208) [SI1] | 2017-11-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 12.5-1 [240V] | N | Y | Y | 12,500 W, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 12.5 | 240 | 96.5 | [9/22/2017] | [ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.7.0] | 2018-10-15 | Y | N |  | 0.32 |  |  | 260 | 660 | 800 | 1.25 | 2.5 | 3.75 | 6.25 | 9.38 | 12.5 | 92.1 | 95 | 95.4 | 95.9 | 95.9 | 95.8 | 95.6 | 93.7 | 96.2 | 96.6 | 97 | 97.1 | 97.1 | 96.8 | 95.4 | 97.2 | 97.3 | 97.5 | 97.6 | 97.7 | 97.5 | Fronius International GmbH12.5Fronius Primo 12.5-1 (240) [SI1] | 2017-11-01 | 2018-10-15
Fronius International GmbH | Fronius Symo 12.5-3 480 [480V] | N | Y | Y | 12.495 kW, 480 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 12.5 | 480 | 97 | [7/27/2017] | [ReCerbo V0.3.14.7 , Roach V0.26.9.0 , Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 0.94 |  |  | 350 | 685 | 800 | 1.25 | 2.5 | 3.75 | 6.25 | 9.37 | 12.5 | 92.5 | 94.9 | 95.6 | 96 | 96.4 | 96.5 | 96 | 94.4 | 96.5 | 97 | 97.3 | 97.5 | 97.5 | 97.2 | 95.6 | 97.3 | 97.7 | 97.9 | 98 | 98 | 97.8 | Fronius International GmbH12.5Fronius Symo 12.5-3 480 [480V] | 2017-08-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 15.0-1 [208V] | N | Y | Y | 13,750 W, 208 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 13.75 | 208 | 97 | [9/22/2017] | [ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.7.0] | 2018-10-15 | Y | N |  | 0.24 |  |  | 320 | 680 | 800 | 1.38 | 2.75 | 4.13 | 6.88 | 10.31 | 13.75 | 93.3 | 95.7 | 96 | 96.3 | 96.2 | 96 | 96 | 95.9 | 97.1 | 97.4 | 97.4 | 97.4 | 97.2 | 97.3 | 95.1 | 96.8 | 97.1 | 97.2 | 97.2 | 97.1 | 97.1 | Fronius International GmbH13.75Fronius Primo 15.0-1 (208) [SI1] | 2017-11-01 | 2018-10-15
Fronius International GmbH | Fronius Primo 15.0-1 [240V] | N | Y | Y | 15,000 W, 240 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 15 | 240 | 97 | [9/22/2017] | [ReCerbo V0.3.14.8 Roach V0.26.16.0 Guard V0.10.7.0] | 2018-10-15 | Y | N |  | 0.32 |  |  | 320 | 680 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.5 | 95.5 | 96 | 96.3 | 96.3 | 96.1 | 96.1 | 94.5 | 96.5 | 96.9 | 97.2 | 97.2 | 97 | 97 | 95.7 | 97.2 | 97.5 | 97.6 | 97.6 | 97.4 | 97.5 | Fronius International GmbH15Fronius Primo 15.0-1 (240) [SI1] | 2017-11-01 | 2018-10-15
Fronius International GmbH | Fronius Symo 15.0-3 [208V] | N | Y | Y | 15,000W, 208 Vac Grid Support Utility Interactive Inverter with arc detector | 15 | 208 | 96.5 | [9/27/2017] | [ReCerbo V0.3.14.8 Roach V0.10.7.0 Guard V0.26.14.0] | 2018-10-15 | Y | N |  | 0.43 |  |  | 325 | 445 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 96.1 | 97 | 97.1 | 97.1 | 96.9 | 96.7 | 96.9 | 95.3 | 96.4 | 96.6 | 96.7 | 96.5 | 96.2 | 96.5 | 92.7 | 94.9 | 95.4 | 95.6 | 95.5 | 95.3 | 95.4 | Fronius International GmbH15Fronius Symo 15.0-3 (208V) [SI1] | 2017-11-01 | 2018-10-15
Fronius International GmbH | Fronius Symo 15.0-3 480 [480V] | N | Y | Y | 14.995 kW, 480 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 15 | 480 | 97 | [7/27/2017] | [ReCerbo V0.3.14.7 , Roach V0.26.9.0 , Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 1.03 |  |  | 350 | 685 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 92 | 94.9 | 95.6 | 96.2 | 96.5 | 96.4 | 96.1 | 93.5 | 96 | 96.7 | 97.2 | 97.4 | 97.4 | 97.1 | 94.6 | 96.8 | 97.4 | 97.8 | 97.9 | 97.9 | 97.6 | Fronius International GmbH15Fronius Symo 15.0-3 480 [480V] | 2017-08-01 | 2018-10-15
Fronius International GmbH | Fronius Symo 17.5-3 480 [480V] | N | Y | Y | Grid Support Utility Interactive Inverter with arc detector and meter | 17.5 | 480 | 97.5 | [7/27/2017] | [ReCerbo V0.3.14.7 , Roach V0.26.9.0 , Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 1.03 |  |  | 400 | 700 | 800 | 1.75 | 3.5 | 5.25 | 8.75 | 13.12 | 17.5 | 92.7 | 95.3 | 95.8 | 96.5 | 96.6 | 96.7 | 96.3 | 95.7 | 97.4 | 97.8 | 98.1 | 98.1 | 98.2 | 98 | 94.8 | 96.9 | 97.4 | 97.7 | 97.8 | 97.8 | 97.6 | Fronius International GmbH17.5Fronius Symo 17.5-3 480 [480V] | 2017-08-01 | 2018-10-15
Fronius International GmbH | Fronius Symo 20.0-3 480 [480V] | N | Y | Y | 19.995 kW, 480 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 20 | 480 | 97.5 | [7/27/2017] | [ReCerbo V0.3.14.7 , Roach V0.26.9.0 , Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 1.04 |  |  | 450 | 712 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.7 | 95.6 | 96.3 | 96.7 | 96.8 | 96.8 | 96.5 | 96 | 97.2 | 97.7 | 98 | 98 | 98 | 97.9 | 95.7 | 97 | 97.5 | 97.7 | 97.8 | 97.8 | 97.6 | Fronius International GmbH20Fronius Symo 20.0-3 480 [480V] |  | 2018-10-15
Fronius International GmbH | Fronius Symo 22.7-3 480 [480V] | N | Y | Y | 22.727 kW, 480 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 22.73 | 480 | 97.5 | [7/27/2017] | [ReCerbo V0.3.14.7 , Roach V0.26.9.0 , Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 1.03 |  |  | 500 | 720 | 800 | 2.27 | 4.55 | 6.82 | 11.36 | 17.05 | 22.73 | 94.3 | 96.2 | 96.7 | 97 | 97 | 96.9 | 96.8 | 96.4 | 97.6 | 97.8 | 98 | 98 | 98 | 97.9 | 95.9 | 97.3 | 97.7 | 97.8 | 97.9 | 97.8 | 97.7 | Fronius International GmbH22.73Fronius Symo 22.7-3 480 [480V] | 2017-08-01 | 2018-10-15
Fronius International GmbH | Fronius Symo 24.0-3 480 [480V] | N | Y | Y | 23.995 kW, 480 Vac Grid Support Utility Interactive Inverter with arc detector and meter | 24 | 480 | 97.5 | [7/27/2017] | [ReCerbo V0.3.14.7 , Roach V0.26.9.0 , Guard V0.10.2.10] | 2018-10-15 | Y | N |  | 1.03 |  |  | 500 | 725 | 800 | 2.4 | 4.8 | 7.2 | 12 | 18 | 24 | 94.3 | 96.1 | 96.6 | 97 | 97 | 97 | 96.8 | 96.2 | 97.5 | 97.8 | 98 | 98 | 97.9 | 97.9 | 95.8 | 97.2 | 97.6 | 97.8 | 97.8 | 97.7 | 97.7 | Fronius International GmbH24Fronius Symo 24.0-3 480 [480V] | 2017-08-01 | 2018-10-15
Fronius USA | Galvo 1.5-1 208-240 [208V] | Y | N | N | 1500 W, 208 Vac Utility Interactive Inverter with arc detector | 1.5 | 208 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.67 |  |  | 100 | 260 | 335 | 0.15 | 0.3 | 0.45 | 0.75 | 1.125 | 1.5 | 85.7 | 91 | 92.6 | 93.8 | 93.9 | 93.8 | 93.3 | 87.4 | 92.2 | 94 | 95 | 95.5 | 95.5 | 94.7 | 87.2 | 92 | 93.5 | 94.6 | 95 | 95.2 | 94.3 | Fronius USA1.5Galvo 1.5-1 208-240 [208V]
Fronius USA | Galvo 1.5-1 208-240 [240V] | Y | N | N | 1500 W, 240 Vac Utility Interactive Inverter with arc detector | 1.5 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.89 |  |  | 100 | 260 | 335 | 0.15 | 0.3 | 0.45 | 0.75 | 1.125 | 1.5 | 87.1 | 91.2 | 93 | 94 | 94.2 | 94.1 | 93.6 | 88 | 92.3 | 94.1 | 95.2 | 95.7 | 95.8 | 94.9 | 87.8 | 92 | 93.6 | 94.9 | 95.3 | 95.5 | 94.5 | Fronius USA1.5Galvo 1.5-1 208-240 [240V]
Fronius USA | Galvo 2.0-1 208-240 [208V] | Y | N | N | 1900 W, 208 Vac Utility Interactive Inverter with arc detector | 1.9 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.67 |  |  | 100 | 260 | 335 | 0.19 | 0.38 | 0.57 | 0.95 | 1.425 | 1.9 | 87.5 | 92.1 | 93.2 | 94 | 93.9 | 93.5 | 93.4 | 89.1 | 93.4 | 94.4 | 95.3 | 95.5 | 95.4 | 94.9 | 88.7 | 93 | 94.2 | 94.5 | 95.1 | 95.2 | 94.5 | Fronius USA1.9Galvo 2.0-1 208-240 [208V]
Fronius USA | Galvo 2.0-1 208-240 [240V] | Y | N | N | 2000 W 240 Vac Utility Interactive Inverter with arc detector | 2 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 100 | 260 | 335 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 88.5 | 92.6 | 93.5 | 94.2 | 94.1 | 93.7 | 93.8 | 89.6 | 93.9 | 94.8 | 95.6 | 95.8 | 95.7 | 95.3 | 89.7 | 93.4 | 94.6 | 94.9 | 95.4 | 95.5 | 94.9 | Fronius USA2Galvo 2.0-1 208-240 [240V]
Fronius USA | IG 2000 NEG | Y | N | N | 2000 W Grid-tied unit with Integrated Disconnects and Performance Meter | 2 |  | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.91 |  |  | 100 | 280 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 86.8 | 90.8 | 92.4 | 93.7 | 93.6 | 94.3 | 93.1 | 87.4 | 91 | 93 | 94.8 | 95.1 | 95.4 | 94.3 | 84.6 | 89.9 | 90.6 | 92.7 | 93.7 | 93.9 | 92.6 | Fronius USA2IG 2000 NEG
Fronius USA | IG 2000 POS | Y | N | N | 2000 W Grid-tied unit with Integrated Disconnects and Performance Meter | 2 |  | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.91 |  |  | 100 | 280 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 86.8 | 90.8 | 92.4 | 93.7 | 93.6 | 94.3 | 93.1 | 87.4 | 91 | 93 | 94.8 | 95.1 | 95.4 | 94.3 | 84.6 | 89.9 | 90.6 | 92.7 | 93.7 | 93.9 | 92.6 | Fronius USA2IG 2000 POS
Fronius USA | IG 2500-LV NEG | Y | N | N | 2350W Grid-tied unit with Integrated Disconnects and Performance Meter | 2.35 |  | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.73 |  |  | 100 | 280 | 400 | 0.24 | 0.47 | 0.71 | 1.18 | 1.76 | 2.35 | 87.8 | 91.4 | 92.6 | 93.3 | 93.1 | 92.2 | 92.7 | 88.4 | 91.5 | 92.8 | 94.2 | 94.3 | 93.6 | 93.7 | 84.8 | 88.4 | 90.5 | 92.6 | 93.3 | 93.1 | 92.2 | Fronius USA2.35IG 2500-LV NEG
Fronius USA | IG 2500-LV POS | Y | N | N | 2350W Grid-tied unit with Integrated Disconnects and Performance Meter | 2.35 |  | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.73 |  |  | 100 | 280 | 400 | 0.24 | 0.47 | 0.71 | 1.18 | 1.76 | 2.35 | 87.8 | 91.4 | 92.6 | 93.3 | 93.1 | 92.2 | 92.7 | 88.4 | 91.5 | 92.8 | 94.2 | 94.3 | 93.6 | 93.7 | 84.8 | 88.4 | 90.5 | 92.6 | 93.3 | 93.1 | 92.2 | Fronius USA2.35IG 2500-LV POS
Fronius USA | Galvo 2.5-1 208-240 [208V] | Y | N | N | 2500 W, 208 Vac Utility Interactive Inverter with arc detector | 2.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.67 |  |  | 100 | 330 | 440 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 90.2 | 93.6 | 94.3 | 94.7 | 94.6 | 94.1 | 94.3 | 91.1 | 94.6 | 95.3 | 95.6 | 95.6 | 95.4 | 95.3 | 91.1 | 94.1 | 94.9 | 95.1 | 95.2 | 95.1 | 94.9 | Fronius USA2.5Galvo 2.5-1 208-240 [208V]
Fronius USA | Galvo 2.5-1 208-240 [240V] | Y | N | N | 2500 W, 240 Vac Utility Interactive Inverter with arc detector | 2.5 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.67 |  |  | 100 | 330 | 440 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 90.6 | 93.9 | 94.6 | 95 | 94.9 | 94.5 | 94.7 | 91.5 | 94.8 | 95.4 | 96 | 96 | 95.8 | 95.7 | 91.5 | 94.3 | 95.3 | 95.5 | 95.7 | 95.6 | 95.3 | Fronius USA2.5Galvo 2.5-1 208-240 [240V]
Fronius USA | IG 3000 NEG | Y | N | N | 2700 W Grid-tied unit with Integrated Disconnects and Performance Meter | 2.7 |  | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.91 |  |  | 100 | 280 | 400 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 88.2 | 92 | 94 | 94.3 | 94.1 | 93.6 | 93.7 | 89.2 | 92.6 | 94.4 | 94.9 | 95.1 | 94.5 | 94.6 | 88.3 | 90 | 92.3 | 93.4 | 93.8 | 93.6 | 93.1 | Fronius USA2.7IG 3000 NEG
Fronius USA | IG 3000 POS | Y | N | N | 2700 W Grid-tied unit with Integrated Disconnects and Performance Meter | 2.7 |  | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.91 |  |  | 100 | 280 | 400 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 88.2 | 92 | 94 | 94.3 | 94.1 | 93.6 | 93.7 | 89.2 | 92.6 | 94.4 | 94.9 | 95.1 | 94.5 | 94.6 | 88.3 | 90 | 92.3 | 93.4 | 93.8 | 93.6 | 93.1 | Fronius USA2.7IG 3000 POS
Fronius USA | Galvo 3.1-1 208-240 [208V] | Y | N | N | 2930 W, 208 Vac Utility Interactive Inverter with arc detector | 2.93 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.7 |  |  | 100 | 330 | 440 | 0.29 | 0.59 | 0.88 | 1.47 | 2.2 | 2.93 | 90.9 | 94.1 | 94.4 | 94.7 | 94.3 | 93.6 | 94.2 | 92.2 | 95 | 95.4 | 95.6 | 95.5 | 95.1 | 95.3 | 91.9 | 94.4 | 95.1 | 95.1 | 95.2 | 94.9 | 95 | Fronius USA2.93Galvo 3.1-1 208-240 [208V] |  | 2018-03-15
Fronius USA | IG Plus 3.0-1 UNI [208V] | Y | N | N | 3000 W, 208 Vac Utility Interactive Inverter | 3 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.62 |  |  | 100 | 366 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.2 | 94.4 | 95.1 | 95.3 | 94.9 | 94.1 | 94.8 | 92.5 | 95.2 | 95.3 | 95.9 | 95.8 | 95.5 | 95.6 | 92.2 | 94.5 | 94.5 | 95.2 | 95.3 | 95.1 | 95 | Fronius USA3IG Plus 3.0-1 UNI [208V]
Fronius USA | IG Plus 3.0-1 UNI [240V] | Y | N | N | 3000 W, 240 Vac Utility Interactive Inverter | 3 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.83 |  |  | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.3 | 95.3 | 95.7 | 95.6 | 95.1 | 95.3 | 91.3 | 95.1 | 95.4 | 96.1 | 96.2 | 96 | 95.8 | 91.3 | 94.7 | 95 | 95.5 | 95.7 | 95.7 | 95.3 | Fronius USA3IG Plus 3.0-1 UNI [240V]
Fronius USA | IG Plus 3.0-1 UNI [277V] | Y | N | N | 3000 W, 277 Vac Utility Interactive Inverter | 3 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 |  |  | 100 | 330 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 90.2 | 94.4 | 95.2 | 95.9 | 96 | 95.7 | 95.5 | 91.1 | 94.9 | 95.5 | 96.1 | 96.3 | 96.2 | 95.9 | 91.5 | 94.5 | 95.4 | 95.7 | 96 | 96.1 | 95.6 | Fronius USA3IG Plus 3.0-1 UNI [277V]
Fronius USA | IG Plus A 3.0 [208V] | Y | N | N | 3000 W, 208 Vac Utility Interactive Inverter, Same as Series V with arc detector | 3 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.53 | 3 | 0.53 | 100 | 366 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.2 | 94.5 | 95.1 | 95.4 | 95.2 | 94.6 | 95 | 92.4 | 95 | 95.2 | 95.9 | 95.9 | 95.6 | 95.6 | 91.6 | 94 | 94.2 | 95.3 | 95.5 | 95.3 | 95.1 | Fronius USA3IG Plus A 3.0 [208V]
Fronius USA | IG Plus A 3.0 [240V] | Y | N | N | 3000 W, 240 Vac Utility Interactive Inverter, Same as Series V with arc detector | 3 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.7 | 3 | 0.7 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.9 | 94.5 | 95.3 | 95.9 | 95.8 | 95.5 | 95.5 | 92.2 | 95.1 | 95.4 | 96.1 | 96.3 | 96.2 | 95.9 | 91.9 | 94.6 | 94.6 | 95.6 | 95.9 | 95.9 | 95.5 | Fronius USA3IG Plus A 3.0 [240V]
Fronius USA | IG Plus A 3.0 [277V] | Y | N | N | 3000 W, 277 Vac Utility Interactive Inverter, Same as Series V with arc detector | 3 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.94 | 3 | 0.94 | 100 | 330 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 90.8 | 94.5 | 95.4 | 96.2 | 96.3 | 96 | 95.8 | 91.5 | 95 | 95.4 | 96.3 | 96.5 | 96.4 | 96 | 91.9 | 94.7 | 95.2 | 95.8 | 96.2 | 96.4 | 95.8 | Fronius USA3IG Plus A 3.0 [277V]
Fronius USA | IG Plus V 3.0 [208V] | Y | N | N | 3000 W, 208 Vac Utility Interactive Inverter | 3 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.53 | 3 | 0.53 | 100 | 366 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.22 | 94.53 | 95.11 | 95.38 | 95.19 | 94.61 | 95.04 | 92.39 | 94.99 | 95.23 | 95.89 | 95.9 | 95.55 | 95.62 | 91.58 | 94 | 94.23 | 95.3 | 95.49 | 95.34 | 95.06 | Fronius USA3IG Plus V 3.0 [208V]
Fronius USA | IG Plus V 3.0 [240V] | Y | N | N | 3000 W, 240 Vac Utility Interactive Inverter | 3 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.7 | 3 | 0.7 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.88 | 94.47 | 95.31 | 95.9 | 95.84 | 95.48 | 95.54 | 92.22 | 95.09 | 95.37 | 96.11 | 96.29 | 96.16 | 95.91 | 91.85 | 94.57 | 94.59 | 95.58 | 95.92 | 95.94 | 95.46 | Fronius USA3IG Plus V 3.0 [240V]
Fronius USA | IG Plus V 3.0 [277V] | Y | N | N | 3000 W, 277 Vac Utility Interactive Inverter | 3 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.94 | 3 | 0.94 | 100 | 330 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 90.8 | 94.51 | 95.44 | 96.17 | 96.26 | 96.04 | 95.82 | 91.52 | 95.02 | 95.35 | 96.31 | 96.49 | 96.42 | 96.04 | 91.92 | 94.72 | 95.21 | 95.82 | 96.23 | 96.39 | 95.78 | Fronius USA3IG Plus V 3.0 [277V]
Fronius USA | Galvo 3.1-1 208-240 [240V] | Y | N | N | 3100 W, 240 Vac Utility Interactive Inverter with arc detector | 3.1 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 100 | 330 | 440 | 0.31 | 0.62 | 0.93 | 1.55 | 2.33 | 3.1 | 91.6 | 94.4 | 94.8 | 95 | 94.7 | 94 | 94.6 | 92.8 | 95.4 | 95.8 | 96 | 95.9 | 95.5 | 95.7 | 92.4 | 94.9 | 95.5 | 95.6 | 95.6 | 95.4 | 95.4 | Fronius USA3.1Galvo 3.1-1 208-240 [240V]
Fronius USA | Fronius Primo 3.8-1 208-240 [208V] | Y | N | N | 3800 W, 208 Vac Utility Interactive Inverter with arc detector and meter | 3.8 | 208 | 96 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 0.41 |  |  | 100 | 650 | 800 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 87.3 | 92.4 | 93.9 | 95.2 | 95.6 | 95.7 | 94.8 | 90.7 | 95.2 | 96.4 | 97.2 | 97.5 | 97.6 | 96.9 | 85.7 | 93.4 | 95.2 | 96.6 | 97.1 | 97.3 | 96.1 | Fronius USA3.8Fronius Primo 3.8-1 208-240 [208V]
Fronius USA | Fronius Primo 3.8-1 208-240 [240V] | Y | N | N | 3800 W, 240 Vac Utility Interactive Inverter with arc detector and meter | 3.8 | 240 | 95.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 0.55 |  |  | 100 | 650 | 800 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 85.5 | 91.5 | 93.3 | 94.8 | 95.4 | 95.6 | 94.4 | 87.2 | 93.4 | 95 | 96.4 | 96.9 | 97.2 | 96 | 87 | 93.7 | 95.5 | 96.9 | 97.4 | 97.6 | 96.5 | Fronius USA3.8Fronius Primo 3.8-1 208-240 [240V]
Fronius USA | IG Plus 3.8-1 UNI [208V] | Y | N | N | 3800 W, 208 Vac Utility Interactive Inverter with arc detector and meter | 3.8 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.62 |  |  | 100 | 366 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93 | 94.9 | 95.3 | 95.1 | 94.4 | 93 | 94.6 | 93.6 | 95.1 | 95.7 | 95.9 | 95.6 | 94.9 | 95.6 | 92.7 | 94.4 | 95 | 95.4 | 95.2 | 94.7 | 95 | Fronius USA3.8IG Plus 3.8-1 UNI [208V]
Fronius USA | IG Plus 3.8-1 UNI [240V] | Y | N | N | 3800 W, 240 Vac Utility Interactive Inverter with arc detector and meter | 3.8 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.83 |  |  | 100 | 390 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.7 | 94.7 | 95.4 | 95.5 | 95.2 | 94.2 | 95.1 | 92.3 | 95 | 95.5 | 96.1 | 96 | 95.7 | 95.8 | 92 | 94.8 | 95 | 95.6 | 95.6 | 95.5 | 95.4 | Fronius USA3.8IG Plus 3.8-1 UNI [240V]
Fronius USA | IG Plus 3.8-1 UNI [277V] | Y | N | N | 3800 W, 277 Vac Utility Interactive Inverter with arc detector and meter | 3.8 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 |  |  | 100 | 330 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.7 | 94.8 | 95.5 | 95.9 | 95.8 | 95.1 | 95.5 | 91.8 | 95.2 | 95.6 | 96.2 | 96.2 | 95.8 | 95.9 | 91.8 | 95.1 | 95.3 | 95.9 | 96.1 | 96 | 95.7 | Fronius USA3.8IG Plus 3.8-1 UNI [277V]
Fronius USA | IG Plus A 3.8 [208V] | Y | N | N | 3800 W, 208 Vac Utility Interactive Inverter, Same as Series V with arc detector | 3.8 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.53 | 3.8 | 0.53 | 100 | 366 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93 | 94.9 | 95.4 | 95.3 | 94.8 | 93.8 | 94.9 | 93.5 | 95 | 95.6 | 96 | 95.7 | 95 | 95.6 | 93 | 93.9 | 94.8 | 95.5 | 95.4 | 94.9 | 95.2 | Fronius USA3.8IG Plus A 3.8 [208V]
Fronius USA | IG Plus A 3.8 [240V] | Y | N | N | 3800 W, 240 Vac Utility Interactive Inverter, Same as Series V with arc detector | 3.8 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.7 | 3.8 | 0.7 | 100 | 390 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.7 | 95 | 95.7 | 95.9 | 95.6 | 94.9 | 95.5 | 93.3 | 95.3 | 95.7 | 96.3 | 96.2 | 95.8 | 96 | 93.1 | 94.6 | 95.1 | 95.9 | 95.9 | 95.7 | 95.6 | Fronius USA3.8IG Plus A 3.8 [240V]
Fronius USA | IG Plus A 3.8 [277V] | Y | N | N | 3800 W, 277 Vac Utility Interactive Inverter, Same as Series V with arc detector | 3.8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.94 | 3.8 | 0.94 | 100 | 330 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.1 | 95 | 95.8 | 96.2 | 96.1 | 95.7 | 95.9 | 92.6 | 95.4 | 95.8 | 96.5 | 96.4 | 96.1 | 96.1 | 93 | 95.2 | 95.3 | 96.1 | 96.4 | 96.3 | 96 | Fronius USA3.8IG Plus A 3.8 [277V]
Fronius USA | IG Plus V 3.8 [208V] | Y | N | N | 3800 W, 208 Vac Utility Interactive Inverter with arc detector and meter | 3.8 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.53 | 3.8 | 0.53 | 100 | 366 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.98 | 94.93 | 95.38 | 95.33 | 94.78 | 93.76 | 94.85 | 93.52 | 95.04 | 95.62 | 95.96 | 95.65 | 95.02 | 95.56 | 92.96 | 93.88 | 94.78 | 95.48 | 95.41 | 94.93 | 95.15 | Fronius USA3.8IG Plus V 3.8 [208V]
Fronius USA | IG Plus V 3.8 [240V] | Y | N | N | 3800 W, 240 Vac Utility Interactive Inverter with arc detector and meter | 3.8 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.7 | 3.8 | 0.7 | 100 | 390 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.7 | 95.04 | 95.67 | 95.88 | 95.57 | 94.87 | 95.47 | 93.31 | 95.3 | 95.74 | 96.28 | 96.2 | 95.81 | 95.98 | 93.05 | 94.61 | 95.08 | 95.85 | 95.93 | 95.71 | 95.62 | Fronius USA3.8IG Plus V 3.8 [240V]
Fronius USA | IG Plus V 3.8 [277V] | Y | N | N | 3800 W, 277 Vac Utility Interactive Inverter with arc detector and meter | 3.8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.94 | 3.8 | 0.94 | 100 | 330 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.08 | 95.02 | 95.77 | 96.22 | 96.12 | 95.68 | 95.86 | 92.56 | 95.38 | 95.82 | 96.46 | 96.42 | 96.14 | 96.14 | 92.98 | 95.16 | 95.31 | 96.1 | 96.35 | 96.27 | 95.97 | Fronius USA3.8IG Plus V 3.8 [277V]
Fronius USA | IG 4000 NEG | Y | N | N | 4000 W, Grid-tied unit with Integrated Disconnects and Performance Meter | 4 |  | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 100 | 280 | 400 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 90 | 92.9 | 93.4 | 93.8 | 93.8 | 93.3 | 93.5 | 90.6 | 93.8 | 94.9 | 95.1 | 95.1 | 94.9 | 94.8 | 87.1 | 91.1 | 92.6 | 93.4 | 93.6 | 93.6 | 93.1 | Fronius USA4IG 4000 NEG
Fronius USA | IG 4000 POS | Y | N | N | 4000 W, Grid-tied unit with Integrated Disconnects and Performance Meter | 4 |  | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 100 | 280 | 400 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 90 | 92.9 | 93.4 | 93.8 | 93.8 | 93.3 | 93.5 | 90.6 | 93.8 | 94.9 | 95.1 | 95.1 | 94.9 | 94.8 | 87.1 | 91.1 | 92.6 | 93.4 | 93.6 | 93.6 | 93.1 | Fronius USA4IG 4000 POS
Fronius USA | IG 4500-LV NEG | Y | N | N | 4500 W, Grid-tied unit with Integrated Disconnects and Performance Meter | 4.5 |  | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.91 |  |  | 100 | 280 | 400 | 0.45 | 0.9 | 1.35 | 2.25 | 3.38 | 4.5 | 90.2 | 92.9 | 93.1 | 93.5 | 93.4 | 92.3 | 93.1 | 90.7 | 93.7 | 94.1 | 94.2 | 94.2 | 93.9 | 94 | 87.6 | 91.5 | 92.9 | 93.4 | 93.3 | 92.9 | 92.9 | Fronius USA4.5IG 4500-LV NEG
Fronius USA | IG 4500-LV POS | Y | N | N | 4500 W, Grid-tied unit with Integrated Disconnects and Performance Meter | 4.5 |  | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.91 |  |  | 100 | 280 | 400 | 0.45 | 0.9 | 1.35 | 2.25 | 3.38 | 4.5 | 90.2 | 92.9 | 93.1 | 93.5 | 93.4 | 92.3 | 93.1 | 90.7 | 93.7 | 94.1 | 94.2 | 94.2 | 93.9 | 94 | 87.6 | 91.5 | 92.9 | 93.4 | 93.3 | 92.9 | 92.9 | Fronius USA4.5IG 4500-LV POS
Fronius USA | Fronius Primo 5.0-1 208-240 [208V] | Y | N | N | 5000 W, 208 Vac Utility Interactive Inverter with arc detector and meter | 5 | 208 | 96.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 0.41 |  |  | 100 | 650 | 800 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 89.4 | 93.8 | 94.8 | 95.8 | 96 | 96 | 95.4 | 92.5 | 96 | 96.8 | 97.5 | 97.6 | 97.6 | 97.2 | 89.3 | 94.6 | 96 | 97 | 97.3 | 97.4 | 96.6 | Fronius USA5Fronius Primo 5.0-1 208-240 [208V]
Fronius USA | Fronius Primo 5.0-1 208-240 [240V] | Y | N | N | 5000 W, 240 Vac Utility Interactive Inverter with arc detector and meter | 5 | 240 | 96.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 0.55 |  |  | 100 | 660 | 800 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 89 | 93.2 | 94.6 | 95.6 | 95.9 | 96 | 95.3 | 91.6 | 95.4 | 96.4 | 97.1 | 97.4 | 97.4 | 96.9 | 92.3 | 96 | 97 | 97.7 | 97.9 | 97.9 | 97.4 | Fronius USA5Fronius Primo 5.0-1 208-240 [240V]
Fronius USA | IG Plus 5.0-1 UNI [208V] | Y | N | N | 5000 W, 208 Vac Utility Interactive Inverter with arc detector and meter | 5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.71 |  |  | 100 | 366 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.1 | 95 | 95.1 | 95.5 | 95.1 | 94.7 | 95.1 | 93.8 | 95.1 | 95.6 | 95.9 | 95.9 | 95.8 | 95.7 | 93.1 | 94.2 | 95 | 95.1 | 95.3 | 95.3 | 95.1 | Fronius USA5IG Plus 5.0-1 UNI [208V]
Fronius USA | IG Plus 5.0-1 UNI [240V] | Y | N | N | 5000 W, 240 Vac Utility Interactive Inverter with arc detector and meter | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.76 |  |  | 100 | 390 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.2 | 95.1 | 95.6 | 95.8 | 95.7 | 95.5 | 95.6 | 94.1 | 95.2 | 96 | 96.1 | 96.3 | 96.2 | 96 | 93.4 | 94.8 | 95.3 | 95.5 | 95.8 | 95.8 | 95.5 | Fronius USA5IG Plus 5.0-1 UNI [240V]
Fronius USA | IG Plus 5.0-1 UNI [277V] | Y | N | N | 5000 W, 277 Vac Utility Interactive Inverter with arc detector and meter | 5 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.02 |  |  | 100 | 330 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.2 | 95.3 | 95.8 | 96 | 96.1 | 96 | 95.9 | 93.6 | 95.3 | 96 | 96.1 | 96.4 | 96.4 | 96.1 | 93.5 | 95.2 | 95.6 | 95.7 | 96 | 96.1 | 95.8 | Fronius USA5IG Plus 5.0-1 UNI [277V]
Fronius USA | IG Plus A 5.0 [208V] | Y | N | N | 5000 W, 208 Vac Utility Interactive Inverter, Same as Series V with arc detector | 5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.6 | 5 | 0.6 | 100 | 366 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.3 | 95 | 95.2 | 95.4 | 95.3 | 94.9 | 95.2 | 94 | 95.3 | 95.7 | 95.8 | 95.9 | 95.8 | 95.7 | 93.2 | 94.2 | 95 | 95.3 | 95.5 | 95.5 | 95.2 | Fronius USA5IG Plus A 5.0 [208V]
Fronius USA | IG Plus A 5.0 [240V] | Y | N | N | 5000 W, 240 Vac Utility Interactive Inverter, Same as Series V with arc detector | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.8 | 5 | 0.8 | 100 | 390 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.2 | 95.3 | 95.7 | 95.8 | 95.8 | 95.7 | 95.7 | 93.8 | 95.2 | 95.8 | 96.1 | 96.3 | 96.2 | 96 | 93.4 | 94.5 | 95.4 | 95.4 | 95.9 | 95.9 | 95.5 | Fronius USA5IG Plus A 5.0 [240V]
Fronius USA | IG Plus A 5.0 [277V] | Y | N | N | 5000 W, 277 Vac Utility Interactive Inverter, Same as Series V with arc detector | 5 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 | 5 | 1.1 | 100 | 330 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.2 | 95.3 | 95.9 | 95.9 | 96.2 | 96.1 | 95.9 | 93.4 | 95.2 | 96 | 96.3 | 96.5 | 96.5 | 96.2 | 93.3 | 95.1 | 95.6 | 95.6 | 96 | 96.3 | 95.7 | Fronius USA5IG Plus A 5.0 [277V]
Fronius USA | IG Plus V 5.0 [208V] | Y | N | N | 5000 W, 208 Vac Utility Interactive Inverter | 5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.6 | 5 | 0.6 | 100 | 366 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.34 | 95.03 | 95.2 | 95.44 | 95.25 | 94.92 | 95.18 | 93.97 | 95.26 | 95.65 | 95.77 | 95.93 | 95.78 | 95.74 | 93.18 | 94.2 | 94.99 | 95.26 | 95.45 | 95.45 | 95.2 | Fronius USA5IG Plus V 5.0 [208V]
Fronius USA | IG Plus V 5.0 [240V] | Y | N | N | 5000 W, 240 Vac Utility Interactive Inverter | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.8 | 5 | 0.8 | 100 | 390 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.16 | 95.32 | 95.66 | 95.84 | 95.81 | 95.66 | 95.66 | 93.84 | 95.24 | 95.83 | 96.07 | 96.25 | 96.24 | 96.02 | 93.42 | 94.51 | 95.36 | 95.35 | 95.85 | 95.91 | 95.52 | Fronius USA5IG Plus V 5.0 [240V]
Fronius USA | IG Plus V 5.0 [277V] | Y | N | N | 5000 W, 277 Vac Utility Interactive Inverter | 5 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 | 5 | 1.1 | 100 | 330 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.16 | 95.3 | 95.92 | 95.92 | 96.2 | 96.13 | 95.94 | 93.36 | 95.17 | 95.97 | 96.32 | 96.45 | 96.45 | 96.18 | 93.31 | 95.08 | 95.59 | 95.57 | 96.02 | 96.25 | 95.73 | Fronius USA5IG Plus V 5.0 [277V]
Fronius USA | IG 5100 NEG | Y | N | N | 5100 W Grid-tied unit with Integrated Disconnects and Performance Meter | 5.1 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.91 |  |  | 100 | 280 | 400 | 0.51 | 1.02 | 1.53 | 2.55 | 3.83 | 5.1 | 91.8 | 93.8 | 94.2 | 94.5 | 94.4 | 93.5 | 94.2 | 92.3 | 94.6 | 95 | 95.2 | 95 | 94.2 | 94.9 | 89.2 | 92.6 | 93.6 | 94.2 | 94.1 | 93.6 | 93.7 | Fronius USA5.1IG 5100 NEG
Fronius USA | IG 5100 POS | Y | N | N | 5100 W Grid-tied unit with Integrated Disconnects and Performance Meter | 5.1 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.91 |  |  | 100 | 280 | 400 | 0.51 | 1.02 | 1.53 | 2.55 | 3.83 | 5.1 | 91.8 | 93.8 | 94.2 | 94.5 | 94.4 | 93.5 | 94.2 | 92.3 | 94.6 | 95 | 95.2 | 95 | 94.2 | 94.9 | 89.2 | 92.6 | 93.6 | 94.2 | 94.1 | 93.6 | 93.7 | Fronius USA5.1IG 5100 POS
Fronius USA | Fronius Primo 6.0-1 208-240 [208V] | Y | N | N | 6000 W, 208 Vac Utility Interactive Inverter with arc detector and meter | 6 | 208 | 96.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 0.41 |  |  | 100 | 660 | 800 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 90.7 | 94.4 | 95.2 | 95.9 | 96 | 95.9 | 95.6 | 93.5 | 96.5 | 97.1 | 97.6 | 97.6 | 97.6 | 97.3 | 91 | 95.4 | 96.4 | 97.2 | 97.3 | 97.4 | 96.8 | Fronius USA6Fronius Primo 6.0-1 208-240 [208V]
Fronius USA | Fronius Primo 6.0-1 208-240 [240V] | Y | N | N | 6000 W, 240 Vac Utility Interactive Inverter with arc detector and meter | 6 | 240 | 96.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 0.55 |  |  | 100 | 660 | 800 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 89.8 | 93.6 | 94.9 | 95.8 | 96 | 96 | 95.4 | 91.4 | 95.3 | 96.3 | 97 | 97.3 | 97.3 | 96.8 | 91.7 | 95.7 | 96.7 | 97.5 | 97.7 | 97.7 | 97.2 | Fronius USA6Fronius Primo 6.0-1 208-240 [240V]
Fronius USA | IG Plus 6.0-1 UNI [208V] | Y | N | N | 6000 W, 208 Vac Utility Interactive Inverter | 6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.71 |  |  | 100 | 366 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1 | 95.3 | 95.1 | 95.4 | 95 | 94.2 | 95 | 95.1 | 95.8 | 95.9 | 96.1 | 96 | 95.6 | 95.9 | 94.5 | 95.1 | 95.4 | 95.5 | 95.4 | 95.2 | 95.3 | Fronius USA6IG Plus 6.0-1 UNI [208V]
Fronius USA | IG Plus 6.0-1 UNI [240V] | Y | N | N | 6000 W, 240 Vac Utility Interactive Inverter | 6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.76 |  |  | 100 | 390 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.8 | 95.5 | 95.6 | 95.9 | 95.7 | 95.1 | 95.6 | 94.8 | 95.7 | 96.1 | 96.3 | 96.3 | 96.1 | 96.2 | 94.4 | 95.2 | 95.6 | 95.8 | 95.9 | 95.8 | 95.7 | Fronius USA6IG Plus 6.0-1 UNI [240V]
Fronius USA | IG Plus 6.0-1 UNI [277V] | Y | N | N | 6000 W, 277 Vac Utility Interactive Inverter | 6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.02 |  |  | 100 | 330 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.8 | 95.5 | 95.9 | 96.1 | 96.1 | 95.7 | 95.9 | 94.3 | 95.7 | 96.1 | 96.3 | 96.4 | 96.3 | 96.2 | 94.4 | 95.3 | 95.9 | 96 | 96.2 | 96.2 | 96 | Fronius USA6IG Plus 6.0-1 UNI [277V]
Fronius USA | IG Plus A 6.0 [208V] | Y | N | N | 6000 W, 208 Vac Utility Interactive Inverter, Same as Series V with arc detector | 6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.6 | 6 | 0.6 | 100 | 366 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.7 | 95.1 | 95.1 | 95.4 | 95.1 | 94.5 | 95.1 | 94.1 | 95.3 | 95.7 | 95.9 | 95.9 | 95.5 | 95.7 | 93.4 | 94.7 | 95.2 | 95.3 | 95.4 | 95.3 | 95.2 | Fronius USA6IG Plus A 6.0 [208V]
Fronius USA | IG Plus A 6.0 [240V] | Y | N | N | 6000 W, 240 Vac Utility Interactive Inverter, Same as Series V with arc detector | 6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.8 | 6 | 0.8 | 100 | 390 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.9 | 95.5 | 95.7 | 95.9 | 95.8 | 95.3 | 95.7 | 94.6 | 95.5 | 96.1 | 96.1 | 96.3 | 96.1 | 96.1 | 93.9 | 95 | 95.7 | 95.6 | 95.9 | 95.9 | 95.7 | Fronius USA6IG Plus A 6.0 [240V]
Fronius USA | IG Plus A 6.0 [277V] | Y | N | N | 6000 W, 277 Vac Utility Interactive Inverter, Same as Series V with arc detector | 6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 | 6 | 1.1 | 100 | 330 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.8 | 95.6 | 96.1 | 96.2 | 96.2 | 96 | 96 | 94.2 | 95.7 | 96.3 | 96.3 | 96.5 | 96.3 | 96.3 | 94.2 | 95.2 | 95.9 | 95.9 | 96.2 | 96.3 | 96 | Fronius USA6IG Plus A 6.0 [277V]
Fronius USA | IG Plus V 6.0 [208V] | Y | N | N | 6000 W, 208 Vac Utility Interactive Inverter | 6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.6 | 6 | 0.6 | 100 | 366 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.72 | 95.06 | 95.09 | 95.38 | 95.12 | 94.52 | 95.08 | 94.07 | 95.31 | 95.73 | 95.86 | 95.85 | 95.45 | 95.72 | 93.4 | 94.66 | 95.15 | 95.3 | 95.4 | 95.26 | 95.23 | Fronius USA6IG Plus V 6.0 [208V]
Fronius USA | IG Plus V 6.0 [240V] | Y | N | N | 6000 W, 240 Vac Utility Interactive Inverter | 6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.8 | 6 | 0.8 | 100 | 390 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.91 | 95.48 | 95.68 | 95.9 | 95.76 | 95.32 | 95.67 | 94.6 | 95.53 | 96.05 | 96.11 | 96.25 | 96.1 | 96.09 | 93.9 | 95.03 | 95.72 | 95.58 | 95.86 | 95.89 | 95.66 | Fronius USA6IG Plus V 6.0 [240V]
Fronius USA | IG Plus V 6.0 [277V] | Y | N | N | 6000 W, 277 Vac Utility Interactive Inverter | 6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 | 6 | 1.1 | 100 | 330 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.77 | 95.63 | 96.05 | 96.16 | 96.18 | 95.95 | 96.03 | 94.23 | 95.73 | 96.25 | 96.32 | 96.46 | 96.33 | 96.27 | 94.15 | 95.17 | 95.87 | 95.85 | 96.18 | 96.33 | 95.95 | Fronius USA6IG Plus V 6.0 [277V]
Fronius USA | IG Plus 7.5-1 UNI [208V] | Y | N | N | 7500 W, 208 Vac Utility Interactive Inverter | 7.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.71 |  |  | 100 | 366 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.63 | 7.5 | 94.4 | 95.2 | 94.7 | 95.1 | 94.4 | 93 | 94.6 | 95 | 95.8 | 95.7 | 96 | 95.7 | 94.8 | 95.7 | 94.2 | 95.2 | 95.3 | 95.4 | 95.2 | 94.6 | 95.2 | Fronius USA7.5IG Plus 7.5-1 UNI [208V]
Fronius USA | IG Plus 7.5-1 UNI [240V] | Y | N | N | 7500 W, 240 Vac Utility Interactive Inverter | 7.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.76 |  |  | 100 | 390 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.63 | 7.5 | 94.4 | 95.5 | 95.3 | 95.7 | 95.3 | 94.3 | 95.3 | 94.8 | 95.8 | 96.1 | 96.2 | 96.1 | 95.7 | 96 | 94.4 | 95.4 | 95.6 | 95.7 | 95.8 | 95.5 | 95.6 | Fronius USA7.5IG Plus 7.5-1 UNI [240V]
Fronius USA | IG Plus 7.5-1 UNI [277V] | Y | N | N | 7500 W, 277 Vac Utility Interactive Inverter | 7.5 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.02 |  |  | 100 | 330 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.63 | 7.5 | 94 | 95.7 | 95.8 | 96.1 | 95.9 | 95.2 | 95.8 | 94.5 | 95.9 | 96.2 | 96.4 | 96.3 | 95.9 | 96.2 | 94.4 | 95.5 | 96 | 96.1 | 96.2 | 96.1 | 96 | Fronius USA7.5IG Plus 7.5-1 UNI [277V]
Fronius USA | IG Plus A 7.5 [208V] | Y | N | N | 7500 W, 208 Vac Utility Interactive Inverter, Same as Series V with arc detector | 7.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.6 | 7.5 | 0.6 | 100 | 366 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.63 | 7.5 | 94.2 | 95.2 | 95 | 95.2 | 94.7 | 93.6 | 94.8 | 94.5 | 95.7 | 95.7 | 95.9 | 95.6 | 94.9 | 95.6 | 93 | 95.1 | 95.4 | 95.4 | 95.3 | 94.9 | 95.2 | Fronius USA7.5IG Plus A 7.5 [208V]
Fronius USA | IG Plus A 7.5 [240V] | Y | N | N | 7500 W, 240 Vac Utility Interactive Inverter, Same as Series V with arc detector | 7.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.8 | 7.5 | 0.8 | 100 | 390 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.63 | 7.5 | 94.4 | 95.6 | 95.6 | 95.8 | 95.5 | 94.7 | 95.5 | 94.5 | 95.9 | 96.1 | 96.2 | 96.2 | 95.7 | 96.1 | 94 | 95.3 | 95.7 | 95.8 | 95.9 | 95.6 | 95.7 | Fronius USA7.5IG Plus A 7.5 [240V]
Fronius USA | IG Plus A 7.5 [277V] | Y | N | N | 7500 W, 277 Vac Utility Interactive Inverter, Same as Series V with arc detector | 7.5 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 | 7.5 | 1.1 | 100 | 330 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.63 | 7.5 | 94.1 | 95.7 | 95.9 | 96.2 | 96 | 95.5 | 95.9 | 94.3 | 95.8 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.9 | 95.3 | 95.8 | 96 | 96.2 | 96.1 | 95.9 | Fronius USA7.5IG Plus A 7.5 [277V]
Fronius USA | IG Plus V 7.5 [208V] | Y | N | N | 7500 W, 208 Vac Utility Interactive Inverter | 7.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.6 | 7.5 | 0.6 | 100 | 366 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.625 | 7.5 | 94.23 | 95.18 | 95 | 95.19 | 94.68 | 93.6 | 94.78 | 94.47 | 95.69 | 95.69 | 95.89 | 95.6 | 94.94 | 95.6 | 93.01 | 95.11 | 95.35 | 95.4 | 95.31 | 94.87 | 95.21 | Fronius USA7.5IG Plus V 7.5 [208V]
Fronius USA | IG Plus V 7.5 [240V] | Y | N | N | 7500 W, 240 Vac Utility Interactive Inverter | 7.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.8 | 7.5 | 0.8 | 100 | 390 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.625 | 7.5 | 94.37 | 95.6 | 95.61 | 95.78 | 95.46 | 94.73 | 95.47 | 94.49 | 95.9 | 96.06 | 96.22 | 96.16 | 95.73 | 96.06 | 93.98 | 95.29 | 95.68 | 95.83 | 95.86 | 95.61 | 95.71 | Fronius USA7.5IG Plus V 7.5 [240V]
Fronius USA | IG Plus V 7.5 [277V] | Y | N | N | 7500 W, 277 Vac Utility Interactive Inverter | 7.5 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 | 7.5 | 1.1 | 100 | 330 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.625 | 7.5 | 94.05 | 95.73 | 95.93 | 96.15 | 95.95 | 95.45 | 95.88 | 94.27 | 95.84 | 96.09 | 96.36 | 96.26 | 95.96 | 96.14 | 93.86 | 95.28 | 95.81 | 95.97 | 96.16 | 96.11 | 95.94 | Fronius USA7.5IG Plus V 7.5 [277V]
Fronius USA | Fronius Primo 7.6-1 208-240 [208V] | Y | N | N | 7600 W, 208 Vac Utility Interactive Inverter with arc detector and meter | 7.6 | 208 | 97 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 0.41 |  |  | 100 | 660 | 800 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.7 | 95.1 | 95.8 | 96.1 | 96.1 | 95.8 | 95.8 | 96 | 97.4 | 97.7 | 97.8 | 97.7 | 97.6 | 97.7 | 94.1 | 96.7 | 97.3 | 97.6 | 97.5 | 97.4 | 97.3 | Fronius USA7.6Fronius Primo 7.6-1 208-240 [208V]
Fronius USA | Fronius Primo 7.6-1 208-240 [240V] | Y | N | N | 7600 W, 240 Vac Utility Interactive Inverter with arc detector and meter | 7.6 | 240 | 97 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 0.55 |  |  | 100 | 660 | 800 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 91.6 | 94.8 | 95.5 | 96 | 96.1 | 95.9 | 95.7 | 94 | 96.4 | 97 | 97.4 | 97.5 | 97.4 | 97.2 | 94.6 | 97 | 97.6 | 97.9 | 97.9 | 97.8 | 97.7 | Fronius USA7.6Fronius Primo 7.6-1 208-240 [240V]
Fronius USA | Fronius Primo 8.2-1 208-240 [208V] | Y | N | N | 7900 W, 208 Vac Utility Interactive Inverter with arc detector and meter | 7.9 | 208 | 97 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 0.41 |  |  | 100 | 660 | 800 | 0.79 | 1.58 | 2.37 | 3.95 | 5.93 | 7.9 | 93 | 95.3 | 95.9 | 96.2 | 96.2 | 95.9 | 96 | 95.8 | 97.3 | 97.7 | 97.8 | 97.8 | 97.5 | 97.7 | 94 | 96.7 | 97.3 | 97.6 | 97.6 | 97.4 | 97.3 | Fronius USA7.9Fronius Primo 8.2-1 208-240 [208V]
Fronius USA | Fronius Primo 8.2-1 208-240 [240V] | Y | N | N | 8200 W, 240 Vac Utility Interactive Inverter with arc detector and meter | 8.2 | 240 | 97 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 0.55 |  |  | 100 | 660 | 800 | 0.82 | 1.64 | 2.46 | 4.1 | 6.15 | 8.2 | 92.1 | 94.9 | 95.7 | 96.2 | 96.2 | 96.1 | 95.9 | 94.2 | 96.6 | 97.1 | 97.4 | 97.4 | 97.4 | 97.2 | 94.7 | 97.1 | 97.6 | 97.9 | 97.9 | 97.8 | 97.7 | Fronius USA8.2Fronius Primo 8.2-1 208-240 [240V]
Fronius USA | Fronius Primo 10.0-1 [208V] | Y | N | N | 9995 W, 208 Vac Utility Interactive Inverter with arc detector | 9.995 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.24 |  |  | 100 | 660 | 800 | 1 | 2 | 3 | 5 | 7.5 | 10 | 92 | 94.7 | 95.1 | 95.6 | 95.6 | 95.5 | 95.3 | 94.5 | 97.4 | 96.8 | 97.3 | 97.3 | 97.4 | 97.1 | 93.3 | 97.1 | 96.5 | 97 | 97.3 | 97.3 | 97 | Fronius USA9.995Fronius Primo 10.0-1 [208V]
Fronius USA | Fronius Primo 10.0-1 [240V] | Y | N | N | 9995 W, 240 Vac Utility Interactive Inverter with arc detector | 9.995 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 100 | 655 | 800 | 1 | 2 | 3 | 5 | 7.5 | 10 | 91.4 | 94.3 | 94.8 | 95.4 | 95.6 | 95.6 | 95.2 | 93.5 | 95.8 | 96.3 | 96.9 | 97.1 | 97 | 96.7 | 95.6 | 97 | 97.2 | 97.6 | 97.7 | 97.5 | 97.5 | Fronius USA9.995Fronius Primo 10.0-1 [240V]
Fronius USA | Fronius Symo 10.0-3 208-240 [208V] | Y | N | N | 9.995 kW, 208 Vac Utility Interactive Inverter | 9.995 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.81 |  |  | 100 | 370 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94 | 95.6 | 96.1 | 96.2 | 96.2 | 96 | 96.1 | 95.4 | 96.8 | 97 | 97.1 | 97.1 | 96.9 | 97 | 94.8 | 96.4 | 96.7 | 96.9 | 96.9 | 96.7 | 96.7 | Fronius USA9.995Fronius Symo 10.0-3 208-240 [208V]
Fronius USA | Fronius Symo 10.0-3 208-240 [240V] | Y | N | N | 9.995 kW, 240 Vac Utility Interactive Inverter | 9.995 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.8 |  |  | 100 | 370 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94 | 95.6 | 96.1 | 96.2 | 96.2 | 96 | 96.1 | 95.4 | 96.8 | 97 | 97.1 | 97.1 | 96.9 | 97 | 94.8 | 96.4 | 96.7 | 96.9 | 96.9 | 96.7 | 96.7 | Fronius USA9.995Fronius Symo 10.0-3 208-240 [240V]
Fronius USA | Fronius Symo 10.0-3 480 [480V] | Y | N | N | 9.995 kW, 480 Vac Utility Interactive Inverter | 9.995 | 480 | 96.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 0.86 |  |  | 100 | 670 | 800 | 1 | 2 | 3 | 5 | 7.5 | 10 | 89.6 | 93.7 | 94.8 | 95.3 | 96 | 96.2 | 95.3 | 91.8 | 95.2 | 96.1 | 96.7 | 97.2 | 97.3 | 96.6 | 92.9 | 96.1 | 96.9 | 97.3 | 97.7 | 97.8 | 97.2 | Fronius USA9.995Fronius Symo 10.0-3 480 [480V]
Fronius USA | IG Plus 10.0-1 UNI [208V] | Y | N | N | 9995W, 208 Vac Utility Interactive Inverter | 9.995 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.64 |  |  | 100 | 366 | 480 | 0.9995 | 1.999 | 2.999 | 4.998 | 7.496 | 9.995 | 93.8 | 94.5 | 95.2 | 95.3 | 94.9 | 93.8 | 94.9 | 93.5 | 95.2 | 95.6 | 95.9 | 95.8 | 95.3 | 95.6 | 92.5 | 94.4 | 94.8 | 95.2 | 95.2 | 95 | 95 | Fronius USA9.995IG Plus 10.0-1 UNI [208V]
Fronius USA | IG Plus 10.0-1 UNI [240V] | Y | N | N | 9995W, 240 Vac Utility Interactive Inverter | 9.995 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.85 |  |  | 100 | 390 | 480 | 0.9995 | 1.999 | 2.999 | 4.998 | 7.496 | 9.995 | 94.1 | 95.1 | 95.7 | 95.8 | 95.5 | 94.9 | 95.5 | 93.7 | 95.5 | 95.9 | 96.2 | 96.2 | 96 | 96 | 93.2 | 95 | 95.3 | 95.6 | 95.7 | 95.6 | 95.5 | Fronius USA9.995IG Plus 10.0-1 UNI [240V]
Fronius USA | IG Plus 10.0-1 UNI [277V] | Y | N | N | 9995W, 277 Vac Utility Interactive Inverter | 9.995 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.13 |  |  | 100 | 330 | 480 | 0.9995 | 1.999 | 2.999 | 4.998 | 7.496 | 9.995 | 94.2 | 95.7 | 95.9 | 96.1 | 96 | 95.6 | 95.9 | 94.5 | 96 | 96.1 | 96.3 | 96.4 | 96.3 | 96.3 | 94.5 | 95.6 | 95.7 | 96 | 96.1 | 96.2 | 96 | Fronius USA9.995IG Plus 10.0-1 UNI [277V]
Fronius USA | IG Plus V 10.0-3 Delta [208V] | Y | N | N | 10000 W, 208 Vac 3-Phase Utility Interactive Inverter | 9.995 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 | 9.995 | 0.9 | 100 | 366 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.1 | 94.7 | 95.3 | 95.3 | 95 | 94.1 | 95 | 94.3 | 95.4 | 95.7 | 96 | 95.8 | 95.2 | 95.7 | 93.3 | 95 | 95.1 | 95.4 | 95.4 | 95.1 | 95.3 | Fronius USA9.995IG Plus V 10.0-3 Delta [208V]
Fronius USA | IG Plus V 10.0-3 Delta [240V] | Y | N | N | 10000 W, 240 Vac 3-Phase Utility Interactive Inverter | 9.995 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.2 | 9.995 | 1.2 | 100 | 366 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.5 | 95.5 | 95.7 | 95.9 | 95.7 | 95.1 | 95.6 | 94.1 | 95.5 | 95.7 | 95.9 | 95.9 | 95.6 | 95.8 | 93.5 | 95.4 | 95.4 | 95.7 | 95.9 | 95.8 | 95.7 | Fronius USA9.995IG Plus V 10.0-3 Delta [240V]
Fronius USA | IG Plus A 10.0 [208V] | Y | N | N | 10000 W, 208 Vac Utility Interactive Inverter, Same as Series V with arc detector | 10 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.77 | 10 | 0.77 | 100 | 366 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94 | 94.6 | 95.1 | 95.2 | 94.8 | 94 | 94.8 | 93.9 | 95.3 | 95.6 | 95.8 | 95.6 | 95.1 | 95.6 | 92.8 | 94.8 | 94.9 | 95.3 | 95.3 | 95 | 95.1 | Fronius USA10IG Plus A 10.0 [208V]
Fronius USA | IG Plus A 10.0 [240V] | Y | N | N | 10000 W, 240 Vac Utility Interactive Inverter, Same as Series V with arc detector | 10 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 10 | 1 | 100 | 390 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.2 | 95.2 | 95.6 | 95.7 | 95.5 | 94.9 | 95.5 | 93.8 | 95.6 | 95.8 | 96 | 96.1 | 95.9 | 95.9 | 93.2 | 95.1 | 95.2 | 95.6 | 95.8 | 95.7 | 95.5 | Fronius USA10IG Plus A 10.0 [240V]
Fronius USA | IG Plus A 10.0 [277V] | Y | N | N | 10000 W, 277 Vac Utility Interactive Inverter, Same as Series V with arc detector | 10 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.36 | 10 | 1.36 | 100 | 330 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.3 | 95.7 | 95.9 | 96.1 | 96 | 95.6 | 95.9 | 94.1 | 95.9 | 96 | 96.2 | 96.3 | 96.1 | 96.1 | 93.7 | 95.5 | 95.4 | 95.8 | 96.1 | 96.2 | 95.8 | Fronius USA10IG Plus A 10.0 [277V]
Fronius USA | IG Plus A 10.0-3 Delta [208V] | Y | N | N | 10000 W, 208 Vac Utility Interactive Inverter, Same as Series V with arc detector | 10 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 | 10 | 0.9 | 100 | 366 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.1 | 94.7 | 95.3 | 95.3 | 95 | 94.1 | 95 | 94.3 | 95.4 | 95.7 | 96 | 95.8 | 95.2 | 95.7 | 93.3 | 95 | 95.1 | 95.4 | 95.4 | 95.1 | 95.3 | Fronius USA10IG Plus A 10.0-3 Delta [208V]
Fronius USA | IG Plus A 10.0-3 Delta [240V] | Y | N | N | 10000 W, 240 Vac Utility Interactive Inverter, Same as Series V with arc detector | 10 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.2 | 10 | 1.2 | 100 | 366 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.5 | 95.5 | 95.7 | 95.9 | 95.7 | 95.1 | 95.6 | 94.1 | 95.5 | 95.7 | 95.9 | 95.9 | 95.6 | 95.8 | 93.5 | 95.4 | 95.4 | 95.7 | 95.9 | 95.8 | 95.7 | Fronius USA10IG Plus A 10.0-3 Delta [240V]
Fronius USA | IG Plus V 10.0 [208V] | Y | N | N | 10000 W, 208 Vac Utility Interactive Inverter | 10 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.77 | 10 | 0.77 | 100 | 366 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 93.96 | 94.59 | 95.13 | 95.15 | 94.79 | 93.95 | 94.82 | 93.94 | 95.27 | 95.61 | 95.79 | 95.64 | 95.11 | 95.55 | 92.8 | 94.78 | 94.89 | 95.27 | 95.3 | 95 | 95.1 | Fronius USA10IG Plus V 10.0 [208V]
Fronius USA | IG Plus V 10.0 [240V] | Y | N | N | 10000 W, 240 Vac Utility Interactive Inverter | 10 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 10 | 1 | 100 | 390 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.18 | 95.24 | 95.61 | 95.7 | 95.51 | 94.94 | 95.47 | 93.77 | 95.61 | 95.8 | 96.04 | 96.12 | 95.86 | 95.93 | 93.16 | 95.13 | 95.2 | 95.55 | 95.79 | 95.7 | 95.52 | Fronius USA10IG Plus V 10.0 [240V]
Fronius USA | IG Plus V 10.0 [277V] | Y | N | N | 10000 W, 277 Vac Utility Interactive Inverter | 10 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.36 | 10 | 1.36 | 100 | 330 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.28 | 95.67 | 95.87 | 96.05 | 95.98 | 95.59 | 95.88 | 94.07 | 95.87 | 96.02 | 96.23 | 96.3 | 96.08 | 96.13 | 93.68 | 95.46 | 95.44 | 95.8 | 96.12 | 96.16 | 95.84 | Fronius USA10IG Plus V 10.0 [277V]
Fronius USA | Fronius Primo 11.4-1 [208V] | Y | N | N | 11,400W, 208 Vac Utility Interactive Inverter with arc detector | 11.4 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.24 |  |  | 240 | 660 | 800 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 93 | 94.9 | 95.4 | 95.8 | 95.8 | 95.7 | 95.6 | 95.4 | 97 | 97.3 | 97.4 | 97.4 | 97.4 | 97.3 | 94.5 | 96.4 | 96.9 | 97.2 | 97.2 | 97.3 | 97.1 | Fronius USA11.4Fronius Primo 11.4-1 [208V]
Fronius USA | Fronius Primo 11.4-1 [240V] | Y | N | N | 11,400W, 240 Vac Utility Interactive Inverter with arc detector | 11.4 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 240 | 660 | 800 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 92.1 | 94.8 | 95.3 | 95.8 | 95.9 | 95.8 | 95.6 | 93.7 | 96.1 | 96.6 | 97 | 97.1 | 97.1 | 96.9 | 94.8 | 96.9 | 97.4 | 97.6 | 97.6 | 97.6 | 97.4 | Fronius USA11.4Fronius Primo 11.4-1 [240V]
Fronius USA | IG Plus 11.4-1 UNI [208V] | Y | N | N | 11400 W, 208 Vac Utility Interactive Inverter | 11.4 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.64 |  |  | 230 | 366 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.7 | 94.6 | 95.3 | 95.3 | 94.6 | 93.2 | 94.7 | 95.1 | 95.7 | 96 | 96 | 95.7 | 95 | 95.8 | 94.1 | 95.1 | 95.3 | 95.5 | 95.3 | 94.8 | 95.3 | Fronius USA11.4IG Plus 11.4-1 UNI [208V]
Fronius USA | IG Plus 11.4-1 UNI [240V] | Y | N | N | 11400 W, 240 Vac Utility Interactive Inverter | 11.4 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.85 |  |  | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.7 | 95.2 | 95.7 | 95.8 | 95.4 | 94.5 | 95.4 | 94.6 | 95.9 | 96.2 | 96.2 | 96.2 | 95.9 | 96.1 | 94.2 | 95.4 | 95.6 | 95.8 | 95.8 | 95.7 | 95.7 | Fronius USA11.4IG Plus 11.4-1 UNI [240V]
Fronius USA | IG Plus 11.4-1 UNI [277V] | Y | N | N | 11400 W, 277 Vac Utility Interactive Inverter | 11.4 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.13 |  |  | 240 | 330 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.7 | 95.6 | 96 | 96.1 | 95.9 | 95.3 | 95.9 | 94.8 | 96 | 96.2 | 96.4 | 96.4 | 96 | 96.2 | 94.4 | 95.8 | 95.8 | 96.1 | 96.2 | 96 | 96 | Fronius USA11.4IG Plus 11.4-1 UNI [277V]
Fronius USA | IG Plus 11.4-3 Delta [208V] | Y | N | N | 11400 W, 208 Vac 3-Phase Utility Interactive Inverter | 11.4 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 230 | 365 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.2 | 94.3 | 95.1 | 95.1 | 94.4 | 93 | 94.55 | 94.4 | 95.3 | 95.8 | 95.9 | 95.6 | 94.9 | 95.59 | 93.4 | 94.6 | 95 | 95.3 | 95.2 | 94.7 | 95.05 | Fronius USA11.4IG Plus 11.4-3 Delta [208V]
Fronius USA | IG Plus 11.4-3 Delta [240V] | Y | N | N | 11400 W, 240 Vac 3-Phase Utility Interactive Inverter | 11.4 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.3 | 95 | 95.6 | 95.7 | 95.2 | 94.2 | 95.25 | 94.1 | 95.7 | 96 | 96.2 | 96.1 | 95.7 | 95.99 | 93.4 | 95.1 | 95.4 | 95.7 | 95.7 | 95.6 | 95.54 | Fronius USA11.4IG Plus 11.4-3 Delta [240V]
Fronius USA | IG Plus A 11.4 [208V] | Y | N | N | 11400 W, 208 Vac Utility Interactive Inverter, Same as Series V with arc detector | 11.4 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.77 | 11.4 | 0.77 | 230 | 366 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.4 | 94.6 | 95.1 | 95.1 | 94.5 | 93.3 | 94.6 | 94.6 | 95.3 | 95.7 | 95.8 | 95.4 | 94.8 | 95.5 | 93.3 | 95 | 95.2 | 95.3 | 95.2 | 94.7 | 95.1 | Fronius USA11.4IG Plus A 11.4 [208V]
Fronius USA | IG Plus A 11.4 [240V] | Y | N | N | 11400 W, 240 Vac Utility Interactive Inverter, Same as Series V with arc detector | 11.4 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 11.4 | 1 | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.6 | 95.2 | 95.6 | 95.7 | 95.3 | 94.5 | 95.3 | 94.3 | 95.7 | 95.9 | 96.1 | 96 | 95.6 | 95.9 | 93.6 | 95.4 | 95.5 | 95.7 | 95.8 | 95.5 | 95.6 | Fronius USA11.4IG Plus A 11.4 [240V]
Fronius USA | IG Plus A 11.4 [277V] | Y | N | N | 11400 W, 277 Vac Utility Interactive Inverter, Same as Series V with arc detector | 11.4 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.36 | 11.4 | 1.36 | 230 | 330 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.7 | 95.7 | 95.9 | 96 | 95.8 | 95.3 | 95.8 | 94.5 | 95.9 | 96.1 | 96.3 | 96.2 | 95.9 | 96.1 | 93.9 | 95.7 | 95.7 | 96 | 96.1 | 96.1 | 95.9 | Fronius USA11.4IG Plus A 11.4 [277V]
Fronius USA | IG Plus A 11.4-3 Delta [208V] | Y | N | N | 11400 W, 208 Vac 3-Phase Utility Interactive Inverter, Same as Series V with arc detector | 11.4 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.77 | 11.4 | 0.77 | 230 | 366 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.4 | 94.6 | 95.1 | 95.1 | 94.5 | 93.3 | 94.6 | 94.6 | 95.3 | 95.7 | 95.8 | 95.4 | 94.8 | 95.5 | 93.3 | 95 | 95.2 | 95.3 | 95.2 | 94.7 | 95.1 | Fronius USA11.4IG Plus A 11.4-3 Delta [208V]
Fronius USA | IG Plus A 11.4-3 Delta [240V] | Y | N | N | 11400 W, 240 Vac 3-Phase Utility Interactive Inverter, Same as Series V with arc detector | 11.4 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.2 | 11.4 | 1.2 | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.7 | 95.4 | 95.8 | 95.8 | 95.5 | 94.7 | 95.5 | 94.5 | 95.8 | 96 | 96.3 | 96.2 | 95.8 | 96.1 | 94 | 95.4 | 95.5 | 95.8 | 95.9 | 95.7 | 95.7 | Fronius USA11.4IG Plus A 11.4-3 Delta [240V]
Fronius USA | IG Plus V 11.4 [208V] | Y | N | N | 11400 W, 208 Vac Utility Interactive Inverter | 11.4 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.77 | 11.4 | 0.77 | 230 | 366 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.38 | 94.56 | 95.11 | 95.08 | 94.48 | 93.34 | 94.63 | 94.57 | 95.31 | 95.74 | 95.78 | 95.43 | 94.8 | 95.47 | 93.33 | 94.99 | 95.17 | 95.33 | 95.22 | 94.66 | 95.12 | Fronius USA11.4IG Plus V 11.4 [208V]
Fronius USA | IG Plus V 11.4 [240V] | Y | N | N | 11400 W, 240 Vac Utility Interactive Inverter | 11.4 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 11.4 | 1 | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.59 | 95.19 | 95.62 | 95.67 | 95.28 | 94.5 | 95.33 | 94.33 | 95.72 | 95.9 | 96.12 | 96.01 | 95.61 | 95.92 | 93.56 | 95.36 | 95.49 | 95.7 | 95.77 | 95.51 | 95.6 | Fronius USA11.4IG Plus V 11.4 [240V]
Fronius USA | IG Plus V 11.4 [277V] | Y | N | N | 11400 W, 277 Vac Utility Interactive Inverter | 11.4 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.36 | 11.4 | 1.36 | 230 | 330 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.66 | 95.65 | 95.94 | 96.03 | 95.84 | 95.31 | 95.81 | 94.49 | 95.89 | 96.13 | 96.27 | 96.21 | 95.88 | 96.11 | 93.86 | 95.69 | 95.65 | 95.97 | 96.14 | 96.05 | 95.93 | Fronius USA11.4IG Plus V 11.4 [277V]
Fronius USA | IG Plus V 11.4-3 Delta [208V] | Y | N | N | 11400 W, 208 Vac 3-Phase Utility Interactive Inverter | 11.4 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.77 | 11.4 | 0.77 | 230 | 366 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.4 | 94.6 | 95.1 | 95.1 | 94.5 | 93.3 | 94.63 | 94.6 | 95.3 | 95.7 | 95.8 | 95.4 | 94.8 | 95.47 | 93.3 | 95 | 95.2 | 95.3 | 95.2 | 94.7 | 95.12 | Fronius USA11.4IG Plus V 11.4-3 Delta [208V]
Fronius USA | IG Plus V 11.4-3 Delta [240V] | Y | N | N | 11401 W, 240 Vac 3-Phase Utility Interactive Inverter | 11.4 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.2 | 11.4 | 1.2 | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.67 | 95.44 | 95.75 | 95.82 | 95.47 | 94.68 | 95.5 | 94.49 | 95.79 | 96.03 | 96.25 | 96.15 | 95.75 | 96.05 | 94.01 | 95.42 | 95.54 | 95.83 | 95.87 | 95.65 | 95.71 | Fronius USA11.4IG Plus V 11.4-3 Delta [240V]
Fronius USA | Fronius Symo 12.0-3 208-240 [208V] | Y | N | N | 11.995 kW, 208 Vac Utility Interactive Inverter | 12 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 300 | 350 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 95.4 | 96.2 | 96.3 | 96.2 | 95.9 | 95.4 | 95.9 | 96.3 | 96.9 | 96.9 | 96.8 | 96.5 | 96.2 | 96.6 | 94.7 | 96.1 | 96.4 | 96.4 | 96.3 | 96 | 96.2 | Fronius USA12Fronius Symo 12.0-3 208-240 [208V]
Fronius USA | Fronius Symo 12.0-3 208-240 [240V] | Y | N | N | 11.995 kW, 240 Vac Utility Interactive Inverter | 12 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.81 |  |  | 300 | 370 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 94.4 | 95.9 | 96.2 | 96.3 | 96.1 | 95.8 | 96.1 | 96 | 96.9 | 97.1 | 97.1 | 97 | 96.8 | 97 | 95.2 | 96.6 | 96.8 | 96.9 | 96.8 | 96.6 | 96.7 | Fronius USA12Fronius Symo 12.0-3 208-240 [240V]
Fronius USA | IG Plus 12.0-3 WYE [277V] | Y | N | N | 12000 W, 3-phase WYE 277 Vac Utility Interactive Inverter | 12 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 240 | 330 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 94.7 | 95.5 | 95.9 | 96 | 95.8 | 95.1 | 95.8 | 94.7 | 95.9 | 96.1 | 96.3 | 96.3 | 95.8 | 96.2 | 94.3 | 95.7 | 95.8 | 96 | 96.2 | 96 | 96 | Fronius USA12IG Plus 12.0-3 WYE [277V]
Fronius USA | IG Plus A 12.0-3 WYE [277V] | Y | N | N | 12000 W, 3-phase WYE 277 Vac Utility Interactive Inverter, Same as Series V with arc detector | 12 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 | 12 | 0.5 | 240 | 330 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.6 | 95.2 | 96.2 | 96.3 | 96.1 | 95.4 | 95.9 | 92.5 | 95.7 | 96.2 | 96.6 | 96.5 | 96.1 | 96.2 | 94.4 | 95.6 | 95.8 | 96.2 | 96.4 | 96.3 | 96.2 | Fronius USA12IG Plus A 12.0-3 WYE [277V]
Fronius USA | IG Plus V 12.0-3 WYE [277V] | Y | N | N | 12000 W, 3-phase WYE 277 Vac Utility Interactive Inverter | 12 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 | 12 | 0.5 | 240 | 330 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.62 | 95.2 | 96.16 | 96.32 | 96.05 | 95.44 | 95.91 | 92.45 | 95.69 | 96.17 | 96.56 | 96.45 | 96.06 | 96.22 | 94.43 | 95.61 | 95.78 | 96.24 | 96.43 | 96.29 | 96.19 | Fronius USA12IG Plus V 12.0-3 WYE [277V]
Fronius USA | Fronius Primo 12.5-1 [208V] | Y | N | N | 12,500W, 208 Vac Utility Interactive Inverter with arc detector | 12.5 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.24 |  |  | 260 | 665 | 800 | 1.25 | 2.5 | 3.75 | 6.25 | 9.38 | 12.5 | 92.5 | 95.1 | 95.5 | 95.9 | 95.9 | 95.6 | 95.6 | 95.3 | 96.9 | 97.3 | 97.5 | 97.3 | 97.3 | 97.2 | 94.5 | 96.6 | 97 | 97.2 | 97.1 | 97.2 | 97 | Fronius USA12.5Fronius Primo 12.5-1 [208V]
Fronius USA | Fronius Primo 12.5-1 [240V] | Y | N | N | 12,500W, 240 Vac Utility Interactive Inverter with arc detector | 12.5 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 260 | 660 | 800 | 1.25 | 2.5 | 3.75 | 6.25 | 9.38 | 12.5 | 92.1 | 95 | 95.4 | 95.9 | 95.9 | 95.8 | 95.6 | 93.7 | 96.2 | 96.6 | 97 | 97.1 | 97.1 | 96.8 | 95.4 | 97.2 | 97.3 | 97.5 | 97.6 | 97.7 | 97.5 | Fronius USA12.5Fronius Primo 12.5-1 [240V]
Fronius USA | Fronius Symo 12.5-3 480 [480V] | Y | N | N | 12.495 kW, 480 Vac Utility Interactive Inverter | 12.5 | 480 | 97 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 0.94 |  |  | 350 | 685 | 800 | 1.25 | 2.5 | 3.75 | 6.25 | 9.37 | 12.5 | 92.5 | 94.9 | 95.6 | 96 | 96.4 | 96.5 | 96 | 94.4 | 96.5 | 97 | 97.3 | 97.5 | 97.5 | 97.2 | 95.6 | 97.3 | 97.7 | 97.9 | 98 | 98 | 97.8 | Fronius USA12.5Fronius Symo 12.5-3 480 [480V]
Fronius USA | Fronius Primo 15.0-1 [208V] | Y | N | N | 13,750W, 208 Vac Utility Interactive Inverter with arc detector | 13.75 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.24 |  |  | 320 | 680 | 800 | 1.38 | 2.75 | 4.13 | 6.88 | 10.31 | 13.75 | 93.3 | 95.7 | 96 | 96.3 | 96.2 | 96 | 96 | 95.9 | 97.1 | 97.4 | 97.4 | 97.4 | 97.2 | 97.3 | 95.1 | 96.8 | 97.1 | 97.2 | 97.2 | 97.1 | 97.1 | Fronius USA13.75Fronius Primo 15.0-1 [208V]
Fronius USA | Fronius Primo 15.0-1 [240V] | Y | N | N | 15,000W, 240 Vac Utility Interactive Inverter with arc detector | 15 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 320 | 680 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.5 | 95.5 | 96 | 96.3 | 96.3 | 96.1 | 96.1 | 94.5 | 96.5 | 96.9 | 97.2 | 97.2 | 97 | 97 | 95.7 | 97.2 | 97.5 | 97.6 | 97.6 | 97.4 | 97.5 | Fronius USA15Fronius Primo 15.0-1 [240V]
Fronius USA | Fronius Symo 15.0-3 [208V] | Y | N | N | 15,000W, 208 Vac Utility Interactive Inverter with arc detector | 15 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.43 |  |  | 325 | 445 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 96.1 | 97 | 97.1 | 97.1 | 96.9 | 96.7 | 96.9 | 95.3 | 96.4 | 96.6 | 96.7 | 96.5 | 96.2 | 96.5 | 92.7 | 94.9 | 95.4 | 95.6 | 95.5 | 95.3 | 95.4 | Fronius USA15Fronius Symo 15.0-3 [208V]
Fronius USA | Fronius Symo 15.0-3 480 [480V] | Y | N | N | 14.995 kW, 480 Vac Utility Interactive Inverter | 15 | 480 | 97 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 1.03 |  |  | 350 | 685 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 92 | 94.9 | 95.6 | 96.2 | 96.5 | 96.4 | 96.1 | 93.5 | 96 | 96.7 | 97.2 | 97.4 | 97.4 | 97.1 | 94.6 | 96.8 | 97.4 | 97.8 | 97.9 | 97.9 | 97.6 | Fronius USA15Fronius Symo 15.0-3 480 [480V]
Fronius USA | Fronius Symo 17.5-3 480 [480V] | Y | N | N | 17.495 kW, 480 Vac Utility Interactive Inverter | 17.5 | 480 | 97.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 1.03 |  |  | 400 | 700 | 800 | 1.75 | 3.5 | 5.25 | 8.75 | 13.12 | 17.5 | 92.7 | 95.3 | 95.8 | 96.5 | 96.6 | 96.7 | 96.3 | 95.7 | 97.4 | 97.8 | 98.1 | 98.1 | 98.2 | 98 | 94.8 | 96.9 | 97.4 | 97.7 | 97.8 | 97.8 | 97.6 | Fronius USA17.5Fronius Symo 17.5-3 480 [480V]
Fronius USA | Fronius Symo 20.0-3 480 [480V] | Y | N | N | 19995 W, 480 Vac Utility Interactive Inverter with arc detector and meter | 20 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.03 |  |  | 450 | 712 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.1 | 95.5 | 96.1 | 96.7 | 96.8 | 96.8 | 96.5 | 95.1 | 97 | 97.5 | 97.9 | 98 | 98 | 97.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.8 | 97.5 | Fronius USA20Fronius Symo 20.0-3 480 [480V]
Fronius USA | Fronius Symo 22.7-3 480 [480V] | Y | N | N | 22.727 kW, 480 Vac Utility Interactive Inverter | 22.73 | 480 | 97.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 1.03 |  |  | 500 | 720 | 800 | 2.27 | 4.55 | 6.82 | 11.36 | 17.05 | 22.73 | 94.3 | 96.2 | 96.7 | 97 | 97 | 96.9 | 96.8 | 96.4 | 97.6 | 97.8 | 98 | 98 | 98 | 97.9 | 95.9 | 97.3 | 97.7 | 97.8 | 97.9 | 97.8 | 97.7 | Fronius USA22.73Fronius Symo 22.7-3 480 [480V]
Fronius USA | Fronius Symo 24.0-3 480 [480V] | Y | N | N | 23.995 kW, 480 Vac Utility Interactive Inverter | 24 | 480 | 97.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 1.03 |  |  | 500 | 725 | 800 | 2.4 | 4.8 | 7.2 | 12 | 18 | 24 | 94.3 | 96.1 | 96.6 | 97 | 97 | 97 | 96.8 | 96.2 | 97.5 | 97.8 | 98 | 98 | 97.9 | 97.9 | 95.8 | 97.2 | 97.6 | 97.8 | 97.8 | 97.7 | 97.7 | Fronius USA24Fronius Symo 24.0-3 480 [480V]
Fronius USA | CL 33.3 Delta [208V] | Y | N | N | 33.3 kW, 208 Vac Delta Utility Interactive Inverter | 33.3 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.85 |  |  | 230 | 366 | 480 | 3.33 | 6.66 | 9.99 | 16.65 | 24.98 | 33.3 | 93.57 | 93.75 | 94.54 | 94.56 | 94.04 | 93.04 | 94.12 | 94.11 | 94.65 | 95.17 | 95.28 | 94.96 | 94.25 | 94.96 | 93.36 | 94.22 | 94.57 | 94.81 | 94.68 | 94.16 | 94.59 | Fronius USA33.3CL 33.3 Delta [208V]
Fronius USA | CL 33.3 Delta [240V] | Y | N | N | 33.3 kW, 240 Vac Delta Utility Interactive Inverter | 33.3 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.53 |  |  | 230 | 390 | 480 | 3.33 | 6.66 | 9.99 | 16.65 | 24.98 | 33.3 | 94.09 | 94.75 | 95.13 | 95.25 | 94.86 | 94.11 | 94.9 | 94.44 | 95.29 | 95.54 | 95.76 | 95.61 | 95.14 | 95.55 | 93.81 | 95.15 | 95.03 | 95.41 | 95.29 | 95.02 | 95.21 | Fronius USA33.3CL 33.3 Delta [240V]
Fronius USA | CL 36.0 Wye [277V] | Y | N | N | 36 kW, 277 Vac Wye Utility Interactive Inverter | 36 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.03 |  |  | 240 | 330 | 480 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 94.33 | 95.14 | 95.48 | 95.74 | 95.49 | 94.88 | 95.45 | 94.51 | 95.53 | 95.5 | 95.98 | 95.89 | 95.51 | 95.77 | 94.15 | 95.46 | 95.12 | 95.79 | 95.88 | 95.73 | 95.67 | Fronius USA36CL 36.0 Wye [277V]
Fronius USA | CL 44.4 Delta [208V] | Y | N | N | 44.4 kW, 208 Vac Delta Utility Interactive Inverter | 44.4 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.14 |  |  | 230 | 365 | 480 | 4.44 | 8.88 | 13.32 | 22.2 | 33.3 | 44.4 | 92.73 | 94.37 | 94.63 | 94.45 | 93.92 | 92.81 | 94.03 | 93.73 | 94.78 | 95.01 | 95.19 | 94.85 | 94.13 | 94.85 | 92.87 | 94.02 | 94.29 | 94.72 | 94.55 | 94.02 | 94.43 | Fronius USA44.4CL 44.4 Delta [208V]
Fronius USA | CL 44.4 Delta [240V] | Y | N | N | 44.4 kW, 240 Vac Delta Utility Interactive Inverter | 44.4 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.92 |  |  | 230 | 390 | 480 | 4.44 | 8.88 | 13.32 | 22.2 | 33.3 | 44.4 | 93.3 | 94.89 | 95.14 | 95.15 | 94.8 | 93.98 | 94.82 | 93.82 | 95 | 95.26 | 95.61 | 95.46 | 95.06 | 95.36 | 93.25 | 94.4 | 94.67 | 95.2 | 95.14 | 94.94 | 94.97 | Fronius USA44.4CL 44.4 Delta [240V]
Fronius USA | CL 48.0 Wye [277V] | Y | N | N | 48 kW, 277 Vac Wye Utility Interactive Inverter | 48 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.56 |  |  | 240 | 330 | 480 | 4.8 | 9.6 | 14.4 | 24 | 36 | 48 | 94.69 | 95.2 | 95.52 | 95.74 | 95.49 | 94.89 | 95.47 | 94.8 | 95.23 | 95.54 | 96 | 95.91 | 95.52 | 95.79 | 94.4 | 94.97 | 95.17 | 95.82 | 95.92 | 95.72 | 95.69 | Fronius USA48CL 48.0 Wye [277V]
Fronius USA | CL 55.5 Delta [208V] | Y | N | N | 55.5 kW, 208 Vac Delta Utility Interactive Inverter | 55.5 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.43 |  |  | 230 | 365 | 480 | 5.55 | 11.1 | 16.65 | 27.75 | 41.63 | 55.5 | 93.21 | 94.5 | 94.73 | 94.4 | 93.82 | 92.79 | 94.01 | 93.81 | 94.64 | 94.98 | 95.13 | 94.8 | 94.05 | 94.8 | 93.05 | 93.94 | 94.1 | 94.68 | 94.53 | 93.95 | 94.39 | Fronius USA55.5CL 55.5 Delta [208V]
Fronius USA | CL 55.5 Delta [240V] | Y | N | N | 55.5 kW, 240 Vac Delta Utility Interactive Inverter | 55.5 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.32 |  |  | 230 | 390 | 480 | 5.55 | 11.1 | 16.65 | 27.75 | 41.63 | 55.5 | 93.87 | 94.76 | 95.08 | 95.07 | 94.67 | 93.94 | 94.74 | 94 | 94.94 | 95.11 | 95.48 | 95.38 | 94.97 | 95.27 | 93.37 | 93.96 | 94.42 | 95.12 | 95.05 | 94.89 | 94.86 | Fronius USA55.5CL 55.5 Delta [240V]
Fronius USA | CL 60.0 Wye [277V] | Y | N | N | 60 kW, 277 Vac Wye Utility Interactive Inverter | 60 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 5.08 |  |  | 240 | 330 | 480 | 6 | 12 | 18 | 30 | 45 | 60 | 95.12 | 95.2 | 95.58 | 95.75 | 95.48 | 94.86 | 95.49 | 95.12 | 95.22 | 95.6 | 96.02 | 95.91 | 95.51 | 95.81 | 94.65 | 95.04 | 95.2 | 95.84 | 95.92 | 95.73 | 95.71 | Fronius USA60CL 60.0 Wye [277V]
FSP Group | FSP600PV-NA-208 [208V] | Y | N | N | 500W, 208 Vac Utility Interactive Inverter | 0.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.16 |  |  | 27 | 36 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.38 | 0.5 | 93.3 | 94.3 | 94.8 | 94.9 | 94.1 | 93 | 94.3 | 93.4 | 94.1 | 94.8 | 95.4 | 95.1 | 94.3 | 95 | 92.4 | 92.9 | 94.5 | 95.6 | 95.5 | 95.1 | 95.1 | FSP Group0.5FSP600PV-NA-208 [208V] | 2017-05 | 2017-08-15
FSP Group | FSP600PV-NA-240 [240V] | Y | N | N | 500W, 240 Vac Utility Interactive Inverter | 0.5 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.16 |  |  | 27 | 36 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.38 | 0.5 | 93.6 | 94.7 | 95.1 | 95.1 | 94.5 | 93.5 | 94.6 | 94.5 | 94.5 | 95.1 | 95.4 | 95.2 | 94.6 | 95.1 | 94.1 | 94.1 | 94.6 | 95.6 | 95.6 | 95.3 | 95.4 | FSP Group0.5FSP600PV-NA-240 [240V] | 2017-05 | 2017-08-15
FSP Group | FSP600PV-NA-277 [277V] | Y | N | N | 500W, 277 Vac Utility Interactive Inverter | 0.5 | 277 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.22 |  |  | 36 | 40.5 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.38 | 0.5 | 94.5 | 93.8 | 95.1 | 95.4 | 95.4 | 95 | 95.2 | 94.1 | 93.5 | 94.9 | 95.5 | 95.6 | 95.4 | 95.3 | 93.5 | 93.4 | 94.6 | 95.6 | 95.8 | 95.7 | 95.4 | FSP Group0.5FSP600PV-NA-277 [277V] | 2017-05 | 2017-08-15
GAF | RIAC 1000 [208V] | Y | N | N | 300 W, 208 Vac Utility Interactive Inverter | 0.3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.05 |  |  | 30 | 40 | 50 | 30 | 60 | 90 | 150 | 225 | 300 | 91.7 | 94.8 | 95.8 | 96 | 96.1 | 96 | 95.8 | 92 | 94.8 | 95.7 | 96.3 | 96.4 | 96.4 | 96 | 91.6 | 94.7 | 95.6 | 96.3 | 96.4 | 96.5 | 96 | GAF0.3RIAC 1000 [208V]
GAF | RIAC 1000 [240V] | Y | N | N | 300 W, 240 Vac Utility Interactive Inverter | 0.3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.05 |  |  | 30 | 40 | 50 | 30 | 60 | 90 | 150 | 225 | 300 | 91.7 | 94.8 | 95.8 | 96 | 96.1 | 96 | 95.8 | 92 | 94.8 | 95.7 | 96.3 | 96.4 | 96.4 | 96 | 91.6 | 94.7 | 95.6 | 96.3 | 96.4 | 96.5 | 96 | GAF0.3RIAC 1000 [240V]
GE Energy | GEPVe-1100-NA-120 [120V] | Y | N | N | 1100 W, 120 Vac Utility Interactive Inverter with PV System Disconnect | 1.1 | 120 | 90.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 182 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 81.8 | 89 | 90.9 | 92.1 | 92.4 | 92.5 | 91.6 | 79.9 | 88 | 90.1 | 91.7 | 92.2 | 92.3 | 91.1 | 74.8 | 84.7 | 87.8 | 90 | 90.8 | 91.1 | 89.3 | GE Energy1.1GEPVe-1100-NA-120 [120V]
GE Energy | GEPVe-2000-NA-240 [240V] | Y | N | N | 2000 W, 240 Vac Utility Interactive Inverter with PV System Disconnect | 2 | 240 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 199 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.3 | 91.7 | 92.6 | 93.5 | 93.2 | 93 | 92.9 | 85.7 | 90.8 | 92.1 | 92.9 | 92.9 | 92.6 | 92.4 | 82.4 | 88.8 | 90.5 | 91.6 | 91.8 | 91.6 | 91.1 | GE Energy2GEPVe-2000-NA-240 [240V]
GE Energy | GEPVb-2500-NA-240 [240V] | Y | N | N | 2500 W, 240 Vac Utility Interactive Inverter with PV System Disconnect | 2.5 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 2.5 | 1 | 100 | 266 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 88.5 | 92.7 | 94.1 | 94.8 | 94.8 | 94.5 | 94.4 | 87.7 | 92.3 | 93.7 | 94.5 | 94.6 | 94.4 | 94.1 | 86.3 | 90.9 | 92.6 | 93.8 | 94 | 93.8 | 93.3 | GE Energy2.5GEPVb-2500-NA-240 [240V]
GE Energy | GEPVe-2500-NA-240 [240V] | Y | N | N | 2500 W, 240 Vac Utility Interactive Inverter with PV System Disconnect | 2.5 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2 | GE Energy2.5GEPVe-2500-NA-240 [240V]
GE Energy | GEPVb-2800-NA-240/208-02 [208V] | Y | N | N | 2.7 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 2.7 | 208 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 2.7 | 1 | 100 | 266 | 480 | 0.27 | 0.54 | 0.81 | 1.35 | 2.025 | 2.7 | 88.7 | 93.1 | 94.1 | 94.6 | 94.5 | 94 | 94.1 | 88 | 92.8 | 93.8 | 94.4 | 94.3 | 93.8 | 93.9 | 84.6 | 90.6 | 92.3 | 93.4 | 93.4 | 92.5 | 92.7 | GE Energy2.7GEPVb-2800-NA-240/208-02 [208V]
GE Energy | GEPVb-2800-NA-240/208-02 [240V] | Y | N | N | 2.8 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 2.8 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.3 | 2.8 | 1.3 | 100 | 266 | 480 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.3 | 93.5 | 94.4 | 95 | 94.8 | 94.4 | 94.5 | 88.6 | 93.1 | 94.2 | 94.7 | 94.6 | 94.2 | 94.3 | 85.3 | 91 | 92.7 | 93.8 | 93.7 | 92.7 | 93.1 | GE Energy2.8GEPVb-2800-NA-240/208-02 [240V]
GE Energy | GEPVe-2800-NA-208 [208V] | Y | N | N | 2800 W, 208 Vac Utility Interactive Inverter with PV System Disconnect | 2.8 | 208 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.85 |  |  | 100 | 230 | 380 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 81.5 | 89.7 | 91.6 | 92.9 | 93.1 | 93 | 92.2 | 80.8 | 89.3 | 91.3 | 92.7 | 92.9 | 92.8 | 92 | 78.3 | 87.9 | 90.2 | 91.9 | 92.2 | 92.1 | 91.1 | GE Energy2.8GEPVe-2800-NA-208 [208V]
GE Energy | GEPVb-3000-NA-240 [240V] | Y | N | N | 3.0 kW Brilliance - DC Disconnect - Display | 3 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 3 | 1 | 100 | 266 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 90.2 | 93.7 | 94.6 | 95 | 95 | 94.6 | 94.7 | 89.5 | 93.7 | 94.5 | 95 | 95 | 94.6 | 94.6 | 88.7 | 92.6 | 94 | 94.6 | 94.6 | 94.3 | 94.2 | GE Energy3GEPVb-3000-NA-240 [240V]
GE Energy | GEPVe-3000-NA-240 [240V] | Y | N | N | 3000 W, 240 Vac Utility Interactive Inverter with PV System Disconnect | 3 | 240 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.63 |  |  | 100 | 222.5 | 380 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 88.9 | 92.9 | 93.8 | 94.3 | 94.2 | 93.9 | 93.9 | 87.9 | 92.5 | 93.5 | 94.1 | 94 | 93.8 | 93.7 | 84.9 | 90.9 | 92.4 | 93.3 | 93.2 | 93 | 92.7 | GE Energy3GEPVe-3000-NA-240 [240V]
GE Energy | GEPVb-3300-NA-240/208-02 [208V] | Y | N | N | 3.1 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.1 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.24 | 3.1 | 1.24 | 100 | 250 | 400 | 0.31 | 0.62 | 0.93 | 1.55 | 2.325 | 3.1 | 91.4 | 94.7 | 95.4 | 95.6 | 95.5 | 95.1 | 95.3 | 90.9 | 94.4 | 95.2 | 95.6 | 95.4 | 95.1 | 95.2 | 89.3 | 93.4 | 94.5 | 95.2 | 95.2 | 94.9 | 94.7 | GE Energy3.1GEPVb-3300-NA-240/208-02 [208V]
GE Energy | GEPVb-3300-NA-208 [208V] | Y | N | N | 3.3 kW Brilliance - DC Disconnect - Display | 3.3 | 208 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 3.3 | 1 | 100 | 266 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 90.1 | 93.3 | 94.2 | 94.6 | 94.3 | 93.6 | 94.1 | 89.5 | 93.2 | 94.1 | 94.6 | 94.3 | 93.6 | 94.1 | 87.2 | 91.7 | 93.2 | 93.9 | 93.7 | 93.1 | 93.3 | GE Energy3.3GEPVb-3300-NA-208 [208V]
GE Energy | GEPVb-3300-NA-240 [240V] | Y | N | N | 3.3 kW Brilliance - DC Disconnect - Display | 3.3 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 3.3 | 1 | 100 | 266 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 90.6 | 93.8 | 94.9 | 95.3 | 95.1 | 94.6 | 94.9 | 90.1 | 93.7 | 94.6 | 95.1 | 95 | 94.4 | 94.7 | 87.2 | 91.9 | 93.4 | 94.4 | 94.3 | 93.8 | 93.8 | GE Energy3.3GEPVb-3300-NA-240 [240V]
GE Energy | GEPVb-3300-NA-240/208-02 [240V] | Y | N | N | 3.3 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 3.3 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.52 | 3.3 | 1.52 | 100 | 250 | 400 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 91.9 | 95 | 95.7 | 95.9 | 95.9 | 95.5 | 95.6 | 91.4 | 94.7 | 95.5 | 95.9 | 95.7 | 95.4 | 95.5 | 89.8 | 93.6 | 94.8 | 95.4 | 95.3 | 95.2 | 95 | GE Energy3.3GEPVb-3300-NA-240/208-02 [240V]
GE Energy | GEPVe-3500-NA-240 [240V] | Y | N | N | 3500 W, 240 Vac Utility Interactive Inverter with PV System Disconnect | 3.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.86 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5 | GE Energy3.5GEPVe-3500-NA-240 [240V]
GE Energy | GEPVb-3800-NA-240 [240V] | Y | N | N | 3.8 kW Brilliance - DC Disconnect - Display | 3.8 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 3.8 | 1 | 100 | 266 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93 | 95.2 | 95.7 | 95.7 | 95.4 | 94.5 | 95.3 | 92.3 | 95 | 95.5 | 95.6 | 95.3 | 94.6 | 95.2 | 91.2 | 94.2 | 94.8 | 95.1 | 95 | 94.3 | 94.7 | GE Energy3.8GEPVb-3800-NA-240 [240V]
GE Energy | GEPVb-4000-NA-240/208-02 [208V] | Y | N | N | 3.8 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.8 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.99 | 3.8 | 0.99 | 100 | 300 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.7 | 94.8 | 95.5 | 95.7 | 95.4 | 95.1 | 95.3 | 91 | 94.6 | 95.3 | 95.6 | 95.4 | 94.9 | 95.2 | 90.2 | 93.6 | 94.7 | 95.1 | 95.1 | 94.7 | 94.7 | GE Energy3.8GEPVb-4000-NA-240/208-02 [208V]
GE Energy | GEPVb-4000-NA-240/208-02 [240V] | Y | N | N | 4.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 4 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 | 4 | 1.1 | 100 | 300 | 480 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 92.2 | 95.1 | 95.8 | 96 | 95.8 | 95.5 | 95.7 | 91.6 | 94.9 | 95.7 | 95.9 | 95.8 | 95.3 | 95.5 | 90.7 | 94.2 | 95 | 95.5 | 95.4 | 95.1 | 95.1 | GE Energy4GEPVb-4000-NA-240/208-02 [240V]
GE Energy | GEPVb-5000-NA-240/208-02 [208V] | Y | N | N | 5.0 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 4.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 4.5 | 1 | 100 | 300 | 480 | 0.45 | 0.9 | 1.35 | 2.25 | 3.375 | 4.5 | 92.1 | 94.9 | 95.5 | 95.5 | 94.9 | 94.3 | 95 | 91.8 | 94.7 | 95.3 | 95.4 | 94.9 | 94.3 | 94.9 | 90.5 | 93.9 | 94.6 | 95 | 94.7 | 94.2 | 94.5 | GE Energy4.5GEPVb-5000-NA-240/208-02 [208V]
GE Energy | GEPVe-4600-NA-208 [208V] | Y | N | N | 4600 W, 208 Vac Utility Interactive Inverter with PV System Disconnect | 4.6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 | 4.6 | 4 | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95 | GE Energy4.6GEPVe-4600-NA-208 [208V]
GE Energy | GEPVe-4800-NA-240 [240V] | Y | N | N | 4800 W, 240 Vac Utility Interactive Inverter with PV System Disconnect | 4.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.1 |  |  | 100 | 263 | 400 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 86.8 | 93.5 | 95.5 | 97 | 97.2 | 97.1 | 96.4 | 85.5 | 92.9 | 95 | 96.7 | 96.9 | 96.8 | 96 | 84.5 | 91.5 | 93.9 | 95.9 | 96.2 | 96.1 | 95.1 | GE Energy4.8GEPVe-4800-NA-240 [240V]
GE Energy | GEPVb-5000-NA-240/208-02 [240V] | Y | N | N | 5.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 5 | 1 | 100 | 300 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.2 | 95.5 | 95.9 | 95.9 | 95.5 | 94.8 | 95.5 | 92.7 | 95.3 | 95.8 | 95.8 | 95.4 | 94.8 | 95.4 | 91.5 | 94.6 | 95.3 | 95.4 | 95.1 | 94.5 | 95 | GE Energy5GEPVb-5000-NA-240/208-02 [240V]
GE Energy | GEPVb-5000-NA-240-01 [240V] | Y | N | N | 5.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 5 | 1 | 100 | 300 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.6 | 95.7 | 96 | 96.1 | 95.5 | 94.8 | 95.6 | 93.2 | 95.6 | 95.9 | 95.9 | 95.5 | 94.8 | 95.5 | 92.3 | 94.8 | 95.5 | 95.6 | 95.2 | 94.6 | 95.2 | GE Energy5GEPVb-5000-NA-240-01 [240V]
GE Energy | GEPVe-5200-NA-240 [240V] | Y | N | N | 5200 W, 240 Vac Utility Interactive Inverter with PV System Disconnect | 5.2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 | 5.2 | 4 | 100 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5 | GE Energy5.2GEPVe-5200-NA-240 [240V]
Gefran | APV 1700-2M-TL-US [208V] | Y | N | N | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.5 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 330 | 360 | 0.15 | 0.3 | 0.45 | 0.75 | 1.125 | 1.5 | 91.07 | 94.89 | 95.98 | 96.37 | 96.19 | 96.01 | 95.92 | 91.74 | 95.48 | 96.48 | 96.85 | 96.7 | 96.5 | 96.43 | 91.45 | 95.19 | 96.25 | 96.74 | 96.65 | 96.46 | 96.33 | Gefran1.5APV 1700-2M-TL-US [208V]
Gefran | APV 1700-2M-TL-US [240V] | Y | N | N | 1.65 kW, 240 Vac Utility Interactive Inverter | 1.65 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 |  |  | 100 | 330 | 360 | 0.165 | 0.33 | 0.495 | 0.825 | 1.238 | 1.65 | 89.51 | 94.23 | 95.46 | 96.29 | 96.25 | 96.03 | 95.78 | 90.24 | 94.71 | 95.95 | 96.58 | 96.64 | 96.51 | 96.19 | 91.3 | 95.36 | 96.46 | 97.02 | 96.99 | 96.82 | 96.62 | Gefran1.65APV 1700-2M-TL-US [240V]
Gefran | APV 1700-2M-TL-US [277V] | Y | N | N | 1.65 kW, 277 Vac Utility Interactive Inverter | 1.65 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.13 |  |  | 100 | 330 | 360 | 0.165 | 0.33 | 0.495 | 0.825 | 1.238 | 1.65 | 89.17 | 93.51 | 95.04 | 96.07 | 96.22 | 96.15 | 95.63 | 89.3 | 94.02 | 95.58 | 96.43 | 96.61 | 96.65 | 96.03 | 89.26 | 94.34 | 95.7 | 96.59 | 96.77 | 96.78 | 96.18 | Gefran1.65APV 1700-2M-TL-US [277V]
Gefran | APV 2300-2M-TL-US [208V] | Y | N | N | 1.8 kW, 208 Vac Utility Interactive Inverter | 1.8 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.09 |  |  | 100 | 360 | 400 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 92.27 | 95.4 | 95.99 | 96.41 | 96.32 | 96.02 | 96.08 | 92.84 | 95.99 | 96.57 | 96.79 | 96.62 | 96.44 | 96.46 | 92.68 | 95.67 | 96.26 | 96.6 | 96.48 | 96.33 | 96.28 | Gefran1.8APV 2300-2M-TL-US [208V]
Gefran | APV 2300-2M-TL-US [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter | 2 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 100 | 360 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.42 | 94.6 | 95.68 | 96.3 | 96.38 | 96.07 | 95.98 | 92.9 | 96.12 | 96.85 | 97.12 | 97.11 | 96.87 | 96.85 | 92.27 | 95.76 | 96.57 | 96.93 | 96.97 | 96.82 | 96.66 | Gefran2APV 2300-2M-TL-US [240V]
Gefran | APV 2300-2M-TL-US [277V] | Y | N | N | 2 kW, 277 Vac Utility Interactive Inverter | 2 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 360 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89.3 | 93.72 | 95.09 | 96.02 | 96.31 | 96.13 | 95.68 | 91.06 | 94.84 | 95.88 | 96.54 | 96.85 | 96.78 | 96.33 | 92.92 | 96.05 | 96.89 | 97.32 | 97.43 | 97.31 | 97.09 | Gefran2APV 2300-2M-TL-US [277V]
Gefran | APV 3100-2M-TL-US [208V] | Y | N | N | 2.5 kW, 208 Vac Utility Interactive Inverter | 2.5 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 100 | 360 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.875 | 2.5 | 92.33 | 95.42 | 96.2 | 96.47 | 96.18 | 95.79 | 96.03 | 93.86 | 96.24 | 96.83 | 97.02 | 96.76 | 96.38 | 96.66 | 92.7 | 95.78 | 96.5 | 96.82 | 96.64 | 96.3 | 96.44 | Gefran2.5APV 3100-2M-TL-US [208V]
Gefran | APV 3100-2M-TL-US [240V] | Y | N | N | 2.8 kW, 240 Vac Utility Interactive Inverter | 2.8 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 |  |  | 100 | 360 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 90.95 | 94.37 | 95.55 | 96.42 | 96.44 | 96.11 | 95.99 | 93.99 | 96.56 | 97.1 | 97.54 | 97.41 | 97.03 | 97.2 | 93.25 | 96.15 | 96.83 | 97.38 | 97.27 | 96.98 | 97.01 | Gefran2.8APV 3100-2M-TL-US [240V] |  | 2018-03-15
Gefran | APV 3100-2M-TL-US [277V] | Y | N | N | 2.8 kW, 277 Vac Utility Interactive Inverter | 2.8 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.19 |  |  | 100 | 360 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.39 | 93.38 | 94.83 | 95.93 | 96.17 | 96.03 | 95.54 | 91.61 | 95.23 | 96.26 | 96.9 | 96.98 | 96.79 | 96.56 | 94.07 | 96.64 | 97.32 | 97.65 | 97.64 | 97.41 | 97.4 | Gefran2.8APV 3100-2M-TL-US [277V]
Gefran | APV 3800-2M-TL-US [208V] | Y | N | N | 3.6 kW, 208 Vac Utility Interactive Inverter | 3.6 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.23 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.95 | 94.55 | 95.5 | 96.38 | 96.5 | 96.35 | 96.07 | 94.47 | 96.66 | 97.32 | 97.56 | 97.44 | 97.18 | 97.28 | 93.04 | 96.01 | 96.85 | 97.31 | 97.29 | 97.09 | 97 | Gefran3.6APV 3800-2M-TL-US [208V]
Gefran | APV 3800-2M-TL-US [240V] | Y | N | N | 3.6 kW, 240 Vac Utility Interactive Inverter | 3.6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.31 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.36 | 94.62 | 95.52 | 96.5 | 96.72 | 96.66 | 96.25 | 95.3 | 97.14 | 97.54 | 97.79 | 97.75 | 97.54 | 97.59 | 94.21 | 96.53 | 97.06 | 97.5 | 97.57 | 97.44 | 97.3 | Gefran3.6APV 3800-2M-TL-US [240V]
Gefran | APV 3800-2M-TL-US [277V] | Y | N | N | 3.6 kW, 277 Vac Utility Interactive Inverter | 3.6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.24 | 93.86 | 94.75 | 96.11 | 96.57 | 96.63 | 95.91 | 93.37 | 96.01 | 96.64 | 97.42 | 97.53 | 97.48 | 97.15 | 94.54 | 96.85 | 97.37 | 97.89 | 97.97 | 97.87 | 97.68 | Gefran3.6APV 3800-2M-TL-US [277V]
Gefran | APV 4400-2M-TL-US [208V] | Y | N | N | 4.2 kW, 208 Vac Utility Interactive Inverter | 4.2 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.58 | 94.43 | 95.52 | 96.63 | 96.81 | 96.73 | 96.29 | 94.13 | 96.46 | 97.09 | 97.28 | 97.07 | 96.73 | 96.95 | 93.57 | 96.16 | 96.78 | 97.22 | 97.46 | 97.15 | 97.09 | Gefran4.2APV 4400-2M-TL-US [208V]
Gefran | APV 4400-2M-TL-US [240V] | Y | N | N | 4.2 kW, 240 Vac Utility Interactive Inverter | 4.2 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.33 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.36 | 94.62 | 95.52 | 96.5 | 96.72 | 96.66 | 96.25 | 95.3 | 97.14 | 97.54 | 97.79 | 97.75 | 97.54 | 97.59 | 94.21 | 96.53 | 97.06 | 97.5 | 97.57 | 97.44 | 97.3 | Gefran4.2APV 4400-2M-TL-US [240V]
Gefran | APV 4400-2M-TL-US [277V] | Y | N | N | 4.2 kW, 277 Vac Utility Interactive Inverter | 4.2 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.38 | 94.39 | 96.04 | 96.56 | 96.84 | 96.56 | 96.33 | 92.15 | 95.2 | 96.3 | 97.27 | 97.57 | 97.13 | 97 | 93.64 | 96.31 | 97.2 | 97.62 | 97.64 | 97.61 | 97.36 | Gefran4.2APV 4400-2M-TL-US [277V]
Gefran | APV 5200-2M-TL-US [208V] | Y | N | N | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.65 | 96.46 | 96.83 | 96.95 | 96.5 | 96.03 | 96.54 | 95.44 | 97.01 | 97.33 | 97.37 | 97 | 96.5 | 97.03 | 94.29 | 96.39 | 96.89 | 97.14 | 96.96 | 96.47 | 96.83 | Gefran4.6APV 5200-2M-TL-US [208V]
Gefran | APV 5200-2M-TL-US [240V] | Y | N | N | 4.6 kW, 240 Vac Utility Interactive Inverter | 4.6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.79 | 95.19 | 96.01 | 96.67 | 96.65 | 96.4 | 96.34 | 95.85 | 97.33 | 97.67 | 97.76 | 97.48 | 97.08 | 97.47 | 96.66 | 96.66 | 97.2 | 97.53 | 97.37 | 97.08 | 97.3 | Gefran4.6APV 5200-2M-TL-US [240V]
Gefran | APV 5200-2M-TL-US [277V] | Y | N | N | 4.6 kW, 277 Vac Utility Interactive Inverter | 4.6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.43 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.24 | 94.93 | 95.62 | 96.64 | 96.82 | 96.76 | 96.36 | 94.63 | 96.69 | 97.2 | 97.63 | 97.57 | 97.41 | 97.37 | 95.39 | 97.11 | 97.55 | 97.86 | 97.82 | 97.65 | 97.66 | Gefran4.6APV 5200-2M-TL-US [277V]
General Electric | PVIA2000NA1240 [240V] | Y | N | N | 2110 W, 240 Vac Utility Interactive Inverter | 2.11 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.21 | 0.42 | 0.63 | 1.06 | 1.58 | 2.11 | 85.3 | 91.6 | 92.9 | 94.3 | 94.6 | 94.5 | 93.8 | 82.1 | 91.9 | 94.2 | 95.6 | 96.1 | 96.4 | 95 | 82.2 | 91.5 | 93.8 | 95.6 | 96.1 | 96.3 | 95 | General Electric2.11PVIA2000NA1240 [240V]
General Electric | PVIA3000NA1240 [240V] | Y | N | N | 3180 W, 240 Vac Utility Interactive Inverter | 3.18 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.32 | 0.64 | 0.95 | 1.59 | 2.39 | 3.18 | 88.8 | 92.9 | 94.1 | 94.6 | 94.3 | 94 | 94 | 88.8 | 94.4 | 95.3 | 96.2 | 96.3 | 95.9 | 95.7 | 89.5 | 93.7 | 95.3 | 96.2 | 96.3 | 96.1 | 95.7 | General Electric3.18PVIA3000NA1240 [240V]
General Electric | PVIA4000NA1240 [240V] | Y | N | N | 4160 W, 240 Vac Utility Interactive Inverter | 4.16 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.42 | 0.83 | 1.25 | 2.08 | 3.12 | 4.16 | 90.6 | 93.8 | 94.5 | 94.8 | 94.6 | 94.2 | 94.4 | 91.4 | 95 | 95.7 | 96.1 | 96.2 | 95.9 | 95.9 | 90.7 | 94.7 | 95.5 | 96.1 | 96.1 | 95.9 | 95.7 | General Electric4.16PVIA4000NA1240 [240V]
General Electric | PVIA5000NA1240 [240V] | Y | N | N | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8 | General Electric5.24PVIA5000NA1240 [240V]
Geoprotek Technology | GS-1000 [208V] | Y | N | N | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.16 | 0.31 | 0.47 | 0.78 | 1.16 | 1.55 | 84.5 | 90.5 | 92.5 | 94.3 | 94.9 | 95 | 93.9 | 85 | 91 | 93.2 | 94.8 | 95.4 | 95.5 | 94.4 | 85.3 | 91.2 | 93.5 | 95 | 95.6 | 95.8 | 94.6 | Geoprotek Technology1.55GS-1000 [208V]
Geoprotek Technology | GS-1000 [240V] | Y | N | N | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.16 | 0.31 | 0.47 | 0.78 | 1.16 | 1.55 | 84.6 | 90.5 | 92.6 | 94.4 | 95.1 | 95.3 | 94 | 84.9 | 91 | 93 | 94.8 | 95.5 | 95.7 | 94.4 | 85.2 | 91.4 | 93.4 | 95.1 | 95.7 | 95.9 | 94.7 | Geoprotek Technology1.55GS-1000 [240V]
Geoprotek Technology | GS-1500 [208V] | Y | N | N | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.16 | 0.31 | 0.47 | 0.78 | 1.16 | 1.55 | 84.5 | 90.5 | 92.5 | 94.3 | 94.9 | 95 | 93.9 | 85 | 91 | 93.2 | 94.8 | 95.4 | 95.5 | 94.4 | 85.3 | 91.2 | 93.5 | 95 | 95.6 | 95.8 | 94.6 | Geoprotek Technology1.55GS-1500 [208V]
Geoprotek Technology | GS-1500 [240V] | Y | N | N | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.16 | 0.31 | 0.47 | 0.78 | 1.16 | 1.55 | 84.6 | 90.5 | 92.6 | 94.4 | 95.1 | 95.3 | 94 | 84.9 | 91 | 93 | 94.8 | 95.5 | 95.7 | 94.4 | 85.2 | 91.4 | 93.4 | 95.1 | 95.7 | 95.9 | 94.7 | Geoprotek Technology1.55GS-1500 [240V]
Geoprotek Technology | GS-2000 [208V] | Y | N | N | 2 kW, 208 Vac Utility Interactive Inverter | 2.06 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.29 |  |  | 100 | 325 | 360 | 0.21 | 0.41 | 0.62 | 1.03 | 1.55 | 2.06 | 88.3 | 93.1 | 94.4 | 95.3 | 95.4 | 95.4 | 94.9 | 89.6 | 93.7 | 94.9 | 95.7 | 95.8 | 95.8 | 95.3 | 89.7 | 94 | 95.1 | 96.1 | 96.4 | 96.1 | 95.8 | Geoprotek Technology2.06GS-2000 [208V]
Geoprotek Technology | GS-2000 [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter | 2.06 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 325 | 360 | 0.21 | 0.41 | 0.62 | 1.03 | 1.55 | 2.06 | 86.9 | 92.1 | 93.8 | 94.9 | 95.3 | 95.4 | 94.6 | 87.8 | 92.9 | 94.3 | 95.6 | 95.8 | 95.7 | 95.1 | 88.1 | 93.1 | 94.4 | 95.7 | 96 | 95.9 | 95.3 | Geoprotek Technology2.06GS-2000 [240V]
Geoprotek Technology | GS-3000 [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.6 | 94.4 | 95.2 | 95.5 | 95.3 | 94.6 | 95.1 | 92.1 | 94.9 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 92.2 | 95.2 | 95.8 | 96.2 | 95.9 | 95.8 | 95.8 | Geoprotek Technology3GS-3000 [208V]
Geoprotek Technology | GS-3000 [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 90 | 93.9 | 94.9 | 95.4 | 95.3 | 94.8 | 95 | 90.6 | 94.3 | 95.3 | 95.8 | 95.9 | 95.6 | 95.5 | 91 | 94.6 | 95.4 | 96 | 96 | 95.8 | 95.7 | Geoprotek Technology3.01GS-3000 [240V]
Green Power Technologies | PV500U + MVT | Y | N | N | 500 kW, 3-phase, Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 500 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 140.4 |  |  | 325 | 395 | 600 | 50 | 100 | 150 | 250 | 375 | 500 | 94.5 | 96.4 | 96.8 | 96.6 | 96.3 | 95.7 | 96.3 | 93.7 | 95.9 | 96.5 | 96.5 | 96.1 | 95.5 | 96.1 | 91.8 | 94.9 | 95.7 | 95.9 | 95.6 | 95.1 | 95.5 | Green Power Technologies500PV500U + MVT
Green Power Technologies | PV500WD | Y | N | N | Photovoltaic Inverter | 600 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 154.4 |  |  | 395 | 503 | 825 | 60 | 12 | 180 | 300 | 450 | 600 | 95.5 | 96.9 | 97.1 | 97 | 96.5 | 96 | 96.6 | 95.1 | 96.6 | 96.9 | 96.6 | 96.2 | 95.6 | 96.3 | 94 | 95.7 | 96.2 | 96.1 | 95.6 | 95.1 | 95.7 | Green Power Technologies600PV500WD
Green Power Technologies | PV630WD | Y | N | N | Photovoltaic Inverter | 750 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 155.7 |  |  | 495 | 578 | 825 | 75 | 150 | 225 | 375 | 563 | 750 | 95.5 | 97 | 97.3 | 97.1 | 96.7 | 96.2 | 96.8 | 95.1 | 96.8 | 97 | 97 | 96.5 | 95.9 | 96.6 | 94.5 | 96.2 | 96.7 | 96.7 | 96.2 | 95.6 | 96.2 | Green Power Technologies750PV630WD
Green Power Technologies | PV750WD | Y | N | N | Photovoltaic Inverter | 890 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 154.1 |  |  | 585 | 646 | 825 | 89 | 178 | 267 | 445 | 667.5 | 890 | 95.8 | 97.2 | 97.4 | 97.3 | 96.8 | 96.3 | 96.9 | 95.3 | 96.9 | 97.2 | 97.1 | 96.7 | 96.2 | 96.8 | 95.1 | 96.8 | 97 | 97 | 96.5 | 95.9 | 96.6 | Green Power Technologies890PV750WD
Green Power Technologies | 940WD3-LV400 [400V] | Y | N | N | 933 kW, 400 Vac Utility Interactive Inverter | 935.55 | 400 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Efficiency data inclusive of transformer effect based on 1500 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 274.29 |  |  | 593 | 682 | 880 | 93.56 | 187.11 | 280.67 | 467.78 | 701.66 | 935.55 | 96.07 | 97.25 | 97.52 | 97.52 | 97.2 | 96.72 | 97.24 | 95.86 | 97.18 | 97.48 | 97.48 | 97.11 | 96.55 | 97.16 | 95.21 | 96.8 | 97.2 | 97.27 | 96.94 | 96.4 | 96.94 | Green Power Technologies935.55940WD3-LV400 [400V] | 2017-04-01 | 2018-06-01
Green Power Technologies | PV900WD | Y | N | N | Photovoltaic Inverter | 1080 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 155.7 |  |  | 705 | 736 | 825 | 108 | 216 | 324 | 540 | 810 | 1080 | 95.7 | 97.2 | 97.5 | 97.4 | 97 | 96.5 | 97.1 | 95.6 | 97.1 | 97.4 | 97.4 | 97 | 96.4 | 97 | 95.4 | 97 | 97.3 | 97.3 | 96.9 | 96.3 | 96.9 | Green Power Technologies1080PV900WD
Green Power Technologies | 1170WD3-LV500 [500V] | Y | N | N | 1135 kW, 500 Vac Utility Interactive Inverter | 1135.968 | 500 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Efficiency data inclusive of transformer effect based on 2000 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 269.45 |  |  | 741 | 793 | 880 | 113.6 | 227.19 | 340.79 | 567.98 | 851.98 | 1136 | 96.3243 | 97.4929 | 97.7506 | 97.7916 | 97.5104 | 97.093 | 97.5291 | 96.1979 | 97.4382 | 97.7225 | 97.7484 | 97.4418 | 96.9627 | 97.466 | 95.9161 | 97.2976 | 97.6014 | 97.6776 | 97.3821 | 96.9105 | 97.384 | Green Power Technologies1135.9681170WD3-LV500 [500V] | 2017-04-01 | 2018-06-01
Green Power Technologies | 1140WD3-HV560 [560V] | Y | N | N | 1130 kW, 560 Vac Utility Interactive Inverter | 1154.944 | 560 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Efficiency data inclusive of transformer effect based on 2000 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 279.91 |  |  | 801 | 913 | 1200 | 115.49 | 230.99 | 346.48 | 577.47 | 866.21 | 1154.9 | 96.2 | 97.56 | 97.89 | 98.03 | 97.84 | 97.49 | 97.79 | 95.7 | 97.27 | 97.65 | 97.81 | 97.6 | 97.2 | 97.54 | 94.73 | 96.69 | 97.22 | 97.51 | 97.33 | 96.97 | 97.2 | Green Power Technologies1154.9441140WD3-HV560 [560V] | 2017-04-01 | 2018-06-01
Green Power Technologies | 1260WD3-HV620 [620V] | Y | N | N | 1205 kW, 620 Vac Utility Interactive Inverter | 1205.298 | 620 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Efficiency data inclusive of transformer effect based on 2000 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 263.99 |  |  | 887 | 978 | 1200 | 120.53 | 241.06 | 361.59 | 602.65 | 903.97 | 1205.3 | 96.11 | 97.53 | 97.85 | 98 | 97.87 | 97.51 | 97.79 | 95.73 | 97.35 | 97.71 | 97.87 | 97.71 | 97.34 | 97.63 | 94.98 | 96.91 | 97.38 | 97.65 | 97.51 | 97.16 | 97.37 | Green Power Technologies1205.2981260WD3-HV620 [620V] | 2017-04-01 | 2018-06-01
Green Power Technologies | 1400WD3-HV690 [690V] | Y | N | N | 1350 kW, 690 Vac Utility Interactive Inverter | 1350.426 | 690 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Efficiency data inclusive of transformer effect based on 2500 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 275.89 |  |  | 987 | 1053 | 1200 | 135.04 | 270.09 | 405.13 | 675.21 | 1012.82 | 1350.4 | 96.17 | 97.67 | 98 | 98.16 | 98.05 | 97.71 | 97.95 | 95.8 | 97.46 | 97.81 | 97.97 | 97.81 | 97.48 | 97.73 | 95.2 | 97.18 | 97.6 | 97.83 | 97.7 | 97.37 | 97.57 | Green Power Technologies1350.4261400WD3-HV690 [690V] | 2017-04-01 | 2018-06-01
GreenVolts | GV-SCP001 [480V] | Y | N | N | 16 kW, 480 Vac Utility Interactive Inverter | 16 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 85 |  |  | 760 | 810 | 960 | 1.6 | 3.2 | 4.8 | 8 | 12 | 16 | 93 | 95.7 | 96.4 | 96.8 | 96.7 | 96.5 | 96.5 | 92.8 | 95.4 | 96.2 | 96.5 | 96.6 | 96.4 | 96.3 | 92.2 | 94.9 | 95.9 | 96.3 | 96.3 | 96.1 | 96 | GreenVolts16GV-SCP001 [480V]
GridPoint | Connect C36 | Y | N | N | 3600 W, 48 Vdc Utility Interactive with battery backup | 3.037 |  | 91 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0 |  |  | 40 | 51.2 | 60 | 0.3037 | 0.6075 | 0.9112 | 1.519 | 2.278 | 3.037 | 88 | 92.2 | 93.2 | 94 | 93 | 91.3 | 92.9 | 82.1 | 88.5 | 90.7 | 91.8 | 91.6 | 89.7 | 90.9 | 80.4 | 86.1 | 87.9 | 90.3 | 90.5 | 88.4 | 89.4 | GridPoint3.037Connect C36
Growatt New Energy Technology Co., Ltd. | Growatt 1500-US [208V] | Y | N | N | 1500 W 208 Vac Utility Interactive Inverter | 1.5 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 330 | 360 | 0.15 | 0.3 | 0.45 | 0.75 | 1.13 | 1.5 | 91.1 | 94.9 | 96 | 96.4 | 96.2 | 96 | 95.9 | 91.7 | 95.5 | 96.5 | 96.8 | 96.7 | 96.5 | 96.4 | 91.5 | 95.2 | 96.2 | 96.7 | 96.7 | 96.5 | 96.3 | Growatt New Energy Technology Co., Ltd.1.5Growatt 1500-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 1500-US [240V] | Y | N | N | 1650 W 240 Vac Utility Interactive Inverter | 1.65 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 |  |  | 100 | 330 | 360 | 0.17 | 0.33 | 0.5 | 0.83 | 1.24 | 1.65 | 89.5 | 94.2 | 95.5 | 96.3 | 96.3 | 96 | 95.8 | 90.2 | 94.7 | 95.9 | 96.6 | 96.6 | 96.5 | 96.2 | 91.3 | 95.4 | 96.5 | 97 | 97 | 96.8 | 96.6 | Growatt New Energy Technology Co., Ltd.1.65Growatt 1500-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 1500-US [277V] | Y | N | N | 1650 W 277 Vac Utility Interactive Inverter | 1.65 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.13 |  |  | 100 | 330 | 360 | 0.17 | 0.33 | 0.5 | 0.83 | 1.24 | 1.65 | 89.2 | 93.5 | 95 | 96.1 | 96.2 | 96.1 | 95.6 | 89.3 | 94 | 95.6 | 96.4 | 96.6 | 96.7 | 96 | 89.3 | 94.3 | 95.7 | 96.6 | 96.8 | 96.8 | 96.2 | Growatt New Energy Technology Co., Ltd.1.65Growatt 1500-US [277V]
Growatt New Energy Technology Co., Ltd. | Growatt 2000-US [208V] | Y | N | N | 1800 W 208 Vac Utility Interactive Inverter | 1.8 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.09 |  |  | 100 | 360 | 400 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 92.3 | 95.4 | 96 | 96.4 | 96.3 | 96 | 96.1 | 92.8 | 96 | 96.6 | 96.8 | 96.6 | 96.4 | 96.5 | 92.7 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | Growatt New Energy Technology Co., Ltd.1.8Growatt 2000-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 2000HF-US [208V] | Y | N | N | 2000 W 208 Vac Utility Interactive Inverter | 2 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 100 | 360 | 450 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.8 | 93 | 94.9 | 95.6 | 95.3 | 95 | 95 | 91.4 | 94.4 | 95.6 | 96.4 | 96.2 | 95.7 | 95.8 | 90.2 | 93.5 | 95 | 95.8 | 95.7 | 95.3 | 95.3 | Growatt New Energy Technology Co., Ltd.2Growatt 2000HF-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 2000HF-US [240V] | Y | N | N | 2000 W 240 Vac Utility Interactive Inverter | 2 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.12 |  |  | 100 | 360 | 450 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.1 | 92.5 | 94.5 | 95.9 | 95.8 | 95.3 | 95.2 | 91.3 | 94 | 95.7 | 96.6 | 96.4 | 95.8 | 96 | 89.4 | 92.4 | 95 | 96.1 | 96 | 95.4 | 95.4 | Growatt New Energy Technology Co., Ltd.2Growatt 2000HF-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 2000-US [240V] | Y | N | N | 2000 W 240 Vac Utility Interactive Inverter | 2 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 100 | 360 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 91.4 | 94.6 | 95.7 | 96.3 | 96.4 | 96.1 | 96 | 92.9 | 96.1 | 96.8 | 97.1 | 97.1 | 96.9 | 96.9 | 92.3 | 95.8 | 96.6 | 96.9 | 97 | 96.8 | 96.7 | Growatt New Energy Technology Co., Ltd.2Growatt 2000-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 2000-US [277V] | Y | N | N | 2000 W 277 Vac Utility Interactive Inverter | 2 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 360 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89.3 | 93.7 | 95.1 | 96 | 96.3 | 96.1 | 95.7 | 91.1 | 94.8 | 95.9 | 96.5 | 96.8 | 96.8 | 96.3 | 92.9 | 96.1 | 96.9 | 97.3 | 97.4 | 97.3 | 97.1 | Growatt New Energy Technology Co., Ltd.2Growatt 2000-US [277V]
Growatt New Energy Technology Co., Ltd. | Growatt 2500HF-US [208V] | Y | N | N | 2500 W 208 Vac Utility Interactive Inverter | 2.5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 100 | 360 | 450 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 90.2 | 93.3 | 94.6 | 95.4 | 95.4 | 95 | 95 | 91.8 | 94.3 | 95.6 | 96.2 | 96 | 95.6 | 95.7 | 90.7 | 93.7 | 94.9 | 95.8 | 95.6 | 95.2 | 95.3 | Growatt New Energy Technology Co., Ltd.2.5Growatt 2500HF-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 2500HF-US [240V] | Y | N | N | 2500 W 240 Vac Utility Interactive Inverter | 2.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.13 |  |  | 100 | 360 | 450 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 90.2 | 93 | 94.5 | 95.6 | 95.4 | 95 | 95 | 91.4 | 94.1 | 95.7 | 96.3 | 96 | 95.7 | 95.8 | 90.8 | 93.2 | 95 | 95.8 | 95.7 | 95.5 | 95.3 | Growatt New Energy Technology Co., Ltd.2.5Growatt 2500HF-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 3000-US [208V] | Y | N | N | 2500 W 208 Vac Utility Interactive Inverter | 2.5 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 100 | 360 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 92.3 | 95.4 | 96.2 | 96.5 | 96.2 | 95.8 | 96 | 93.9 | 96.2 | 96.8 | 97 | 96.8 | 96.4 | 96.7 | 92.7 | 95.8 | 96.5 | 96.8 | 96.6 | 96.3 | 96.4 | Growatt New Energy Technology Co., Ltd.2.5Growatt 3000-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 3000-US [240V] | Y | N | N | 3000 W 240 Vac Utility Interactive Inverter | 2.8 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 |  |  | 100 | 360 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 91 | 94.4 | 95.6 | 96.4 | 96.4 | 96.1 | 96 | 94 | 96.6 | 97.1 | 97.5 | 97.4 | 97 | 97.2 | 93.3 | 96.1 | 96.8 | 97.4 | 97.3 | 97 | 97 | Growatt New Energy Technology Co., Ltd.2.8Growatt 3000-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 3000-US [277V] | Y | N | N | 3000 W 277 Vac Utility Interactive Inverter | 2.8 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.19 |  |  | 100 | 360 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.4 | 93.4 | 94.8 | 95.9 | 96.2 | 96 | 95.5 | 91.6 | 95.2 | 96.3 | 96.9 | 97 | 96.8 | 96.6 | 94.1 | 96.6 | 97.3 | 97.7 | 97.6 | 97.4 | 97.4 | Growatt New Energy Technology Co., Ltd.2.8Growatt 3000-US [277V]
Growatt New Energy Technology Co., Ltd. | Growatt 3000HF-US [208V] | Y | N | N | 3000 W 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 100 | 360 | 450 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 90.5 | 93.5 | 95.1 | 95.5 | 95.2 | 95.1 | 95 | 91.2 | 94.2 | 95.5 | 96.2 | 95.9 | 95.6 | 95.6 | 90.2 | 93.5 | 95 | 95.9 | 95.7 | 95.4 | 95.3 | Growatt New Energy Technology Co., Ltd.3Growatt 3000HF-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 3000HF-US [240V] | Y | N | N | 3000 W 240 Vac Utility Interactive Inverter | 3 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 360 | 450 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 89.4 | 93.1 | 94.8 | 95.6 | 95.4 | 94.9 | 95 | 91.1 | 94.2 | 95.7 | 96.4 | 96 | 95.5 | 95.8 | 90.4 | 93.6 | 95.2 | 96.1 | 95.7 | 95.4 | 95.4 | Growatt New Energy Technology Co., Ltd.3Growatt 3000HF-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 3600 MTL-US [208V] | Y | N | N | 3600W 208 Vac Utility Interactive Inverter | 3.6 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.3 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.9 | 94.6 | 95.5 | 96.4 | 96.5 | 96.3 | 96.1 | 94.5 | 96.7 | 97.3 | 97.6 | 97.4 | 97.2 | 97.3 | 93 | 96 | 96.9 | 97.3 | 97.3 | 97.1 | 97 | Growatt New Energy Technology Co., Ltd.3.6Growatt 3600 MTL-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 3600 MTL-US [240V] | Y | N | N | 3600W 240 Vac Utility Interactive Inverter | 3.6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.31 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.4 | 94.6 | 95.5 | 96.5 | 96.7 | 96.7 | 96.2 | 95.3 | 97.1 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | 94.2 | 96.5 | 97.1 | 97.5 | 97.6 | 97.4 | 97.3 | Growatt New Energy Technology Co., Ltd.3.6Growatt 3600 MTL-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 3600 MTL-US [277V] | Y | N | N | 3600W 277 Vac Utility Interactive Inverter | 3.6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.2 | 93.9 | 94.7 | 96.1 | 96.6 | 96.6 | 95.9 | 93.4 | 96 | 96.6 | 97.4 | 97.5 | 97.5 | 97.2 | 94.5 | 96.8 | 97.4 | 97.9 | 98 | 97.9 | 97.7 | Growatt New Energy Technology Co., Ltd.3.6Growatt 3600 MTL-US [277V]
Growatt New Energy Technology Co., Ltd. | Growatt 4000MTLP-US [208V] | Y | N | N | 4000 W 208 Vac Utility Interactive Inverter | 3.62 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.36 | 0.72 | 1.08 | 1.81 | 2.71 | 3.62 | 88.8 | 91.7 | 93.1 | 94.6 | 95.2 | 95.2 | 94.4 | 92.2 | 95.7 | 95.7 | 96.5 | 96.7 | 96.7 | 96.3 | 91.4 | 94.3 | 95.3 | 96.2 | 96.5 | 96.6 | 96 | Growatt New Energy Technology Co., Ltd.3.62Growatt 4000MTLP-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 4000MTLP-US [240V] | Y | N | N | 4000 W 240 Vac Utility Interactive Inverter | 4.05 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.4 | 0.81 | 1.21 | 2.02 | 3.04 | 4.05 | 89.5 | 92.1 | 93.7 | 95 | 95.5 | 95.6 | 94.8 | 93.1 | 95.4 | 96.2 | 96.9 | 97.1 | 97.1 | 96.7 | 92.3 | 94.8 | 95.9 | 96.6 | 96.9 | 97 | 96.4 | Growatt New Energy Technology Co., Ltd.4.05Growatt 4000MTLP-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 4000MTLP-US [277V] | Y | N | N | 4000 W 277 Vac Utility Interactive Inverter | 4.06 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.41 | 0.81 | 1.22 | 2.03 | 3.04 | 4.06 | 88.3 | 91.5 | 93.1 | 94.6 | 95.3 | 95.5 | 94.4 | 93.6 | 95.7 | 96.6 | 95.3 | 97.4 | 97.4 | 96.6 | 92.7 | 95.1 | 96.3 | 96.9 | 97.2 | 97.3 | 96.8 | Growatt New Energy Technology Co., Ltd.4.06Growatt 4000MTLP-US [277V]
Growatt New Energy Technology Co., Ltd. | Growatt 4200 MTL-US [208V] | Y | N | N | 4200W 208 Vac Utility Interactive Inverter | 4.2 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.6 | 94.4 | 95.5 | 96.6 | 96.8 | 96.7 | 96.3 | 94.1 | 96.5 | 97.1 | 97.3 | 97.1 | 96.7 | 97 | 93.6 | 96.2 | 96.8 | 97.2 | 97.5 | 97.1 | 97.1 | Growatt New Energy Technology Co., Ltd.4.2Growatt 4200 MTL-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 4200 MTL-US [240V] | Y | N | N | 4200W 240 Vac Utility Interactive Inverter | 4.2 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.33 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.4 | 94.6 | 95.5 | 96.5 | 96.7 | 96.7 | 96.2 | 95.3 | 97.1 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | 94.2 | 96.5 | 97.1 | 97.5 | 97.6 | 97.4 | 97.3 | Growatt New Energy Technology Co., Ltd.4.2Growatt 4200 MTL-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 4200 MTL-US [277V] | Y | N | N | 4200W 277 Vac Utility Interactive Inverter | 4.2 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.4 | 94.4 | 96 | 96.6 | 96.8 | 96.6 | 96.3 | 92.1 | 95.2 | 96.3 | 97.3 | 97.6 | 97.1 | 97 | 93.6 | 96.3 | 97.2 | 97.6 | 97.6 | 97.6 | 97.4 | Growatt New Energy Technology Co., Ltd.4.2Growatt 4200 MTL-US [277V]
Growatt New Energy Technology Co., Ltd. | Growatt 5000MTLP-US [208V] | Y | N | N | 5000 W 208 Vac Utility Interactive Inverter | 4.59 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 89.9 | 92.5 | 93.8 | 94.9 | 95.1 | 95.1 | 94.6 | 93.2 | 95.3 | 96 | 96.6 | 96.7 | 96.6 | 96.4 | 92.5 | 94.8 | 95.7 | 96.4 | 96.6 | 96.5 | 96.2 | Growatt New Energy Technology Co., Ltd.4.59Growatt 5000MTLP-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 5000 MTL-US [208V] | Y | N | N | 4600 W 208 Vac Utility Interactive Inverter | 4.6 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.7 | 96.5 | 96.8 | 96.9 | 96.5 | 96 | 96.5 | 95.4 | 97 | 97.3 | 97.4 | 97 | 96.5 | 97 | 94.3 | 96.4 | 96.9 | 97.1 | 97 | 96.5 | 96.8 | Growatt New Energy Technology Co., Ltd.4.6Growatt 5000 MTL-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 5000 MTL-US [240V] | Y | N | N | 4600 W 240 Vac Utility Interactive Inverter | 4.6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.8 | 95.2 | 96 | 96.7 | 96.6 | 96.4 | 96.3 | 95.8 | 97.3 | 97.7 | 97.8 | 97.5 | 97.1 | 97.5 | 96.7 | 96.7 | 97.2 | 97.5 | 97.4 | 97.1 | 97.3 | Growatt New Energy Technology Co., Ltd.4.6Growatt 5000 MTL-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 5000 MTL-US [277V] | Y | N | N | 4600 W 277 Vac Utility Interactive Inverter | 4.6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.43 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.2 | 94.9 | 95.6 | 96.6 | 96.8 | 96.8 | 96.4 | 94.6 | 96.7 | 97.2 | 97.6 | 97.6 | 97.4 | 97.4 | 95.4 | 97.1 | 97.6 | 97.9 | 97.8 | 97.7 | 97.7 | Growatt New Energy Technology Co., Ltd.4.6Growatt 5000 MTL-US [277V]
Growatt New Energy Technology Co., Ltd. | Growatt 5000MTLP-US [277V] | Y | N | N | 5000 W 277 Vac Utility Interactive Inverter | 5.06 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.06 | 89.5 | 92.3 | 93.8 | 95 | 95.5 | 95.5 | 94.8 | 94.3 | 96.1 | 96.8 | 97.3 | 97.4 | 97.3 | 97.1 | 93.5 | 95.6 | 96.4 | 97 | 97.2 | 97.2 | 96.9 | Growatt New Energy Technology Co., Ltd.5.06Growatt 5000MTLP-US [277V]
Growatt New Energy Technology Co., Ltd. | Growatt 5000MTLP-US [240V] | Y | N | N | 5000 W 240 Vac Utility Interactive Inverter | 5.07 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.07 | 90.5 | 93 | 94.3 | 95.2 | 95.4 | 95.3 | 94.9 | 93.9 | 95.8 | 96.5 | 97 | 97.1 | 96.9 | 96.8 | 93.1 | 95.3 | 96.1 | 96.8 | 96.9 | 96.9 | 96.6 | Growatt New Energy Technology Co., Ltd.5.07Growatt 5000MTLP-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 6000MTLP-US [208V] | Y | N | N | 6000 W 208 Vac Utility Interactive Inverter | 5.34 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.53 | 1.07 | 1.6 | 2.67 | 4.01 | 5.34 | 90.7 | 93.2 | 94.3 | 95 | 95 | 94.9 | 94.7 | 93.9 | 95.7 | 96.3 | 96.7 | 96.6 | 96.4 | 96.4 | 93.3 | 95.3 | 95.9 | 96.5 | 96.5 | 96.3 | 96.2 | Growatt New Energy Technology Co., Ltd.5.34Growatt 6000MTLP-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 6000MTLP-US [240V] | Y | N | N | 6000 W 240 Vac Utility Interactive Inverter | 6.08 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.61 | 1.22 | 1.82 | 3.04 | 4.56 | 6.08 | 91.3 | 93.6 | 94.7 | 95.4 | 95.5 | 95.6 | 95.1 | 94.6 | 96.1 | 96.7 | 97 | 97 | 96.8 | 96.8 | 93.9 | 95.6 | 96.3 | 96.8 | 96.8 | 96.7 | 96.6 | Growatt New Energy Technology Co., Ltd.6.08Growatt 6000MTLP-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 6000MTLP-US [277V] | Y | N | N | 6000 W 277 Vac Utility Interactive Inverter | 6.08 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.61 | 1.22 | 1.82 | 3.04 | 4.56 | 6.08 | 90.4 | 93 | 94.4 | 95.3 | 95.4 | 95.3 | 94.9 | 94.9 | 96.4 | 96.9 | 97.3 | 97.4 | 97.2 | 97.2 | 94.1 | 95.9 | 96.6 | 97.1 | 97.2 | 97.1 | 96.9 | Growatt New Energy Technology Co., Ltd.6.08Growatt 6000MTLP-US [277V]
Growatt New Energy Technology Co., Ltd. | Growatt 7000MTLP-US [208V] | Y | N | N | 7000W 208 Vac Utility Interactive Inverter | 6.093 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 280 | 385 | 485 | 609.3 | 1218.6 | 1827.9 | 3046.5 | 4569.75 | 6093 | 93.9 | 95.4 | 95.8 | 95.9 | 95.5 | 95.3 | 95.6 | 95.4 | 96.6 | 96.8 | 96.6 | 96.1 | 95.9 | 96.3 | 94.3 | 95.9 | 96.4 | 96.5 | 96.2 | 96 | 96.2 | Growatt New Energy Technology Co., Ltd.6.093Growatt 7000MTLP-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 7600MTLP-US [208V] | Y | N | N | 7000W 208 Vac Utility Interactive Inverter | 6.741 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 270 | 380 | 480 | 674.1 | 1348.2 | 2022.3 | 3370.51 | 5055.76 | 6741.01 | 94.1 | 95.5 | 95.7 | 95.7 | 95.2 | 95 | 95.3 | 95.7 | 96.7 | 96.8 | 96.6 | 96.1 | 95.9 | 96.3 | 94.7 | 96.2 | 96.5 | 96.5 | 96.1 | 95.8 | 96.2 | Growatt New Energy Technology Co., Ltd.6.74101Growatt 7600MTLP-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 7000MTLP-US [240V] | Y | N | N | 7000W 240 Vac Utility Interactive Inverter | 7.011 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.051 |  |  | 270 | 385 | 485 | 701.11 | 1402.22 | 2103.33 | 3505.55 | 5258.33 | 7011.1 | 94 | 95.7 | 95.9 | 96 | 95.8 | 95.5 | 95.8 | 95.7 | 96.8 | 97 | 96.9 | 96.7 | 96.4 | 96.7 | 94.6 | 96.4 | 96.8 | 96.9 | 96.7 | 96.3 | 96.6 | Growatt New Energy Technology Co., Ltd.7.011Growatt 7000MTLP-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 7000MTLP-US [277V] | Y | N | N | 7000W 277 Vac Utility Interactive Inverter | 7.0161 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.051 |  |  | 275 | 385 | 480 | 701.61 | 1403.21 | 2104.82 | 3508.04 | 5262.05 | 7016.07 | 92.8 | 95.2 | 95.4 | 95.9 | 96.1 | 95.9 | 95.8 | 93.6 | 96.3 | 96.7 | 96.9 | 96.8 | 96.5 | 96.6 | 95 | 96.6 | 97.1 | 97.3 | 97.2 | 97 | 97.1 | Growatt New Energy Technology Co., Ltd.7.01607Growatt 7000MTLP-US [277V]
Growatt New Energy Technology Co., Ltd. | Growatt 7600MTLP-US [240V] | Y | N | N | 7600 W 240 Vac Utility Interactive Inverter | 7.604 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.051 |  |  | 270 | 380 | 480 | 760.4 | 1520.8 | 2281.19 | 3801.99 | 5702.99 | 7603.98 | 94.3 | 95.8 | 96.2 | 96.1 | 95.8 | 95.3 | 95.8 | 96.1 | 97 | 97.2 | 97.1 | 96.8 | 96.3 | 96.9 | 94.9 | 96.5 | 96.9 | 96.9 | 96.7 | 96.3 | 96.7 | Growatt New Energy Technology Co., Ltd.7.604Growatt 7600MTLP-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 7600MTLP-US [277V] | Y | N | N | 7600 W 277 Vac Utility Interactive Inverter | 7.652 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.051 |  |  | 270 | 380 | 480 | 765.15 | 1530.3 | 2295.45 | 3825.75 | 5738.63 | 7651.5 | 94.3 | 95.8 | 96.2 | 96.1 | 95.8 | 95.3 | 95.8 | 96.1 | 97 | 97.2 | 97.1 | 96.8 | 96.3 | 96.9 | 94.9 | 96.5 | 96.9 | 96.9 | 96.7 | 96.3 | 96.7 | Growatt New Energy Technology Co., Ltd.7.652Growatt 7600MTLP-US [277V]
Growatt New Energy Technology Co., Ltd. | Growatt 8000TL-US [208V] | Y | N | N | 8000W 208 Vac Utility Interactive Inverter | 8.07 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 345 | 480 | 0.81 | 1.61 | 2.42 | 4.03 | 6.05 | 8.07 | 95.6 | 96.7 | 97.1 | 97.2 | 97.1 | 96.9 | 97.1 | 94.9 | 96.3 | 96.8 | 97 | 96.9 | 96.8 | 96.8 | 92.6 | 95 | 95.8 | 96.4 | 96.4 | 96.2 | 96.1 | Growatt New Energy Technology Co., Ltd.8.07Growatt 8000TL-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 8000TL-US [240V] | Y | N | N | 8000W 240 Vac Utility Interactive Inverter | 8.08 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 100 | 380 | 480 | 0.81 | 1.62 | 2.42 | 4.04 | 6.06 | 8.08 | 95.4 | 96.7 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | 95.1 | 96.6 | 97 | 97.3 | 97.3 | 97.2 | 97.1 | 93.2 | 95.5 | 96.2 | 96.8 | 96.4 | 96.9 | 96.3 | Growatt New Energy Technology Co., Ltd.8.08Growatt 8000TL-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 9000TL-US [208V] | Y | N | N | 9000W 208 Vac Utility Interactive Inverter | 9.08 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 345 | 480 | 0.91 | 1.82 | 2.72 | 4.54 | 6.81 | 9.08 | 95.9 | 96.8 | 97.1 | 97.2 | 97 | 96.8 | 97 | 95.3 | 96.5 | 96.9 | 97 | 97 | 96.7 | 96.9 | 93.1 | 95.3 | 96 | 96.4 | 96.4 | 96.2 | 96.2 | Growatt New Energy Technology Co., Ltd.9.08Growatt 9000TL-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 9000TL-US [240V] | Y | N | N | 9000W 240 Vac Utility Interactive Inverter | 9.08 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 100 | 380 | 480 | 0.91 | 1.82 | 2.72 | 4.54 | 6.81 | 9.08 | 95.8 | 96.9 | 97.2 | 97.4 | 97.4 | 97.2 | 97.2 | 95.5 | 96.8 | 97.1 | 97.3 | 97.3 | 97.1 | 97.2 | 93.8 | 95.8 | 96.4 | 96.7 | 96.9 | 96.8 | 96.6 | Growatt New Energy Technology Co., Ltd.9.08Growatt 9000TL-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 10000TL-US [208V] | Y | N | N | 10000 W 208 Vac Utility Interactive Inverter | 10.09 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 308 | 345 | 480 | 1.01 | 2.02 | 3.03 | 5.04 | 7.57 | 10.09 | 95.8 | 96.9 | 97.1 | 97.2 | 97 | 96.6 | 97 | 95.5 | 96.6 | 96.9 | 97 | 96.9 | 96.5 | 96.8 | 93.1 | 95.4 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | Growatt New Energy Technology Co., Ltd.10.09Growatt 10000TL-US [208V]
Growatt New Energy Technology Co., Ltd. | Growatt 10000 TL3-US [240V] | Y | N | N | 10000 W 240 Vac Utility Interactive Inverter | 10.1 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.01 |  |  | 250 | 420 | 480 | 1.1 | 2.2 | 3.3 | 5.5 | 7.58 | 10.1 | 89.5 | 93.1 | 94.1 | 94.9 | 95 | 95 | 94.6 | 90.1 | 93.9 | 95.2 | 96 | 96.3 | 96.4 | 95.7 | 89.9 | 94.2 | 95.4 | 96.3 | 96.7 | 96.8 | 96 | Growatt New Energy Technology Co., Ltd.10.1Growatt 10000 TL3-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 12000 TL3-US [277V] | Y | N | N | 11620W 277 Vac Utility Interactive Inverter | 11.62 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.01 |  |  | 250 | 420 | 480 | 1.16 | 2.32 | 3.49 | 5.81 | 8.72 | 11.62 | 89.8 | 93.4 | 94.4 | 95.2 | 94.9 | 95 | 94.6 | 90.2 | 94.2 | 95.3 | 96.2 | 96.4 | 96.5 | 95.9 | 91 | 94.6 | 95.6 | 96.4 | 96.6 | 96.7 | 96.1 | Growatt New Energy Technology Co., Ltd.11.62Growatt 12000 TL3-US [277V]
Growatt New Energy Technology Co., Ltd. | Growatt 11000TL-US [240V] | Y | N | N | 11000W 240 Vac Utility Interactive Inverter | 11.7 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 356 | 380 | 480 | 1.17 | 2.34 | 3.51 | 5.85 | 8.78 | 11.7 | 96 | 97 | 97.3 | 97.3 | 97.2 | 97 | 97.2 | 95.8 | 96.9 | 97.2 | 97.3 | 97.2 | 96.9 | 97.1 | 94.3 | 96 | 96.5 | 97 | 96.8 | 96.5 | 96.6 | Growatt New Energy Technology Co., Ltd.11.7Growatt 11000TL-US [240V]
Growatt New Energy Technology Co., Ltd. | Growatt 18000 TL3-US [277V] | Y | N | N | 18220W 277 Vac Utility Interactive Inverter | 18.31 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.01 |  |  | 250 | 420 | 480 | 1.83 | 3.66 | 5.49 | 9.15 | 13.73 | 18.31 | 92.3 | 94.9 | 95.4 | 95.2 | 95.5 | 95.4 | 95.3 | 92.5 | 95.8 | 96.4 | 96.8 | 96.9 | 96.6 | 96.6 | 92.9 | 95.8 | 96.5 | 96.9 | 97.1 | 96.8 | 96.7 | Growatt New Energy Technology Co., Ltd.18.31Growatt 18000 TL3-US [277V]
Growatt New Energy Technology Co., Ltd. | Growatt 20000 TL3-US [277V] | Y | N | N | 20000W 277 Vac Utility Interactive Inverter | 20.42 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 250 | 420 | 480 | 2.04 | 4.08 | 6.12 | 10.21 | 15.31 | 20.42 | 92.7 | 95.1 | 95.5 | 95.6 | 95.7 | 95.7 | 95.5 | 93.1 | 96 | 96.5 | 96.8 | 96.8 | 96.8 | 96.6 | 93.5 | 96 | 96.6 | 97 | 97.1 | 97 | 96.8 | Growatt New Energy Technology Co., Ltd.20.42Growatt 20000 TL3-US [277V]
Growatt New Energy Technology Co., Ltd. | Growatt 33000TL3-US | Y | N | N | 32,273W (277/480 Vac) transformerless Utility Interactive Inverter | 32.27 |  | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.092 |  |  | 480 | 700 | 800 | 3.23 | 6.45 | 9.68 | 16.14 | 24.2 | 32.27 | 97.3 | 97.8 | 98.1 | 98.1 | 97.8 | 97.5 | 97.9 | 97.8 | 98.6 | 98.8 | 98.9 | 98.7 | 98.5 | 98.7 | 97.5 | 98 | 98.3 | 98.5 | 98.3 | 98.1 | 98.3 | Growatt New Energy Technology Co., Ltd.32.27Growatt 33000TL3-US
Growatt New Energy Technology Co., Ltd. | Growatt 36000TL3-US | Y | N | N | 35,712W (277/480 Vac) transformerless Utility Interactive Inverter | 35.71 |  | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.051 |  |  | 520 | 700 | 800 | 3.57 | 7.14 | 10.71 | 17.86 | 26.78 | 35.71 | 97.5 | 98.1 | 98.2 | 98.3 | 97.9 | 97.6 | 98 | 98 | 98.6 | 98.6 | 98.6 | 98.6 | 98.4 | 98.6 | 97.4 | 98.1 | 98.2 | 98.2 | 98.3 | 98.1 | 98.2 | Growatt New Energy Technology Co., Ltd.35.71Growatt 36000TL3-US
Growatt New Energy Technology Co., Ltd. | Growatt 40000TL3-US | Y | N | N | 39,847 W(277/480 Vac) transformerless Utility Interactive Inverter | 39.85 |  | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.051 |  |  | 570 | 700 | 800 | 3.98 | 7.97 | 11.95 | 19.92 | 29.89 | 39.85 | 97.5 | 98 | 98 | 98.2 | 98 | 97.6 | 98 | 98.2 | 98.6 | 98.6 | 98.4 | 98.7 | 98.5 | 98.6 | 97.5 | 98.1 | 98.1 | 98 | 98.3 | 98.1 | 98.2 | Growatt New Energy Technology Co., Ltd.39.85Growatt 40000TL3-US
Hansol Technics | HSPV-A250 | Y | N | N | 250 W Utility Interactive Inverter | 0.25 |  | 93 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.2 |  |  | 27 | 30 | 36 | 0.02 | 0.05 | 0.07 | 0.12 | 0.19 | 0.25 | 85.9 | 90.6 | 91.4 | 93 | 93.4 | 93.2 | 92.6 | 86.1 | 90.6 | 91.5 | 93.2 | 93.7 | 93.3 | 92.8 | 85.6 | 90.5 | 91.6 | 93.1 | 93.9 | 93.8 | 93 | Hansol Technics0.25HSPV-A250
Heart Transverter | HT2000 | Y | N | N | Utility Interactive Inverter | 1.97 |  | 89 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 15.7 |  |  | 20 | 30 | 40 | 0.2 | 0.39 | 0.59 | 0.99 | 1.48 | 1.97 | 88.6 | 89.1 | 90.6 | 89.1 | 87.4 | 85.6 | 88.2 | 85.4 | 89.6 | 91.5 | 89.8 | 88.6 | 86.7 | 89 | 87.6 | 89.7 | 91 | 90.4 | 89.2 | 87.7 | 89.5 | Heart Transverter1.97HT2000
Helios USA | 6TA [120V] | Y | N | N | 212W, 120Vac Inverter | 0.21 | 120 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.21 | 87.9 | 94.4 | 95.8 | 95.7 | 94.8 | 93.5 | 94.8 | 85.2 | 92.5 | 94.6 | 95.3 | 95.1 | 94.2 | 94.5 | 83.6 | 92 | 94.3 | 94.9 | 94.9 | 93.9 | 94.2 | Helios USA0.216TA [120V]
HiQ Solar | Mini3500-US | Y | N | N | 3.5 kW Utility Interactive Inverter | 3.5 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 3.74 |  |  | 100 | 160 | 170 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 87.5 | 92.4 | 94 | 95.2 | 95.4 | 94.9 | 94.7 | 87.2 | 92.6 | 94.1 | 95.3 | 95.4 | 95 | 94.7 | 87.4 | 92.5 | 94.2 | 95.3 | 95.5 | 95.1 | 94.8 | HiQ Solar3.5Mini3500-US
HiQ Solar | TS208-5k75 [208V] | Y | N | N | 5.75 kW, 208 Vac, 3-phase Utility Interactive Inverter | 5.75 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.5 |  |  | 325 | 380 | 525 | 0.58 | 1.15 | 1.73 | 2.88 | 4.31 | 5.75 | 95.7 | 97.3 | 97.7 | 97.8 | 97.5 | 97.1 | 97.5 | 94.8 | 97.1 | 97.5 | 97.7 | 97.5 | 97.1 | 97.4 | 92.4 | 95.8 | 96.7 | 97.1 | 97.2 | 97 | 96.9 | HiQ Solar5.75TS208-5k75 [208V]
HiQ Solar | TS480-8k [480V] | Y | N | N | 8 kW, 480 Vac, Utility Interactive Inverter, 3-phase dual MPPT | 8 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 |  |  | 100 | 740 | 800 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 93.6 | 96.6 | 97.4 | 97.7 | 97.9 | 97.9 | 97.6 | 95.3 | 97.5 | 98 | 98.4 | 98.5 | 98.5 | 98.3 | 94.6 | 97.2 | 97.9 | 98.4 | 98.6 | 98.6 | 98.2 | HiQ Solar8TS480-8k [480V]
HiQ Solar | TSXL480-10k [480V] | N | Y | N | 10 KW, 480 Vac Grid Support Utility Interactve Inverter | 9.975 | 480 | 97.5 | [09/28/2018] | [0.28] | Not Applicable | N | N |  | 8.3 |  |  | 450 | 750 | 850 | 0.9975 | 1.995 | 2.9925 | 4.9875 | 7.4812 | 9.975 | 94.1157 | 96.7771 | 97.3429 | 97.7271 | 97.6957 | 97.5171 | 97.4619 | 94.11 | 96.8457 | 97.6443 | 98.1614 | 98.22 | 98.14 | 97.9015 | 93.1871 | 96.46 | 97.4557 | 98.1029 | 98.2386 | 98.2 | 97.8232 | HiQ Solar9.975TSXL480-10k [480V] | 2018-11-01
HiSEL Power | HiSEL-K 1500 [208V] | Y | N | N | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 100 | 300 | 360 | 0.15 | 0.3 | 0.45 | 0.75 | 1.13 | 1.5 | 86.5 | 91.8 | 93.5 | 95 | 94.9 | 95.1 | 94.3 | 88.8 | 93.4 | 94.7 | 95.7 | 95.9 | 95.8 | 95.3 | 90.7 | 94.2 | 95.6 | 96.4 | 96.3 | 96.4 | 95.9 | HiSEL Power1.5HiSEL-K 1500 [208V]
HiSEL Power | HiSEL-K 1500 [240V] | Y | N | N | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.5 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.13 |  |  | 100 | 300 | 360 | 0.15 | 0.3 | 0.45 | 0.75 | 1.13 | 1.5 | 85.9 | 91.4 | 93.2 | 94.8 | 95 | 95.2 | 94.2 | 87.5 | 92.8 | 94.3 | 95.6 | 96 | 96 | 95.2 | 90.4 | 94 | 95 | 96 | 96.4 | 96.4 | 95.8 | HiSEL Power1.5HiSEL-K 1500 [240V]
HiSEL Power | HiSEL-K 2000 [208V] | Y | N | N | 2 kW, 208 Vac Utility Interactive Inverter | 2 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.13 |  |  | 100 | 350 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.1 | 93.6 | 94.7 | 95.3 | 95.4 | 95.2 | 95 | 92.6 | 95 | 96 | 96.1 | 96.2 | 96 | 95.9 | 91.6 | 94.7 | 95.4 | 95.9 | 96.2 | 95.8 | 95.7 | HiSEL Power2HiSEL-K 2000 [208V]
HiSEL Power | HiSEL-K 2000 [240V] | Y | N | N | 2.8 kW, 240 Vac Utility Interactive Inverter | 2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.17 |  |  | 100 | 380 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89.6 | 93.2 | 94.5 | 95.3 | 95.6 | 95.5 | 95 | 92.2 | 94.7 | 96 | 96.5 | 96.7 | 96.4 | 96.3 | 94.1 | 95.4 | 96.2 | 96.5 | 96.5 | 96.4 | 96.3 | HiSEL Power2HiSEL-K 2000 [240V]
HiSEL Power | HiSEL-K 3000 [208V] | Y | N | N | 2.8 kW, 208 Vac Utility Interactive Inverter | 2.8 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 |  |  | 100 | 350 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 90.3 | 93.4 | 94.8 | 95.6 | 95.6 | 95.6 | 95.2 | 93.1 | 95.7 | 96.3 | 96.7 | 96.5 | 95.9 | 96.3 | 92 | 95 | 95.9 | 96.5 | 96.4 | 96 | 96.1 | HiSEL Power2.8HiSEL-K 3000 [208V]
HiSEL Power | HiSEL-K 3000 [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 2.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 |  |  | 100 | 380 | 440 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.1 | 93 | 94.5 | 95.5 | 95.8 | 95.8 | 95.2 | 93.1 | 95.9 | 96.3 | 96.9 | 96.9 | 96.9 | 96.7 | 92.7 | 95.6 | 96.7 | 96.9 | 96.9 | 96.9 | 96.6 | HiSEL Power2.8HiSEL-K 3000 [240V]
HiSEL Power | HiSEL-K 4000 [208V] | Y | N | N | 4 kW, 208 Vac Utility Interactive Inverter | 4 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 350 | 440 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 93.7 | 96.1 | 96.8 | 97.2 | 97.1 | 96.8 | 96.9 | 95.4 | 97.1 | 97.5 | 97.6 | 97.4 | 97.2 | 97.4 | 94 | 96.3 | 97 | 97.4 | 97.3 | 97.1 | 97.1 | HiSEL Power4HiSEL-K 4000 [208V]
HiSEL Power | HiSEL-K 4000 [240V] | Y | N | N | 4.6 kW, 240 Vac Utility Interactive Inverter | 4 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 |  |  | 100 | 380 | 440 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 93.1 | 95.8 | 96.6 | 97.3 | 97.4 | 97.2 | 97 | 95.5 | 97.1 | 97.6 | 97.9 | 97.8 | 97.5 | 97.6 | 94.6 | 96.7 | 97.4 | 97.6 | 97.6 | 97.4 | 97.4 | HiSEL Power4HiSEL-K 4000 [240V]
HiSEL Power | HiSEL-K 5000 [208V] | Y | N | N | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 350 | 440 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.8 | 96.1 | 96.8 | 97.1 | 96.9 | 96.4 | 96.7 | 95.3 | 97 | 97.5 | 97.5 | 97.3 | 96.8 | 97.2 | 94 | 96.3 | 96.9 | 97.2 | 97.1 | 96.7 | 96.9 | HiSEL Power4.6HiSEL-K 5000 [208V]
HiSEL Power | HiSEL-K 5000 [240V] | Y | N | N | 4.6 kW, 240 Vac Utility Interactive Inverter | 4.6 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 100 | 380 | 440 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.3 | 95.8 | 96.7 | 97.2 | 97.2 | 96.9 | 96.9 | 95.4 | 96.9 | 97.6 | 97.9 | 97.8 | 97.5 | 97.6 | 94.6 | 96.7 | 97.2 | 97.6 | 97.6 | 97.4 | 97.4 | HiSEL Power4.6HiSEL-K 5000 [240V]
Home Director | HD-SUN-INV1100-EVR [120V] | Y | N | N | 1100 W, 120 Vac Utility Interactive Inverter | 1.1 | 120 | 90.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 182 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 81.8 | 89 | 90.9 | 92.1 | 92.4 | 92.5 | 91.6 | 79.9 | 88 | 90.1 | 91.7 | 92.2 | 92.3 | 91.1 | 74.8 | 84.7 | 87.8 | 90 | 90.8 | 91.1 | 89.3 | Home Director1.1HD-SUN-INV1100-EVR [120V]
Home Director | HD-SUN-INV2000-EVR [240V] | Y | N | N | 2000 W, 240 Vac Utility Interactive Inverter | 2 | 240 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 199 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.3 | 91.7 | 92.6 | 93.5 | 93.2 | 93 | 92.9 | 85.7 | 90.8 | 92.1 | 92.9 | 92.9 | 92.6 | 92.4 | 82.4 | 88.8 | 90.5 | 91.6 | 91.8 | 91.6 | 91.1 | Home Director2HD-SUN-INV2000-EVR [240V]
Home Director | HD-SUN-INV2500 [240V] | Y | N | N | 2500 W, 240 Vac Utility Interactive Inverter | 2.5 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2 | Home Director2.5HD-SUN-INV2500 [240V]
Home Director | HD-SUN-INV3000 [240V] | Y | N | N | 3000 W, 240 Vac Utility Interactive Inverter | 3 | 240 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.63 |  |  | 100 | 222.5 | 380 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 88.9 | 92.9 | 93.8 | 94.3 | 94.2 | 93.9 | 93.9 | 87.9 | 92.5 | 93.5 | 94.1 | 94 | 93.8 | 93.7 | 84.9 | 90.9 | 92.4 | 93.3 | 93.2 | 93 | 92.7 | Home Director3HD-SUN-INV3000 [240V]
Home Director | HD-SUN-INV3500 [240V] | Y | N | N | 3500 W, 240 Vac Utility Interactive Inverter | 3.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.86 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5 | Home Director3.5HD-SUN-INV3500 [240V]
Home Director | HD-SUN-INV4600 [208V] | Y | N | N | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 |  |  | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95 | Home Director4.6HD-SUN-INV4600 [208V]
Home Director | HD-SUN-INV4800 [240V] | Y | N | N | 4800 W, 240 Vac Utility Interactive Inverter | 4.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.1 |  |  | 100 | 263 | 400 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 86.8 | 93.5 | 95.5 | 97 | 97.2 | 97.1 | 96.4 | 85.5 | 92.9 | 95 | 96.7 | 96.9 | 96.8 | 96 | 84.5 | 91.5 | 93.9 | 95.9 | 96.2 | 96.1 | 95.1 | Home Director4.8HD-SUN-INV4800 [240V]
Home Director | HD-SUN-INV5200 [240V] | Y | N | N | 5200 W, 240 Vac Utility Interactive Inverter | 5.2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 |  |  | 100 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5 | Home Director5.2HD-SUN-INV5200 [240V]
Hoymiles Converter Technology | MI-250 [240V] | Y | N | N | 250 W, 240 Vac Utility Interactive Inverter | 0.25 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.1 |  |  | 27 | 37 | 48 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 94.7 | 95.7 | 96.1 | 96.5 | 96.4 | 95.8 | 96.2 | 95.1 | 96 | 96.1 | 96.5 | 96.6 | 96.7 | 96.5 | 94.7 | 95.9 | 96 | 96.4 | 96.4 | 96.6 | 96.3 | Hoymiles Converter Technology0.25MI-250 [240V]
Huawei Technologies Co., Ltd. | SUN2000-3.8KTL-USL0 [240V] | Y | Y | N | 3.8 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter | 3.8 | 240 | 99 | [06/14/2018] | [V100R001D00] | Not Applicable | Y | N |  | 2.18 |  |  | 370 | 395 | 420 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 96.375 | 98.2332 | 98.6641 | 99.0028 | 99.0572 | 99.0776 | 98.8512 | 96.1637 | 98.1176 | 98.4788 | 98.9469 | 99.0231 | 99.0365 | 98.7828 | 96.0702 | 97.9945 | 98.4563 | 98.8641 | 98.9923 | 98.9967 | 98.7345 | Huawei Technologies Co., Ltd.3.8SUN2000-3.8KTL-USL0 [240V] | 2018-07-16
Huawei Technologies Co., Ltd. | SUN2000-5KTL-USL0 [240V] | Y | Y | N | 5 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter | 5 | 240 | 99 | [06/14/2018] | [V100R001D00] | Not Applicable | Y | N |  | 2.07 |  |  | 370 | 395 | 420 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 97.0703 | 98.3856 | 98.7211 | 99.0239 | 99.0199 | 98.8703 | 98.8677 | 96.8811 | 98.3814 | 98.661 | 98.9319 | 98.966 | 98.8203 | 98.8023 | 96.6926 | 98.2929 | 98.5924 | 98.8825 | 98.8862 | 98.7742 | 98.7272 | Huawei Technologies Co., Ltd.5SUN2000-5KTL-USL0 [240V] | 2018-07-16
Huawei Technologies Co., Ltd. | SUN2000-7.6KTL-USL0 [240V] | Y | Y | N | 7.6 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter | 7.6 | 240 | 99 | [06/14/2018] | [V100R001D00] | Not Applicable | Y | N |  | 2.06 |  |  | 370 | 395 | 420 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 98.0246 | 98.8109 | 98.9586 | 98.9973 | 98.9182 | 98.749 | 98.8901 | 97.8253 | 98.7187 | 98.917 | 98.9382 | 98.8674 | 98.7164 | 98.8316 | 97.6925 | 98.6266 | 98.8792 | 98.9113 | 98.8473 | 98.6766 | 98.7988 | Huawei Technologies Co., Ltd.7.6SUN2000-7.6KTL-USL0 [240V] | 2018-07-16
Huawei Technologies Co., Ltd. | SUN2000-9KTL-USL0 [240V] | Y | Y | Y | 9 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter | 9 | 240 | 99 | [06/14/2018] | [V100R001D00] | 2018-10-15 | Y | N |  | 1.97 |  |  | 370 | 395 | 420 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 97.6847 | 98.6455 | 98.9199 | 99.0618 | 99.0359 | 98.9738 | 98.9507 | 97.5338 | 98.5959 | 98.9052 | 99.0405 | 99.016 | 98.932 | 98.9233 | 97.5773 | 98.5984 | 98.8583 | 99.0241 | 99.0091 | 98.9183 | 98.9118 | Huawei Technologies Co., Ltd.9SUN2000-9KTL-USL0 [240V] | 2018-07-16 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-10KTL-USL0 [240V] | Y | Y | Y | 10 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter | 10 | 240 | 99 | [06/14/2018] | [V100R001D00] | 2018-10-15 | Y | N |  | 1.98 |  |  | 370 | 395 | 420 | 1 | 2 | 3 | 5 | 7.5 | 10 | 97.6401 | 98.656 | 98.9366 | 99.0483 | 99.013 | 98.9033 | 98.933 | 97.4485 | 98.548 | 98.8594 | 99.0041 | 98.9773 | 98.8792 | 98.8813 | 97.1851 | 98.4207 | 98.7677 | 98.933 | 98.9378 | 98.845 | 98.8158 | Huawei Technologies Co., Ltd.10SUN2000-10KTL-USL0 [240V] | 2018-07-16 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-11.4KTL-USL0 [240V] | Y | Y | Y | 11.4 kW, 240 Vac 1-phase transformerless Grid Support Utility Interactive Inverter | 11.4 | 240 | 99 | [06/14/2018] | [V100R001D00] | 2018-10-15 | Y | N |  | 1.97 |  |  | 370 | 395 | 420 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 97.8855 | 98.7855 | 98.9735 | 99.0471 | 98.9836 | 98.8375 | 98.9346 | 97.7154 | 98.6539 | 98.9173 | 98.9881 | 98.9407 | 98.8014 | 98.8775 | 97.5395 | 98.5822 | 98.8395 | 98.9436 | 98.9124 | 98.7749 | 98.8319 | Huawei Technologies Co., Ltd.11.4SUN2000-11.4KTL-USL0 [240V] | 2018-07-16 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-22KTL-US | Y | N | N | 22 kW transformerless Utility Interactive Inverter | 22.2 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.9 |  |  | 560 | 730 | 800 | 2.22 | 4.44 | 6.66 | 11.1 | 16.65 | 22.2 | 96 | 97.3 | 97.7 | 98 | 98 | 97.9 | 97.8 | 95.9 | 97.4 | 97.8 | 98.1 | 98.2 | 98.1 | 98 | 96.5 | 97.8 | 98.2 | 98.5 | 98.5 | 98.4 | 98.3 | Huawei Technologies Co., Ltd.22.2SUN2000-22KTL-US |  | 2018-05-01
Huawei Technologies Co., Ltd. | SUN2000-25KTL-US | Y | N | N | 25 kW transformerless Utility Interactive Inverter | 25 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 560 | 730 | 800 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 95.7 | 97.1 | 97.6 | 97.9 | 97.9 | 97.9 | 97.7 | 96.3 | 97.7 | 98.2 | 98.4 | 98.4 | 98.4 | 98.3 | 95.9 | 97.5 | 98 | 98.3 | 98.3 | 98.3 | 98.1 | Huawei Technologies Co., Ltd.25SUN2000-25KTL-US |  | 2018-05-01
Huawei Technologies Co., Ltd. | SUN2000-30KTL-US | Y | N | N | 30 kW transformerless Utility Interactive Inverter | 30 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 560 | 730 | 800 | 3 | 6 | 9 | 15 | 22.5 | 30 | 96.1 | 97.4 | 97.7 | 97.9 | 97.9 | 97.8 | 97.8 | 96.6 | 97.9 | 98.3 | 98.4 | 98.4 | 98.3 | 98.3 | 96.4 | 97.8 | 98.2 | 98.3 | 98.3 | 98.2 | 98.2 | Huawei Technologies Co., Ltd.30SUN2000-30KTL-US |  | 2018-05-01
Huawei Technologies Co., Ltd. | SUN2000-33KTL-US | Y | N | N | 33 kW Utility Interactive Inverter | 33 |  | 98.5 | Not Applicable | Not Applicable | Not Applicable | N | N |  | 1.8 |  |  | 460 | 720 | 850 | 3.3 | 6.6 | 9.9 | 16.5 | 24.75 | 33 | 95.6305 | 97.31 | 97.6239 | 97.8333 | 97.8889 | 97.7881 | 97.7211 | 97.5169 | 98.6741 | 98.8513 | 98.8841 | 98.8741 | 98.7894 | 98.8049 | 96.9145 | 98.1094 | 98.38 | 98.4576 | 98.4622 | 98.3838 | 98.3679 | Huawei Technologies Co., Ltd.33SUN2000-33KTL-US |  | 2018-05-01
Huawei Technologies Co., Ltd. | SUN2000-33KTL-US [480V] | N | Y | Y | 33 kW, 480 Vac, transformerless Grid Support Utility Interactive Inverter | 33 | 480 | 98.5 | [3/22/2017] | [SUN2000 V200 R002C20] | 2018-10-15 | N | N |  | 1.8 |  |  | 460 | 720 | 850 | 3.3 | 6.6 | 9.9 | 16.5 | 24.75 | 33 | 95.6305 | 97.31 | 97.6239 | 97.8333 | 97.8889 | 97.7881 | 97.7211 | 97.5169 | 98.6741 | 98.8513 | 98.8841 | 98.8741 | 98.7894 | 98.8049 | 96.9145 | 98.1094 | 98.38 | 98.4576 | 98.4622 | 98.3838 | 98.3679 | Huawei Technologies Co., LTD33SUN2000-33KTL-US [SI1] | 2017-11-01 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-36KTL-US | Y | N | N | 36 kW Utility Interactive Inverter | 36 |  | 98.5 | Not Applicable | Not Applicable | Not Applicable | N | N |  | 1.8 |  |  | 490 | 720 | 850 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 96.4077 | 97.5458 | 97.8137 | 97.9912 | 97.9878 | 97.8775 | 97.8768 | 97.9739 | 98.7413 | 98.8734 | 98.8955 | 98.8578 | 98.762 | 98.8216 | 97.1101 | 98.2156 | 98.4158 | 98.4713 | 98.4443 | 98.3524 | 98.3771 | Huawei Technologies Co., Ltd.36SUN2000-36KTL-US |  | 2018-05-01
Huawei Technologies Co., Ltd. | SUN2000-36KTL-US [480V] | N | Y | Y | 36 kW, 480 Vac, Transformerlss Grid Support Utility Interactive Inverter | 36 | 480 | 98.5 | [3/22/2017] | [SUN2000 V200 R002C20] | 2018-10-15 | N | N |  | 1.8 |  |  | 490 | 720 | 850 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 96.4077 | 97.5458 | 97.8137 | 97.9912 | 97.9878 | 97.8775 | 97.8768 | 97.9739 | 98.7413 | 98.8734 | 98.8955 | 98.8578 | 98.762 | 98.8216 | 97.1101 | 98.2156 | 98.4158 | 98.4713 | 98.4443 | 98.3524 | 98.3771 | Huawei Technologies Co., LTD36SUN2000-36KTL-US [SI1] | 2017-11-01 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-40KTL-US | Y | N | N | 40 kW Utility Interactive Inverter | 40 |  | 98.5 | Not Applicable | Not Applicable | Not Applicable | N | N |  | 1.8 |  |  | 530 | 720 | 850 | 4 | 8 | 12 | 20 | 30 | 40 | 96.7485 | 97.7289 | 97.9466 | 98.102 | 98.049 | 97.9087 | 97.9728 | 98.0538 | 98.7273 | 98.7781 | 98.8628 | 98.7907 | 98.8053 | 98.7724 | 97.2662 | 98.2155 | 98.3638 | 98.4571 | 98.3764 | 98.4169 | 98.3414 | Huawei Technologies Co., Ltd.40SUN2000-40KTL-US |  | 2018-05-01
Huawei Technologies Co., Ltd. | SUN2000-40KTL-US [480V] | N | Y | Y | 40 kW, 480 Vac, transformerless Grid Support Utility Interactive Inverter | 40 | 480 | 98.5 | [3/22/2017] | [SUN2000 V200 R002C20] | 2018-10-15 | N | N |  | 1.8 |  |  | 530 | 720 | 850 | 4 | 8 | 12 | 20 | 30 | 40 | 96.7485 | 97.7289 | 97.9466 | 98.102 | 98.049 | 97.9087 | 97.9728 | 98.0538 | 98.7273 | 98.7781 | 98.8628 | 98.7907 | 98.8053 | 98.7724 | 97.2662 | 98.2155 | 98.3638 | 98.4571 | 98.3764 | 98.4169 | 98.3414 | Huawei Technologies Co., LTD40SUN2000-40KTL-US [SI1] | 2017-11-01 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-45KTL-US-HV-D0 | Y | N | N | 45 kW transformerless Utility Interactive Inverter | 45.207 |  | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 1.11 |  |  | 800 | 1000 | 1200 | 97.5 | 98.1 | 98.2 | 98.2 | 98.1 | 97.9 | 98.2 | 98.6 | 98.7 | 98.6 | 98.5 | 98.4 | 98.5 | 98.2 | 98.6 | 98.7 | 98.6 | 98.5 | 98.4 | 98.5 | 98.1 | 98.5 | 98.5 | 98.5 | 98.4 | 98.2 | 98.4 | Huawei Technologies Co., Ltd.45.207SUN2000-45KTL-US-HV-D0 |  | 2018-05-01
Huawei Technologies Co., Ltd. | SUN2000-45KTL-US-HV-D0 [600V] | N | Y | Y | 45kW, 600Vac, Transformerlss Grid Support Utility Interactive Inverter | 45.207 | 600 | 98.5 | [9/29/2017] | [SUN2000HA V100R001] | 2018-10-15 | N | N |  |  |  | 1.11 | 800 | 1000 | 1200 | 97.5 | 98.1 | 98.2 | 98.2 | 98.1 | 97.9 | 98.2 | 98.6 | 98.7 | 98.6 | 98.5 | 98.4 | 98.5 | 98.2 | 98.6 | 98.7 | 98.6 | 98.5 | 98.4 | 98.5 | 98.1 | 98.5 | 98.5 | 98.5 | 98.4 | 98.2 | 98.4 | Huawei Technologies Co., LTD45.207SUN2000-45KTL-US-HV-D0 | 2017-11-15 | 2018-10-15
Huawei Technologies Co., Ltd. | SUN2000-100KTL-USH0 [800V] | Y | N | N | 100 kW, 800 Vac, 3-phase transformerless Utility Interactive Inverter | 100 | 800 | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 2.61 |  |  | 880 | 1120 | 1200 | 10 | 20 | 30 | 50 | 75 | 100 | 97.2971 | 98.0491 | 98.3042 | 98.447 | 98.4104 | 98.3164 | 98.338 | 97.6913 | 98.412 | 98.5995 | 98.6923 | 98.6594 | 98.5739 | 98.6037 | 98.2248 | 98.7907 | 98.9363 | 98.9879 | 98.9811 | 98.631 | 98.9199 | Huawei Technologies Co., Ltd.100SUN2000-100KTL-USH0 [800V] | 2018-05-01
HYOSUNG | HS-P1000GLO-U | Y | N | N | 1000 kW Utility Interactive Inverter | 991.4 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 177.45 |  |  | 600 | 665 | 880 | 99.14 | 198.28 | 297.42 | 495.7 | 743.55 | 991.4 | 96.2085 | 97.7725 | 98.2235 | 98.4344 | 98.3905 | 98.213 | 98.2526 | 95.5901 | 97.4963 | 98.0225 | 98.3115 | 98.318 | 98.1791 | 98.124 | 93.7224 | 96.1179 | 96.9934 | 97.458 | 97.5495 | 97.4122 | 97.232 | HYOSUNG991.4HS-P1000GLO-U
Ideal Power Inc. | 30C [480V] | Y | Y | Y | 30 kW, 480 Vac Grid Support Utility Interactive Battery Charge controller | 29.99 | 480 | 95 | [12/08/2017];[12/08/2017] | [3.2.42];[3.2.60] | 2018-10-15 | N | N |  | 56.8 |  |  | 550 | 700 | 850 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.7 | 94.3 | 94.8 | 95.2 | 95.1 | 94.8 | 94.9 | 92.2 | 94.2 | 94.6 | 95.3 | 95.4 | 95.5 | 95.1 | 89.6 | 92.8 | 93.3 | 94.8 | 95.2 | 95.4 | 94.6 | Ideal Power Inc29.9930C [480] [SI1] | 2018-02-01 | 2018-10-15
Ideal Power Inc. | 30C3 [480V] | Y | Y | Y | 30 kW, 480 Vac Grid Support Utility Interactive Battery Charge controller with additional Photovoltaic input | 29.99 | 480 | 95 | [12/08/2017];[12/08/2017] | [3.2.42];[3.2.60] | 2018-10-15 | N | N |  | 56.8 |  |  | 550 | 700 | 850 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.7 | 94.3 | 94.8 | 95.2 | 95.1 | 94.8 | 94.9 | 92.2 | 94.2 | 94.6 | 95.3 | 95.4 | 95.5 | 95.1 | 89.6 | 92.8 | 93.3 | 94.8 | 95.2 | 95.4 | 94.6 | Ideal Power Inc29.9930C3 [480] [SI1] | 2018-02-01 | 2018-10-15
Ideal Power Inc. | 30PV | Y | N | N | 30 kW Utility Interactive Inverter | 29.99 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 51.2 |  |  | 550 | 700 | 850 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.3 | 94.4 | 94.8 | 95.2 | 95.2 | 94.8 | 95 | 91.3 | 94 | 94.6 | 95.3 | 95.4 | 95.3 | 95 | 88.7 | 92.1 | 93.4 | 94.7 | 95.1 | 95.5 | 94.4 | Ideal Power Inc.29.9930PV | 2017-05 | 2018-08-15
Ideal Power Inc. | 30PV+S [480V] | Y | Y | Y | 30 kW, 480 Vac Grid Support Utility Interactive Inverter with PV and Battery Input for ground referenced arrays and batteries | 29.99 | 480 | 95 | [12/08/2017];[12/08/2017] | [3.2.42];[3.2.60] | 2018-10-15 | N | N |  | 51.2 |  |  | 550 | 700 | 850 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.3 | 94.4 | 94.8 | 95.2 | 95.2 | 94.8 | 95 | 91.3 | 94 | 94.6 | 95.3 | 95.4 | 95.3 | 95 | 88.7 | 92.1 | 93.4 | 94.7 | 95.1 | 95.5 | 94.4 | Ideal Power Inc29.9930PV+S [480] [SI1] | 2018-02-01 | 2018-10-15
Ideal Power Inc. | 30PVF | Y | N | N | 30 kW Utility Interactive Inverter | 29.99 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 51.2 |  |  | 550 | 700 | 850 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.3 | 94.4 | 94.8 | 95.2 | 95.2 | 94.8 | 95 | 91.3 | 94 | 94.6 | 95.3 | 95.4 | 95.3 | 95 | 88.7 | 92.1 | 93.4 | 94.7 | 95.1 | 95.5 | 94.4 | Ideal Power Inc.29.9930PVF | 2017-05 | 2018-08-15
Ideal Power Inc. | 30PVF+S [480V] | Y | Y | Y | 30 kW, 480 Vac Grid Support Utility Interactive Inverter with PV and Battery Input for floating ground referenced arrays and batteries | 29.99 | 480 | 95 | [12/08/2017] | [3.2.42] | 2018-10-15 | N | N |  | 51.2 |  |  | 550 | 700 | 850 | 3 | 6 | 9 | 15 | 22.49 | 29.99 | 92.3 | 94.4 | 94.8 | 95.2 | 95.2 | 94.8 | 95 | 91.3 | 94 | 94.6 | 95.3 | 95.4 | 95.3 | 95 | 88.7 | 92.1 | 93.4 | 94.7 | 95.1 | 95.5 | 94.4 | Ideal Power Inc29.9930PVF+S [480] [SI1] | 2018-02-01 | 2018-10-15
Ideal Power Inc. | IPV-30 kW-480 [480V] | Y | N | N | 30 kW, 480 Vac, 3-Phase Utility Interactive Inverter | 30.07 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 9.83 |  |  | 600 | 800 | 900 | 3.01 | 6.01 | 9.02 | 15.04 | 22.56 | 30.07 | 95.2 | 96 | 96.3 | 96.5 | 96.5 | 96.2 | 96.4 | 95.1 | 96.1 | 96.4 | 96.7 | 96.6 | 96.3 | 96.5 | 94.2 | 95.6 | 96.1 | 96.5 | 96.5 | 96.2 | 96.3 | Ideal Power Inc.30.07IPV-30 kW-480 [480V] |  | 2018-08-15
i-Energy | GT260 [240V] | Y | N | N | 210 W, 240 Vac Utility Interactive Inverter | 0.23 | 240 | 92 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.15 |  |  | 30 | 40 | 49 | 0.02 | 0.05 | 0.07 | 0.12 | 0.17 | 0.23 | 85.9 | 90.8 | 90.4 | 92.7 | 93.4 | 93.4 | 92.5 | 84.7 | 89.2 | 89.7 | 92.5 | 93.7 | 93.6 | 92.4 | 83 | 87.4 | 89.9 | 90.8 | 92.7 | 93.6 | 91.4 | i-Energy0.23GT260 [240V]
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 2.8 HF U 208 Vac [208V] | Y | N | N | 2.8 kW, 208 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 2.8 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 371 | 500 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 88.8 | 93.2 | 94.1 | 94.7 | 94.3 | 93.8 | 94.1 | 91.2 | 94.8 | 95.8 | 96.1 | 95.9 | 95.3 | 95.6 | 87.8 | 92.5 | 94.9 | 95.9 | 96 | 95.7 | 95.3 | INGETEAM POWER TECHNOLOGY S.A.2.8Ingecon Sun 2.8 HF U 208 Vac [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 2.8 HF U 240 Vac [240V] | Y | N | N | 2.8 kW, 240 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 2.8 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 371 | 500 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 87.3 | 92.7 | 93.9 | 94.7 | 94.7 | 94.6 | 94.2 | 90.3 | 94.7 | 95.7 | 96.5 | 96.4 | 96.1 | 96 | 88.5 | 93.8 | 95.1 | 96.2 | 96.4 | 96.2 | 95.8 | INGETEAM POWER TECHNOLOGY S.A.2.8Ingecon Sun 2.8 HF U 240 Vac [240V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 2.8 HF U 277Vac [277V] | Y | N | N | 2.8 kW, 277 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 2.8 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 371 | 500 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 85.2 | 91.9 | 93.6 | 94.6 | 94.7 | 94.6 | 94 | 88.8 | 94.1 | 95.6 | 96.6 | 96.5 | 96.7 | 96 | 88.3 | 94 | 95.3 | 96.5 | 96.7 | 96.7 | 96 | INGETEAM POWER TECHNOLOGY S.A.2.8Ingecon Sun 2.8 HF U 277Vac [277V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 2.8 TL U M 208 Vac [208V] | Y | N | N | 2.8 kW, 208 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 2.8 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 600 | 750 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 90.1 | 95 | 96 | 96.3 | 95.7 | 95.2 | 95.6 | 94.2 | 97.3 | 97.9 | 98.2 | 98.5 | 98.4 | 98.2 | 93.4 | 96.5 | 97.4 | 97.9 | 98 | 98 | 97.7 | INGETEAM POWER TECHNOLOGY S.A.2.8Ingecon Sun 2.8 TL U M 208 Vac [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 2.8 TL U M 240 Vac [240V] | Y | N | N | 2.8 kW, 240 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 2.8 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 600 | 750 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 88.6 | 94.2 | 95.5 | 96 | 95.5 | 94.9 | 95.2 | 92.9 | 97 | 97.9 | 98.4 | 98.6 | 98.5 | 98.1 | 93.2 | 96.6 | 97.6 | 98.3 | 98.4 | 98.4 | 98 | INGETEAM POWER TECHNOLOGY S.A.2.8Ingecon Sun 2.8 TL U M 240 Vac [240V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 3.3 HF U 208 Vac [208V] | Y | N | N | 3.3 kW, 208 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 3.3 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 371 | 500 | 0.33 | 0.66 | 0.99 | 1.65 | 2.47 | 3.3 | 89.1 | 93.5 | 94.3 | 94.5 | 94.1 | 93.6 | 94 | 92.2 | 95.3 | 95.9 | 96 | 95.6 | 95.2 | 95.6 | 89.8 | 94.2 | 95.3 | 96 | 96 | 95.7 | 95.6 | INGETEAM POWER TECHNOLOGY S.A.3.3Ingecon Sun 3.3 HF U 208 Vac [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 3.3 HF U 240 Vac [240V] | Y | N | N | 3.3 kW, 240 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 3.3 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 427 | 500 | 0.33 | 0.66 | 0.99 | 1.65 | 2.47 | 3.3 | 88.5 | 92.9 | 94.2 | 94.6 | 94.4 | 94.1 | 94.1 | 91.3 | 95.1 | 96 | 96.5 | 96.3 | 96.1 | 96 | 88.8 | 94.3 | 95.6 | 96.3 | 96.4 | 96.2 | 95.9 | INGETEAM POWER TECHNOLOGY S.A.3.3Ingecon Sun 3.3 HF U 240 Vac [240V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 3.3 HF U 277Vac [277V] | Y | N | N | 3.3 kW, 277 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 3.3 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 482 | 500 | 0.33 | 0.66 | 0.99 | 1.65 | 2.47 | 3.3 | 86.1 | 92.4 | 93.7 | 94.7 | 94.5 | 94.2 | 94 | 87.8 | 94.3 | 95.7 | 96.8 | 96.9 | 97 | 96.2 | 88.8 | 94.5 | 95.6 | 96.5 | 96.6 | 96.5 | 96.1 | INGETEAM POWER TECHNOLOGY S.A.3.3Ingecon Sun 3.3 HF U 277Vac [277V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 3.3 TL U M 208 Vac [208V] | Y | N | N | 3.3 kW, 208 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 3.3 | 208 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 600 | 750 | 0.33 | 0.66 | 0.99 | 1.65 | 2.47 | 3.3 | 90.4 | 95.8 | 96.3 | 96.7 | 96.1 | 95.3 | 96 | 94.9 | 97.6 | 98.1 | 98.4 | 98.3 | 98 | 98.1 | 94 | 96.8 | 97.7 | 98 | 98 | 97.9 | 97.8 | INGETEAM POWER TECHNOLOGY S.A.3.3Ingecon Sun 3.3 TL U M 208 Vac [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 3.3 TL U M 240 Vac [240V] | Y | N | N | 3.3 kW, 240 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 3.3 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 690 | 750 | 0.33 | 0.66 | 0.99 | 1.65 | 2.47 | 3.3 | 89.4 | 95 | 96.1 | 96.4 | 96 | 95.3 | 95.7 | 94.3 | 97.5 | 98.1 | 98.5 | 98.5 | 98.4 | 98.2 | 93.9 | 97.2 | 98 | 98.3 | 98.4 | 98.4 | 98.1 | INGETEAM POWER TECHNOLOGY S.A.3.3Ingecon Sun 3.3 TL U M 240 Vac [240V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 3.6TL U 208V [208V] | Y | N | N | 3.6 kW, 208 Vac, 1-phase Utility Interactive Inverter | 3.6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 300 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.6 | 95.4 | 96.1 | 96.5 | 96.3 | 96 | 96.1 | 92.8 | 96.1 | 96.8 | 97.2 | 97.2 | 96.9 | 96.9 | 85.4 | 92.9 | 94.5 | 95.7 | 96 | 95.9 | 95.1 | INGETEAM POWER TECHNOLOGY S.A.3.6INGECON SUN 3.6TL U 208V [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 3.6TL U 240V [240V] | Y | N | N | 3.6 kW, 240 Vac, 1-phase Utility Interactive Inverter | 3.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 380 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90.5 | 94.6 | 95.7 | 96.4 | 96.5 | 96.3 | 96 | 91.9 | 95.7 | 96.7 | 97.4 | 97.6 | 97.5 | 97.1 | 87.5 | 93.4 | 95.1 | 96.4 | 96.8 | 96.8 | 96 | INGETEAM POWER TECHNOLOGY S.A.3.6INGECON SUN 3.6TL U 240V [240V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 3.6TL U 277 [277V] | Y | N | N | 3.6 kW, 277 Vac, 1-phase Utility Interactive Inverter | 3.6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 50 |  |  | 100 | 380 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 89 | 93.7 | 95.1 | 96.2 | 96.4 | 96.3 | 95.7 | 91.2 | 95.8 | 97 | 97.7 | 98 | 98 | 97.4 | 88 | 94.2 | 95.7 | 96.9 | 97.3 | 97.4 | 96.5 | INGETEAM POWER TECHNOLOGY S.A.3.6INGECON SUN 3.6TL U 277 [277V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5 HF U 208 Vac [208V] | Y | N | N | 5 kW, 208 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 376 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.3 | 94.8 | 95.1 | 94.7 | 93.9 | 93.7 | 94.2 | 94.3 | 95.9 | 96 | 95.4 | 94.4 | 93.9 | 94.9 | 92.5 | 95.3 | 95.9 | 95.8 | 95.2 | 94.5 | 95.3 | INGETEAM POWER TECHNOLOGY S.A.5Ingecon Sun 5 HF U 208 Vac [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5 HF U 240 Vac [240V] | Y | N | N | 5 kW, 240 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 5 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 427 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.1 | 95 | 95.7 | 95.5 | 94.8 | 94.3 | 94.9 | 94.7 | 96.9 | 97.3 | 97.1 | 96.9 | 96.8 | 96.9 | 93.1 | 96 | 96.6 | 96.7 | 96.1 | 95.8 | 96.2 | INGETEAM POWER TECHNOLOGY S.A.5Ingecon Sun 5 HF U 240 Vac [240V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5 HF U 277Vac [277V] | Y | N | N | 5 kW, 277 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 5 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 482 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90.2 | 93.5 | 94.5 | 94.6 | 94.4 | 94 | 94.2 | 92.3 | 95.4 | 96 | 96.3 | 96 | 95.5 | 95.8 | 92.8 | 95.3 | 96 | 96.2 | 95.9 | 95.5 | 95.8 | INGETEAM POWER TECHNOLOGY S.A.5Ingecon Sun 5 HF U 277Vac [277V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5 TL U M 208 Vac [208V] | Y | N | N | 5 kW, 208 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 5 | 208 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 600 | 750 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93 | 96.4 | 97.1 | 97.1 | 96.4 | 95.6 | 96.5 | 96.2 | 98 | 98.2 | 98.1 | 97.9 | 97.6 | 97.9 | 95.3 | 97.4 | 97.7 | 97.8 | 97.5 | 97.2 | 97.5 | INGETEAM POWER TECHNOLOGY S.A.5Ingecon Sun 5 TL U M 208 Vac [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5 TL U M 240 Vac [240V] | Y | N | N | 5 kW, 240 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 5 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 690 | 750 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.4 | 96 | 96.9 | 97.1 | 96.6 | 96 | 96.5 | 95.9 | 98 | 98.3 | 98.4 | 98.3 | 98 | 98.2 | 95.5 | 97.6 | 98.1 | 98.3 | 98.1 | 97.9 | 98 | INGETEAM POWER TECHNOLOGY S.A.5Ingecon Sun 5 TL U M 240 Vac [240V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5TL U [208V] | Y | N | N | 5 kW, 208 Vac, 1-phase Utility Interactive Inverter | 5 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 300 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90.2 | 94.4 | 95.3 | 95.6 | 95.5 | 95.2 | 95.2 | 93.1 | 95.6 | 96.4 | 96.9 | 96.8 | 96.7 | 96.5 | 90.3 | 94.3 | 95.3 | 96 | 96.1 | 96 | 95.6 | INGETEAM POWER TECHNOLOGY S.A.5Ingecon Sun 5TL U [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5TL U [240V] | Y | N | N | 5 kW, 240 Vac, 1-phase Utility Interactive Inverter | 5 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 340 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90.2 | 94.4 | 95.3 | 95.6 | 95.5 | 95.2 | 95.2 | 93.1 | 95.6 | 96.4 | 96.9 | 96.8 | 96.7 | 96.5 | 90.3 | 94.3 | 95.3 | 96 | 96.1 | 96 | 95.6 | INGETEAM POWER TECHNOLOGY S.A.5Ingecon Sun 5TL U [240V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5TL U [277V] | Y | N | N | 5 kW, 277 Vac, 1-phase Utility Interactive Inverter | 5 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 380 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90.2 | 93.7 | 94.9 | 95.5 | 95.5 | 95.4 | 95.1 | 93 | 95.5 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 90.8 | 94.7 | 95.8 | 96.5 | 96.6 | 96.6 | 96.1 | INGETEAM POWER TECHNOLOGY S.A.5Ingecon Sun 5TL U [277V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5U [208V] | Y | N | N | 5 kW, 208 Vac, 1-phase Utility Interactive Inverter | 5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 300 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90.92 | 94.34 | 94.85 | 94.82 | 94.15 | 93.29 | 94.21 | 93.12 | 95.21 | 95.86 | 95.76 | 95.18 | 94.44 | 95.27 | 91.62 | 94.8 | 95.35 | 95.43 | 94.98 | 94.25 | 94.94 | INGETEAM POWER TECHNOLOGY S.A.5Ingecon Sun 5U [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5U [240V] | Y | N | N | 5 kW, 240 Vac, 1-phase Utility Interactive Inverter | 5 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 340 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90 | 93.7 | 94.5 | 94.8 | 94.5 | 93.9 | 94.3 | 92.2 | 95.1 | 96.1 | 96.3 | 96 | 95.6 | 95.8 | 91.6 | 94.9 | 95.7 | 95.9 | 95.7 | 95.3 | 95.5 | INGETEAM POWER TECHNOLOGY S.A.5Ingecon Sun 5U [240V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 5U [277V] | Y | N | N | 5 kW, 277 Vac, 1-phase Utility Interactive Inverter | 5 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 380 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 88 | 92.7 | 94 | 94.5 | 94.5 | 94.1 | 94.1 | 91.4 | 94.9 | 96 | 96.5 | 96.4 | 96.2 | 96.1 | 90.8 | 94.8 | 95.7 | 96.2 | 96.2 | 96 | 95.9 | INGETEAM POWER TECHNOLOGY S.A.5Ingecon Sun 5U [277V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 6 HF U 240 Vac [240V] | Y | N | N | 6 kW, 240 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 6 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 427 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 95 | 95.1 | 95 | 94.1 | 94.5 | 94.4 | 94.6 | 96.1 | 96.2 | 96.3 | 95.9 | 95.5 | 96 | 93.7 | 95.8 | 96.2 | 96 | 95.3 | 94.5 | 95.5 | INGETEAM POWER TECHNOLOGY S.A.6Ingecon Sun 6 HF U 240 Vac [240V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 6 HF U 277Vac [277V] | Y | N | N | 6 kW, 277 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 6 | 277 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 482 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 91.5 | 94.1 | 94.6 | 94.9 | 94.3 | 93.7 | 94.3 | 93.8 | 95.7 | 96.2 | 96.1 | 95.7 | 95.2 | 95.7 | 93.9 | 95.7 | 96.2 | 96.1 | 95.7 | 95.1 | 95.7 | INGETEAM POWER TECHNOLOGY S.A.6Ingecon Sun 6 HF U 277Vac [277V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 6 TL U M 240 Vac [240V] | Y | N | N | 6 kW, 240 Vac, 1-phase, Indoor/Outdoor Utility Interactive Inverter | 6 | 240 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 690 | 750 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 97 | 97.6 | 97.6 | 97.2 | 96.6 | 97.2 | 96.9 | 98.6 | 98.9 | 98.8 | 98.6 | 98.3 | 98.6 | 96.4 | 98.4 | 98.6 | 98.6 | 98.4 | 98.1 | 98.4 | INGETEAM POWER TECHNOLOGY S.A.6Ingecon Sun 6 TL U M 240 Vac [240V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 6TL U 240 [240V] | Y | N | N | 6 kW, 240 Vac, 1-phase Utility Interactive Inverter | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 240 | 450 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 95.3 | 95.9 | 96.1 | 95.9 | 95.4 | 95.8 | 94.7 | 96.9 | 97.3 | 97.5 | 97.4 | 97.2 | 97.3 | 91.8 | 95.1 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | INGETEAM POWER TECHNOLOGY S.A.6INGECON SUN 6TL U 240 [240V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 6TL U 277V [277V] | Y | N | N | 6 kW, 277 Vac, 1-phase Utility Interactive Inverter | 6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 277 | 450 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92 | 94.9 | 95.7 | 96.1 | 96 | 95.6 | 95.7 | 94.6 | 97 | 97.5 | 97.7 | 97.7 | 97.5 | 97.5 | 91.9 | 95.6 | 96.5 | 96.9 | 97.1 | 97 | 96.7 | INGETEAM POWER TECHNOLOGY S.A.6INGECON SUN 6TL U 277V [277V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 7.5TL U 208 [208V] | Y | N | N | 7.5 kW, 208 Vac, 1-phase Utility Interactive Inverter | 7.5 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 300 | 450 | 0.75 | 1.5 | 2.25 | 3.75 | 5.63 | 7.5 | 94.3 | 96.3 | 96.6 | 96.5 | 96.2 | 95.6 | 96.2 | 94.8 | 96.9 | 97.3 | 97.3 | 97.2 | 96.6 | 97.1 | 90.1 | 94.6 | 95.5 | 96.1 | 96.1 | 95.8 | 95.7 | INGETEAM POWER TECHNOLOGY S.A.7.5INGECON SUN 7.5TL U 208 [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 7.5TL U 240 [240V] | Y | N | N | 7.5 kW, 240 Vac, 1-phase Utility Interactive Inverter | 7.5 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 400 | 450 | 0.75 | 1.5 | 2.25 | 3.75 | 5.625 | 7.5 | 93.3 | 96 | 96.5 | 96.6 | 96.4 | 96.1 | 96.3 | 92.6 | 95.9 | 96.6 | 97.1 | 97 | 96.8 | 96.7 | 90.8 | 95.2 | 96.1 | 96.7 | 96.7 | 96.5 | 96.3 | INGETEAM POWER TECHNOLOGY S.A.7.5INGECON SUN 7.5TL U 240 [240V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 7.5TL U 277 [277V] | Y | N | N | 7.5 kW, 277 Vac, 1-phase Utility Interactive Inverter | 7.5 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 400 | 450 | 0.75 | 1.5 | 2.25 | 3.75 | 5.625 | 7.5 | 91.7 | 95.3 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.3 | 96.6 | 97.3 | 97.8 | 97.8 | 97.8 | 97.5 | 91.3 | 95.7 | 96.6 | 97.2 | 97.3 | 97.3 | 96.9 | INGETEAM POWER TECHNOLOGY S.A.7.5INGECON SUN 7.5TL U 277 [277V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 8.6TL U 240 [240V] | Y | N | N | 8.6 kW, 240 Vac, 1-phase Utility Interactive Inverter | 8.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 400 | 450 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 94 | 96.3 | 96.7 | 96.7 | 96.5 | 96 | 96.4 | 93 | 96 | 96.8 | 97 | 96.9 | 96.6 | 96.7 | 91.9 | 95.6 | 96.3 | 96.7 | 96.7 | 96.5 | 96.4 | INGETEAM POWER TECHNOLOGY S.A.8.6INGECON SUN 8.6TL U 240 [240V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 8.6TL U 277 [277V] | Y | N | N | 8.6 kW, 277 Vac, 1-phase Utility Interactive Inverter | 8.6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 400 | 450 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93 | 95.7 | 96.4 | 96.6 | 96.4 | 96 | 96.3 | 94.2 | 96.9 | 97.4 | 97.8 | 97.7 | 97.6 | 97.5 | 92.6 | 96.1 | 96.8 | 97.3 | 97.3 | 97.1 | 97 | INGETEAM POWER TECHNOLOGY S.A.8.6INGECON SUN 8.6TL U 277 [277V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 10TL U [277V] | Y | N | N | 10 kW, 277 Vac, 1-phase Utility Interactive Inverter | 10 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 400 | 450 | 1 | 2 | 3 | 5 | 7.5 | 10 | 93.9 | 96.4 | 96.9 | 97.1 | 96.8 | 96.4 | 96.7 | 94.9 | 97.1 | 97.6 | 97.8 | 97.7 | 97.5 | 97.5 | 93.6 | 96.4 | 97 | 97.3 | 97.2 | 97 | 97 | INGETEAM POWER TECHNOLOGY S.A.10INGECON SUN 10TL U [277V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 15U [208V] | Y | N | N | 15 kW, 208 Vac, 3-phase Utility Interactive Inverter | 15 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2 | 15 | 2 | 300 | 350 | 480 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 90.17 | 94.59 | 95.28 | 95.55 | 95.43 | 95.02 | 95.16 | 89.77 | 94.46 | 95.07 | 95.41 | 95.3 | 94.95 | 95.01 | 88.88 | 94.01 | 94.62 | 95 | 94.95 | 94.66 | 94.62 | INGETEAM POWER TECHNOLOGY S.A.15Ingecon Sun 15U [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 15U [480V] | Y | N | N | 15 kW, 480 Vac, 3-phase Utility Interactive Inverter | 15 | 480 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 | 15 | 4 | 300 | 350 | 480 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 89.89 | 93.84 | 94.85 | 95.66 | 95.6 | 95.28 | 95.19 | 89.52 | 93.58 | 94.69 | 95.53 | 95.51 | 95.24 | 95.07 | 88.3 | 92.84 | 94.15 | 95.13 | 95.08 | 94.92 | 94.59 | INGETEAM POWER TECHNOLOGY S.A.15Ingecon Sun 15U [480V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 18 TL U M [480V] | Y | N | N | 18 kW, 480 Vac, 3-phase transformerless, Indoor/Outdoor Utility Interactive Inverter | 18 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 10 |  |  | 375 | 700 | 820 | 1.8 | 3.6 | 5.4 | 9 | 13.5 | 18 | 93.9 | 96.1 | 96.4 | 96.8 | 96.8 | 96.7 | 96.6 | 96.7 | 98.2 | 98.5 | 98.7 | 98.7 | 98.6 | 98.6 | 95.8 | 97.8 | 98.2 | 98.5 | 98.5 | 98.5 | 98.3 | INGETEAM POWER TECHNOLOGY S.A.18Ingecon Sun 18 TL U M [480V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 24 TL U M [480V] | Y | N | N | 24 kW, 480 Vac, 3-phase transformerless, Indoor/Outdoor Utility Interactive Inverter | 24 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 10 |  |  | 460 | 700 | 820 | 2.4 | 4.8 | 7.2 | 12 | 18 | 24 | 95.7 | 97.1 | 97.2 | 97.3 | 97.2 | 97 | 97.1 | 97.8 | 98.6 | 98.7 | 98.7 | 98.6 | 98.5 | 98.6 | 97.2 | 98.2 | 98.5 | 98.5 | 98.4 | 98.3 | 98.4 | INGETEAM POWER TECHNOLOGY S.A.24Ingecon Sun 24 TL U M [480V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 25U [208V] | Y | N | N | 25 kW, 208 Vac, 3-phase Utility Interactive Inverter | 25 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2 | 25 | 2 | 300 | 350 | 480 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 91.45 | 94.79 | 95.72 | 96.09 | 95.92 | 95.5 | 95.67 | 90.99 | 94.59 | 95.53 | 95.99 | 95.9 | 95.48 | 95.59 | 90.34 | 94.03 | 95.14 | 95.67 | 95.58 | 95.05 | 95.23 | INGETEAM POWER TECHNOLOGY S.A.25Ingecon Sun 25U [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 25U [480V] | Y | N | N | 25 kW, 480 Vac, 3-phase Utility Interactive Inverter | 25 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 | 25 | 4 | 300 | 350 | 480 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 90.88 | 94.57 | 95.53 | 95.95 | 95.8 | 95.33 | 95.52 | 90.47 | 94.45 | 95.44 | 95.91 | 95.77 | 95.34 | 95.46 | 89.83 | 93.95 | 95.01 | 95.52 | 95.43 | 95.02 | 95.08 | INGETEAM POWER TECHNOLOGY S.A.25Ingecon Sun 25U [480V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 40TL U M [480V] | Y | N | N | 40 kW, 480 Vac, 3-phase, Indoor/Outdoor Utility Interactive Inverter | 39.95 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 10 |  |  | 520 | 700 | 820 | 3.9 | 8 | 12.1 | 19.2 | 30.1 | 40.1 | 96.74 | 97.78 | 97.76 | 97.55 | 97.15 | 96.61 | 97.28 | 97.69 | 98.32 | 98.48 | 98.29 | 97.95 | 97.68 | 98.08 | 96.93 | 97.91 | 98.14 | 98.11 | 97.86 | 97.51 | 97.9 | INGETEAM POWER TECHNOLOGY S.A.39.95Ingecon Sun 40TL U M [480V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 100U [208V] | Y | N | N | 100 kW, 208 Vac, 3-phase Utility Interactive Inverter | 100 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.82 | 94.01 | 94.82 | 95.34 | 95.08 | 93.88 | 94.82 | 90.27 | 93.75 | 94.58 | 95.15 | 95.04 | 93.75 | 94.69 | 89.04 | 92.9 | 93.9 | 94.75 | 94.31 | 93.33 | 94.02 | INGETEAM POWER TECHNOLOGY S.A.100Ingecon Sun 100U [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 100U [240V] | Y | N | N | 100 kW, 240 Vac, 3-phase Utility Interactive Inverter | 100 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3 |  |  | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.85 | 94.14 | 94.86 | 95.17 | 95.09 | 93.98 | 94.81 | 90.33 | 93.83 | 94.68 | 95.05 | 94.99 | 93.86 | 94.66 | 88.99 | 92.99 | 93.99 | 94.61 | 94.41 | 93.54 | 94.07 | INGETEAM POWER TECHNOLOGY S.A.100Ingecon Sun 100U [240V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 100UP [208V] | Y | N | N | 100 kW, 208 Vac, 3-phase Utility Interactive Inverter | 100 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 100 | 1 | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.53 | 94.8 | 95.45 | 95.79 | 95.69 | 94.57 | 95.41 | 91.06 | 94.55 | 95.25 | 95.65 | 95.55 | 94.67 | 95.26 | 89.83 | 93.76 | 94.6 | 95.2 | 95.16 | 94.4 | 94.78 | INGETEAM POWER TECHNOLOGY S.A.100Ingecon Sun 100UP [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 100UP [480V] | Y | N | N | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2 | 100 | 2 | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.91 | 95.03 | 95.69 | 95.95 | 95.84 | 94.83 | 95.6 | 91.44 | 94.7 | 95.5 | 95.81 | 95.71 | 94.7 | 95.43 | 90.22 | 94 | 94.91 | 95.38 | 95.33 | 94.33 | 94.97 | INGETEAM POWER TECHNOLOGY S.A.100Ingecon Sun 100UP [480V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 125 TL U 208 Outdoor [208V] | Y | N | N | 125 kW, 208 Vac, 3-phase Utility Interactive Inverter | 125 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 350 | 550 | 750 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 93.9 | 96.5 | 96.9 | 97 | 96.7 | 96 | 96.6 | 92.4 | 95.7 | 96.4 | 96.7 | 96.4 | 95.8 | 96.3 | 91 | 95.1 | 95.9 | 96.3 | 96.1 | 95.8 | 95.9 | INGETEAM POWER TECHNOLOGY S.A.125INGECON SUN 125 TL U 208 Outdoor [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 125 U 208 Outdoor [208V] | Y | N | N | 125 kW, 208 Vac, 3-phase Utility Interactive Inverter | 125 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 350 | 550 | 750 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 93.7 | 96.4 | 97 | 97.2 | 96.7 | 96.5 | 96.7 | 92.3 | 95.6 | 96.4 | 96.6 | 96.3 | 96.2 | 96.2 | 91.2 | 94.9 | 96 | 96.6 | 96 | 95.9 | 95.9 | INGETEAM POWER TECHNOLOGY S.A.125INGECON SUN 125 U 208 Outdoor [208V] |  | 2018-10-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 125 U 480 Outdoor [480V] | Y | N | N | 125 kW, 480 Vac, 3-phase Utility Interactive Inverter | 125 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 350 | 550 | 750 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 93.8 | 96.5 | 97.1 | 97.3 | 97.1 | 96.7 | 97 | 92.4 | 95.8 | 96.5 | 96.8 | 96.8 | 96.4 | 96.5 | 91.1 | 95 | 95.9 | 96.3 | 96.4 | 96.1 | 96 | INGETEAM POWER TECHNOLOGY S.A.125INGECON SUN 125 U 480 Outdoor [480V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 165 TL U 275 Outdoor [275V] | Y | N | N | 165 kW, 275Vac, 3-phase Utility Interactive Inverter | 165 | 275 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 460 | 605 | 750 | 16.5 | 33 | 49.5 | 82.5 | 123.8 | 165 | 94 | 96.7 | 97.2 | 97.4 | 97.1 | 96.5 | 97 | 93.2 | 96.2 | 96.9 | 97.2 | 96.9 | 96.5 | 96.7 | 92.4 | 95.9 | 96.6 | 96.9 | 96.7 | 96.3 | 96.5 | INGETEAM POWER TECHNOLOGY S.A.165INGECON SUN 165 TL U 275 Outdoor [275V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 200 TL U 330 Outdoor [330V] | Y | N | N | 200 kW, 330Vac, 3-phase Utility Interactive Inverter | 200 | 330 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 550 | 650 | 750 | 20 | 40 | 60 | 100 | 150 | 200 | 94.5 | 97 | 97.5 | 97.7 | 97.5 | 97 | 97.4 | 94 | 96.7 | 97.3 | 97.6 | 97.4 | 97 | 97.2 | 93.5 | 96.6 | 97.2 | 97.5 | 97.3 | 96.9 | 97.1 | INGETEAM POWER TECHNOLOGY S.A.200INGECON SUN 200 TL U 330 Outdoor [330V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 220 TL U 360 Outdoor [360V] | Y | N | N | 220 kW, 360Vac, 3-phase Utility Interactive Inverter | 220 | 360 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 600 | 675 | 750 | 22 | 44 | 66 | 110 | 165 | 220 | 94.2 | 96.9 | 97.5 | 97.6 | 97.5 | 97 | 97.33 | 93.8 | 96.7 | 97.3 | 97.5 | 97.4 | 97 | 97.22 | 93.8 | 96.7 | 97.1 | 97.5 | 97.4 | 96.9 | 97.21 | INGETEAM POWER TECHNOLOGY S.A.220INGECON SUN 220 TL U 360 Outdoor [360V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 375TL X208 Indoor [208V] | Y | N | N | 375 kW, 208 Vac, 3-phase Utility Interactive Inverter | 375 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 90 |  |  | 350 | 550 | 750 | 37.5 | 75 | 112.5 | 187.5 | 281.3 | 375 | 96 | 96.7 | 96.7 | 97 | 96.7 | 95.7 | 96.7 | 95.2 | 96.1 | 96.3 | 96.6 | 96.4 | 95.7 | 96.4 | 94.6 | 95.6 | 95.9 | 96.2 | 96.1 | 95.4 | 96 | INGETEAM POWER TECHNOLOGY S.A.375INGECON SUN 375TL X208 Indoor [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 375TL X208 Outdoor [208V] | Y | N | N | 375 kW, 208 Vac, 3-phase Utility Interactive Inverter | 375 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 90 |  |  | 350 | 550 | 750 | 37.5 | 75 | 112.5 | 187.5 | 281.3 | 375 | 96 | 96.7 | 96.7 | 97 | 96.7 | 95.7 | 96.7 | 95.2 | 96.1 | 96.3 | 96.6 | 96.4 | 95.7 | 96.4 | 94.6 | 95.6 | 95.9 | 96.2 | 96.1 | 95.4 | 96 | INGETEAM POWER TECHNOLOGY S.A.375INGECON SUN 375TL X208 Outdoor [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 500T U X480 Indoor [208V] | Y | N | N | 500 kW, 208 Vac, 3-phase Utility Interactive Inverter | 500 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Discontinued | 120 |  |  | 350 | 550 | 750 | 50 | 100 | 150 | 250 | 375 | 500 | 95.3 | 96.8 | 97.2 | 97.1 | 96.6 | 95.8 | 96.7 | 94.8 | 96.3 | 96.7 | 96.7 | 96.3 | 95.7 | 96.4 | 94.3 | 95.7 | 96.1 | 96.3 | 96 | 95.4 | 96 | INGETEAM POWER TECHNOLOGY S.A.500INGECON SUN 500T U X480 Indoor [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 500T U X480 Outdoor [208V] | Y | N | N | 500 kW, 208 Vac, 3-phase Utility Interactive Inverter | 500 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Discontinued | 120 |  |  | 350 | 550 | 750 | 50 | 100 | 150 | 250 | 375 | 500 | 95.3 | 96.8 | 97.2 | 97.1 | 96.6 | 95.8 | 96.7 | 94.8 | 96.3 | 96.7 | 96.7 | 96.3 | 95.7 | 96.4 | 94.3 | 95.7 | 96.1 | 96.3 | 96 | 95.4 | 96 | INGETEAM POWER TECHNOLOGY S.A.500INGECON SUN 500T U X480 Outdoor [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 500TL U X208 Indoor [208V] | Y | N | N | 500 kW, 208 Vac, 3-phase Utility Interactive Inverter | 500 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 120 |  |  | 350 | 550 | 750 | 50 | 100 | 150 | 250 | 375 | 500 | 96.2 | 96.6 | 96.8 | 96.9 | 96.6 | 95.9 | 96.6 | 95.5 | 96 | 96.2 | 96.5 | 96.4 | 95.9 | 96.3 | 95 | 95.4 | 95.6 | 96.1 | 96.1 | 95.5 | 95.9 | INGETEAM POWER TECHNOLOGY S.A.500INGECON SUN 500TL U X208 Indoor [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 500TL U X208 Outdoor [208V] | Y | N | N | 500 kW, 208 Vac, 3-phase Utility Interactive Inverter | 500 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 120 |  |  | 350 | 550 | 750 | 50 | 100 | 150 | 250 | 375 | 500 | 96.2 | 96.6 | 96.8 | 96.9 | 96.6 | 95.9 | 96.6 | 95.5 | 96 | 96.2 | 96.5 | 96.4 | 95.9 | 96.3 | 95 | 95.4 | 95.6 | 96.1 | 96.1 | 95.5 | 95.9 | INGETEAM POWER TECHNOLOGY S.A.500INGECON SUN 500TL U X208 Outdoor [208V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 500TL U X275 Indoor [275V] | Y | N | N | 500 kW, 3-phase, 275 Vac indoor, grid-tie photovoltaic Inverter | 500 | 275 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 90 |  |  | 460 | 605 | 750 | 50 | 100 | 150 | 250 | 375 | 500 | 96.1 | 96.9 | 97 | 97.4 | 97.2 | 96.5 | 97.2 | 95.8 | 96.6 | 96.8 | 97.2 | 97.1 | 96.4 | 97 | 95.3 | 96.2 | 96.5 | 96.9 | 96.9 | 96.3 | 96.7 | INGETEAM POWER TECHNOLOGY S.A.500INGECON SUN 500TL U X275 Indoor [275V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 600TL U X330 Indoor [330V] | Y | N | N | 600 kW, 3-phase, 330 Vac indoor, grid-tie photovoltaic Inverter | 600 | 330 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 90 |  |  | 550 | 650 | 750 | 60 | 120 | 180 | 300 | 450 | 600 | 96.2 | 97 | 97.2 | 97.6 | 97.5 | 96.9 | 97.4 | 95.9 | 96.7 | 97 | 97.5 | 97.4 | 96.8 | 97.2 | 95.7 | 96.5 | 96.9 | 97.3 | 97.3 | 96.7 | 97.1 | INGETEAM POWER TECHNOLOGY S.A.600INGECON SUN 600TL U X330 Indoor [330V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 600TL U X330 Outdoor [330V] | Y | N | N | 600 kW, 3-phase, 330 Vac outdoor, grid-tie photovoltaic Inverter | 600 | 330 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 90 |  |  | 550 | 650 | 750 | 60 | 120 | 180 | 300 | 450 | 600 | 96.2 | 97 | 97.2 | 97.6 | 97.5 | 96.9 | 97.4 | 95.9 | 96.7 | 97 | 97.5 | 97.4 | 96.8 | 97.2 | 95.7 | 96.5 | 96.9 | 97.3 | 97.3 | 96.7 | 97.1 | INGETEAM POWER TECHNOLOGY S.A.600INGECON SUN 600TL U X330 Outdoor [330V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 600TL X330 Outdoor [330V] | Y | N | N | 600 kW, 330Vac, 3-phase Utility Interactive Inverter | 600 | 330 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 90 |  |  | 550 | 650 | 750 | 60 | 120 | 180 | 300 | 450 | 600 | 96.2 | 97 | 97.2 | 97.6 | 97.5 | 96.9 | 97.4 | 95.9 | 96.7 | 97 | 97.5 | 97.4 | 96.8 | 97.2 | 95.7 | 96.5 | 96.9 | 97.3 | 97.3 | 96.7 | 97.1 | INGETEAM POWER TECHNOLOGY S.A.600INGECON SUN 600TL X330 Outdoor [330V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 610TL U B220 Indoor [220V] | Y | N | N | 610 kW, 220Vac, 3-phase Indoor Utility Interactive Inverter | 610 | 220 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/610. | 80 |  |  | 440 | 590 | 740 | 61 | 122 | 183 | 305 | 457.5 | 610 | 97.11 | 98.06 | 98.25 | 98.17 | 97.74 | 97.1 | 97.85 | 96.37 | 97.64 | 98.01 | 97.9 | 97.48 | 96.73 | 97.56 | 95.53 | 97.29 | 97.68 | 97.72 | 97.45 | 96.53 | 97.41 | INGETEAM POWER TECHNOLOGY S.A.610Ingecon Sun 610TL U B220 Indoor [220V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 610TL U B220 Outdoor [300V] | Y | N | N | 610 kW, 300Vac, 3-phase Outdoor Utility Interactive Inverter | 610 | 300 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/610. | 80 |  |  | 440 | 590 | 740 | 61 | 122 | 183 | 305 | 457.5 | 610 | 97.11 | 98.06 | 98.25 | 98.17 | 97.74 | 97.1 | 97.85 | 96.37 | 97.64 | 98.01 | 97.9 | 97.48 | 96.73 | 97.56 | 95.53 | 97.29 | 97.68 | 97.72 | 97.45 | 96.53 | 97.41 | INGETEAM POWER TECHNOLOGY S.A.610Ingecon Sun 610TL U B220 Outdoor [300V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 660TL U X275 Indoor [275V] | Y | N | N | 660 kW, 275Vac, 3-phase Utility Interactive Inverter | 660 | 275 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 120 |  |  | 460 | 605 | 750 | 66 | 132 | 198 | 330 | 495 | 660 | 96.3 | 96.8 | 97.1 | 97.3 | 97.1 | 96.5 | 97.1 | 96 | 96.5 | 96.7 | 97 | 97 | 96.6 | 96.9 | 95.7 | 96.1 | 96.4 | 96.8 | 96.8 | 96.3 | 96.6 | INGETEAM POWER TECHNOLOGY S.A.660INGECON SUN 660TL U X275 Indoor [275V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 660TL U X275 Outdoor [275V] | Y | N | N | 660 kW, 275Vac, 3-phase Utility Interactive Inverter | 660 | 275 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 120 |  |  | 460 | 605 | 750 | 66 | 132 | 198 | 330 | 495 | 660 | 96.3 | 96.8 | 97.1 | 97.3 | 97.1 | 96.5 | 97.1 | 96 | 96.5 | 96.7 | 97 | 97 | 96.6 | 96.9 | 95.7 | 96.1 | 96.4 | 96.8 | 96.8 | 96.3 | 96.6 | INGETEAM POWER TECHNOLOGY S.A.660INGECON SUN 660TL U X275 Outdoor [275V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 660TL X360 Indoor [360V] | Y | N | N | 660 kW, 360Vac, 3-phase Utility Interactive Inverter | 660 | 360 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 90 |  |  | 605 | 677 | 750 | 66 | 132 | 198 | 330 | 495 | 660 | 96.2 | 97 | 97.1 | 97.7 | 97.6 | 97 | 97.4 | 96.1 | 96.9 | 97.2 | 97.6 | 97.5 | 97 | 97.4 | 95.9 | 96.7 | 97.1 | 97.5 | 97.4 | 96.9 | 97.3 | INGETEAM POWER TECHNOLOGY S.A.660INGECON SUN 660TL X360 Indoor [360V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 660TL X360 Outdoor [360V] | Y | N | N | 660 kW, 360Vac, 3-phase Utility Interactive Inverter | 660 | 360 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 90 |  |  | 605 | 677 | 750 | 66 | 132 | 198 | 330 | 495 | 660 | 96.2 | 97 | 97.1 | 97.7 | 97.6 | 97 | 97.4 | 96.1 | 96.9 | 97.2 | 97.6 | 97.5 | 97 | 97.4 | 95.9 | 96.7 | 97.1 | 97.5 | 97.4 | 96.9 | 97.3 | INGETEAM POWER TECHNOLOGY S.A.660INGECON SUN 660TL X360 Outdoor [360V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 800TL U X330 Indoor [330V] | Y | N | N | 800 kW, 330Vac, 3-phase Utility Interactive Inverter | 800 | 330 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 120 |  |  | 550 | 650 | 750 | 80 | 160 | 240 | 400 | 600 | 800 | 96.5 | 96.9 | 97.2 | 97.4 | 97.4 | 96.9 | 97.3 | 96.3 | 96.7 | 96.9 | 97.3 | 97.3 | 96.9 | 97.2 | 96.1 | 96.4 | 96.7 | 97.1 | 97.2 | 96.7 | 97 | INGETEAM POWER TECHNOLOGY S.A.800INGECON SUN 800TL U X330 Indoor [330V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 800TL U X330 Outdoor [330V] | Y | N | N | 800 kW, 330Vac, 3-phase Utility Interactive Inverter | 800 | 330 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 120 |  |  | 550 | 650 | 750 | 80 | 160 | 240 | 400 | 600 | 800 | 96.5 | 96.9 | 97.2 | 97.4 | 97.4 | 96.9 | 97.3 | 96.3 | 96.7 | 96.9 | 97.3 | 97.3 | 96.9 | 97.2 | 96.1 | 96.4 | 96.7 | 97.1 | 97.2 | 96.7 | 97 | INGETEAM POWER TECHNOLOGY S.A.800INGECON SUN 800TL U X330 Outdoor [330V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 830TL U B300 Indoor [300V] | Y | N | N | 830 kW, 300Vac, 3-phase Indoor Utility Interactive Inverter | 830 | 300 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/830. | 80 |  |  | 440 | 590 | 740 | 83 | 166 | 249 | 415 | 622.5 | 830 | 97.21 | 98.13 | 98.27 | 98.16 | 97.74 | 97.18 | 97.86 | 96.5 | 97.77 | 97.96 | 97.92 | 97.55 | 97.06 | 97.62 | 95.7 | 97.41 | 97.7 | 97.66 | 97.36 | 96.88 | 97.38 | INGETEAM POWER TECHNOLOGY S.A.830Ingecon Sun 830TL U B300 Indoor [300V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 830TL U B300 Outdoor [300V] | Y | N | N | 830 kW, 300Vac, 3-phase Outdoor Utility Interactive Inverter | 830 | 300 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/830. | 80 |  |  | 440 | 590 | 740 | 83 | 166 | 249 | 415 | 622.5 | 830 | 97.21 | 98.13 | 98.27 | 98.16 | 97.74 | 97.18 | 97.86 | 96.5 | 97.77 | 97.96 | 97.92 | 97.55 | 97.06 | 97.62 | 95.7 | 97.41 | 97.7 | 97.66 | 97.36 | 96.88 | 97.38 | INGETEAM POWER TECHNOLOGY S.A.830Ingecon Sun 830TL U B300 Outdoor [300V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 880TL X360 Indoor [360V] | Y | N | N | 880 kW, 360Vac, 3-phase Utility Interactive Inverter | 880 | 360 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 120 |  |  | 605 | 677 | 750 | 88 | 176 | 264 | 440 | 660 | 880 | 96.5 | 96.9 | 97.2 | 97.5 | 97.5 | 97 | 97.4 | 96.4 | 96.8 | 97 | 97.4 | 97.5 | 97 | 97.3 | 96.3 | 96.6 | 96.9 | 97.3 | 97.4 | 96.9 | 97.2 | INGETEAM POWER TECHNOLOGY S.A.880INGECON SUN 880TL X360 Indoor [360V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | INGECON SUN 880TL X360 Outdoor [360V] | Y | N | N | 880 kW, 360Vac, 3-phase Utility Interactive Inverter | 880 | 360 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 120 |  |  | 605 | 677 | 750 | 88 | 176 | 264 | 440 | 660 | 880 | 96.5 | 96.9 | 97.2 | 97.5 | 97.5 | 97 | 97.4 | 96.4 | 96.8 | 97 | 97.4 | 97.5 | 97 | 97.3 | 96.3 | 96.6 | 96.9 | 97.3 | 97.4 | 96.9 | 97.2 | INGETEAM POWER TECHNOLOGY S.A.880INGECON SUN 880TL X360 Outdoor [360V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 915TL U B330 Indoor [330V] | Y | N | N | 915 kW, 330Vac, 3-phase Indoor Utility Interactive Inverter | 915 | 330 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/915. | 80 |  |  | 485 | 613 | 740 | 91.5 | 183 | 274.5 | 457.5 | 686.25 | 915 | 97.17 | 98.13 | 98.33 | 98.22 | 97.86 | 97.27 | 97.95 | 96.5 | 97.84 | 98.09 | 98.05 | 97.69 | 97.15 | 97.75 | 95.82 | 97.49 | 97.82 | 97.81 | 97.51 | 97.17 | 97.53 | INGETEAM POWER TECHNOLOGY S.A.915Ingecon Sun 915TL U B330 Indoor [330V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 915TL U B330 Outdoor [330V] | Y | N | N | 915 kW, 330Vac, 3-phase Outdoor Utility Interactive Inverter | 915 | 330 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/915. | 80 |  |  | 485 | 613 | 740 | 91.5 | 183 | 274.5 | 457.5 | 686.25 | 915 | 97.17 | 98.13 | 98.33 | 98.22 | 97.86 | 97.27 | 97.95 | 96.5 | 97.84 | 98.09 | 98.05 | 97.69 | 97.15 | 97.75 | 95.82 | 97.49 | 97.82 | 97.81 | 97.51 | 97.17 | 97.53 | INGETEAM POWER TECHNOLOGY S.A.915Ingecon Sun 915TL U B330 Outdoor [330V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1000TL U B360 Indoor [360V] | Y | N | N | 1000 kW, 360Vac, 3-phase Indoor Utility Interactive Inverter | 1000 | 360 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1000. | 80 |  |  | 524 | 632 | 740 | 100 | 200 | 300 | 500 | 750 | 1000 | 97.34 | 98.14 | 98.33 | 98.21 | 97.83 | 97.31 | 97.94 | 96.84 | 97.92 | 98.13 | 98.08 | 97.7 | 97.09 | 97.78 | 96.36 | 97.64 | 97.97 | 97.94 | 97.55 | 96.97 | 97.61 | INGETEAM POWER TECHNOLOGY S.A.1000Ingecon Sun 1000TL U B360 Indoor [360V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1000TL U B360 Outdoor [360V] | Y | N | N | 1000 kW, 360Vac, 3-phase Outdoor Utility Interactive Inverter | 1000 | 360 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1000. | 80 |  |  | 524 | 632 | 740 | 100 | 200 | 300 | 500 | 750 | 1000 | 97.34 | 98.14 | 98.33 | 98.21 | 97.83 | 97.31 | 97.94 | 96.84 | 97.92 | 98.13 | 98.08 | 97.7 | 97.09 | 97.78 | 96.36 | 97.64 | 97.97 | 97.94 | 97.55 | 96.97 | 97.61 | INGETEAM POWER TECHNOLOGY S.A.1000Ingecon Sun 1000TL U B360 Outdoor [360V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1110TL U B400 Indoor [400V] | Y | N | N | 1110 kW, 400Vac, 3-phase Indoor Utility Interactive Inverter | 1110 | 400 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1110. | 80 |  |  | 580 | 660 | 740 | 111 | 222 | 333 | 555 | 832.5 | 1110 | 97.16 | 98.08 | 98.29 | 98.27 | 97.94 | 97.39 | 98 | 96.8 | 97.93 | 98.19 | 98.25 | 97.8 | 97.32 | 97.89 | 96.54 | 97.71 | 98.06 | 98.12 | 97.67 | 97.35 | 97.75 | INGETEAM POWER TECHNOLOGY S.A.1110Ingecon Sun 1110TL U B400 Indoor [400V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1110TL U B400 Outdoor [400V] | Y | N | N | 1110 kW, 400Vac, 3-phase Outdoor Utility Interactive Inverter | 1110 | 400 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1110. | 80 |  |  | 580 | 660 | 740 | 111 | 222 | 333 | 555 | 832.5 | 1110 | 97.16 | 98.08 | 98.29 | 98.27 | 97.94 | 97.39 | 98 | 96.8 | 97.93 | 98.19 | 98.25 | 97.8 | 97.32 | 97.89 | 96.54 | 97.71 | 98.06 | 98.12 | 97.67 | 97.35 | 97.75 | INGETEAM POWER TECHNOLOGY S.A.1110Ingecon Sun 1110TL U B400 Outdoor [400V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1165TL U B420 Indoor [420V] | Y | N | N | 1165 kW, 420Vac, 3-phase Indoor Utility Interactive Inverter | 1165 | 420 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1165. | 80 |  |  | 610 | 675 | 740 | 116.5 | 233 | 349.5 | 582.5 | 873.75 | 1165 | 97.28 | 98.08 | 98.28 | 98.26 | 98.01 | 97.47 | 98.04 | 96.99 | 97.92 | 98.18 | 98.24 | 97.91 | 97.53 | 97.95 | 96.74 | 97.75 | 98.03 | 98.15 | 97.85 | 97.42 | 97.87 | INGETEAM POWER TECHNOLOGY S.A.1165Ingecon Sun 1165TL U B420 Indoor [420V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1165TL U B420 Outdoor [420V] | Y | N | N | 1165 kW, 420Vac, 3-phase Outdoor Utility Interactive Inverter | 1165 | 420 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1165. | 80 |  |  | 610 | 675 | 740 | 116.5 | 233 | 349.5 | 582.5 | 873.75 | 1165 | 97.28 | 98.08 | 98.28 | 98.26 | 98.01 | 97.47 | 98.04 | 96.99 | 97.92 | 98.18 | 98.24 | 97.91 | 97.53 | 97.95 | 96.74 | 97.75 | 98.03 | 98.15 | 97.85 | 97.42 | 97.87 | INGETEAM POWER TECHNOLOGY S.A.1165Ingecon Sun 1165TL U B420 Outdoor [420V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1170TL U B450 Indoor [450V] | Y | N | N | 1170 kW, 450 Vac, 3-phase Indoor Utility Interactive Inverter | 1170 | 450 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1170. | 90 |  |  | 660 | 874 | 1110 | 117 | 234 | 351 | 585 | 877.5 | 1170 | 96.72 | 97.82 | 98.06 | 97.98 | 97.77 | 97.44 | 97.79 | 95.95 | 97.35 | 97.71 | 97.64 | 97.46 | 97.08 | 97.44 | 94.9 | 96.86 | 97.3 | 97.29 | 97.12 | 96.78 | 97.06 | INGETEAM POWER TECHNOLOGY S.A.1170Ingecon Sun 1170TL U B450 Indoor [450V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1170TL U B450 Outdoor [450V] | Y | N | N | 1170 kW, 450 Vac, 3-phase Outdoor Utility Interactive Inverter | 1170 | 450 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1170. | 90 |  |  | 660 | 874 | 1110 | 117 | 234 | 351 | 585 | 877.5 | 1170 | 96.72 | 97.82 | 98.06 | 97.98 | 97.77 | 97.44 | 97.79 | 95.95 | 97.35 | 97.71 | 97.64 | 97.46 | 97.08 | 97.44 | 94.9 | 96.86 | 97.3 | 97.29 | 97.12 | 96.78 | 97.06 | INGETEAM POWER TECHNOLOGY S.A.1170Ingecon Sun 1170TL U B450 Outdoor [450V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1400TL U B540 Indoor [450V] | Y | N | N | 1400 kW, 450 Vac, 3-phase Indoor Utility Interactive Inverter | 1400 | 450 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1400. | 90 |  |  | 786 | 936 | 1110 | 140 | 280 | 420 | 700 | 1050 | 1400 | 96.97 | 97.87 | 98.13 | 98.03 | 97.86 | 97.59 | 97.88 | 96.48 | 97.59 | 97.88 | 97.81 | 97.65 | 97.31 | 97.65 | 95.86 | 97.26 | 97.61 | 97.58 | 97.44 | 97.11 | 97.4 | INGETEAM POWER TECHNOLOGY S.A.1400Ingecon Sun 1400TL U B540 Indoor [450V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1400TL U B540 Outdoor [450V] | Y | N | N | 1400 kW, 450 Vac, 3-phase Outdoor Utility Interactive Inverter | 1400 | 450 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1400. | 90 |  |  | 786 | 936 | 1110 | 140 | 280 | 420 | 700 | 1050 | 1400 | 96.97 | 97.87 | 98.13 | 98.03 | 97.86 | 97.59 | 97.88 | 96.48 | 97.59 | 97.88 | 97.81 | 97.65 | 97.31 | 97.65 | 95.86 | 97.26 | 97.61 | 97.58 | 97.44 | 97.11 | 97.4 | INGETEAM POWER TECHNOLOGY S.A.1400Ingecon Sun 1400TL U B540 Outdoor [450V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1500TL U B578 Indoor [450V] | Y | N | N | 1500 kW, 450 Vac, 3-phase Indoor Utility Interactive Inverter | 1500 | 450 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1500. | 90 |  |  | 840 | 963 | 1110 | 150 | 300 | 450 | 750 | 1125 | 1500 | 96.86 | 97.84 | 98.1 | 98.04 | 97.87 | 97.57 | 97.88 | 96.48 | 97.64 | 97.96 | 97.91 | 97.71 | 97.39 | 97.72 | 96.06 | 97.33 | 97.77 | 97.72 | 97.56 | 97.24 | 97.53 | INGETEAM POWER TECHNOLOGY S.A.1500Ingecon Sun 1500TL U B578 Indoor [450V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1500TL U B578 Outdoor [450V] | Y | N | N | 1500 kW, 450 Vac, 3-phase Outdoor Utility Interactive Inverter | 1500 | 450 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1500. | 90 |  |  | 840 | 963 | 1110 | 150 | 300 | 450 | 750 | 1125 | 1500 | 96.86 | 97.84 | 98.1 | 98.04 | 97.87 | 97.57 | 97.88 | 96.48 | 97.64 | 97.96 | 97.91 | 97.71 | 97.39 | 97.72 | 96.06 | 97.33 | 97.77 | 97.72 | 97.56 | 97.24 | 97.53 | INGETEAM POWER TECHNOLOGY S.A.1500Ingecon Sun 1500TL U B578 Outdoor [450V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1560TL U B600 Indoor [450V] | Y | N | N | 1560 kW, 450 Vac, 3-phase Indoor Utility Interactive Inverter | 1560 | 450 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1560. | 90 |  |  | 870 | 978 | 1110 | 156 | 312 | 468 | 780 | 1170 | 1560 | 96.67 | 97.84 | 98.13 | 98.11 | 97.98 | 97.63 | 97.95 | 96.41 | 97.69 | 98.02 | 98.01 | 97.73 | 97.44 | 97.76 | 95.96 | 97.42 | 97.85 | 97.84 | 97.57 | 97.27 | 97.57 | INGETEAM POWER TECHNOLOGY S.A.1560Ingecon Sun 1560TL U B600 Indoor [450V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1560TL U B600 Outdoor [450V] | Y | N | N | 1560 kW, 450 Vac, 3-phase Outdoor Utility Interactive Inverter | 1560 | 450 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1560. | 90 |  |  | 870 | 978 | 1110 | 156 | 312 | 468 | 780 | 1170 | 1560 | 96.67 | 97.84 | 98.13 | 98.11 | 97.98 | 97.63 | 97.95 | 96.41 | 97.69 | 98.02 | 98.01 | 97.73 | 97.44 | 97.76 | 95.96 | 97.42 | 97.85 | 97.84 | 97.57 | 97.27 | 97.57 | INGETEAM POWER TECHNOLOGY S.A.1560Ingecon Sun 1560TL U B600 Outdoor [450V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1600TL U B615 Indoor [450V] | Y | N | N | 1600 kW, 450 Vac, 3-phase Indoor Utility Interactive Inverter | 1600 | 450 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1600. | 90 |  |  | 892 | 988 | 1110 | 160 | 320 | 480 | 800 | 1200 | 1600 | 96.77 | 97.81 | 98.12 | 98.17 | 97.95 | 97.6 | 97.95 | 96.47 | 97.68 | 98.01 | 98.02 | 97.81 | 97.45 | 97.8 | 96.12 | 97.43 | 97.86 | 97.87 | 97.68 | 97.31 | 97.65 | INGETEAM POWER TECHNOLOGY S.A.1600Ingecon Sun 1600TL U B615 Indoor [450V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1600TL U B615 Outdoor [450V] | Y | N | N | 1600 kW, 450 Vac, 3-phase Outdoor Utility Interactive Inverter | 1600 | 450 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1600. | 90 |  |  | 892 | 988 | 1110 | 160 | 320 | 480 | 800 | 1200 | 1600 | 96.77 | 97.81 | 98.12 | 98.17 | 97.95 | 97.6 | 97.95 | 96.47 | 97.68 | 98.01 | 98.02 | 97.81 | 97.45 | 97.8 | 96.12 | 97.43 | 97.86 | 97.87 | 97.68 | 97.31 | 97.65 | INGETEAM POWER TECHNOLOGY S.A.1600Ingecon Sun 1600TL U B615 Outdoor [450V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1640TL U B630 Indoor [450V] | Y | N | N | 1640 kW, 450 Vac, 3-phase Indoor Utility Interactive Inverter | 1640 | 450 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1640. | 90 |  |  | 915 | 1000 | 1110 | 164 | 328 | 492 | 820 | 1230 | 1640 | 96.62 | 97.85 | 98.12 | 98.06 | 97.91 | 97.62 | 97.9 | 96.32 | 97.73 | 98.04 | 97.97 | 97.81 | 97.49 | 97.79 | 96.02 | 97.54 | 97.91 | 97.82 | 97.68 | 97.38 | 97.65 | INGETEAM POWER TECHNOLOGY S.A.1640Ingecon Sun 1640TL U B630 Indoor [450V] |  | 2018-05-15
INGETEAM POWER TECHNOLOGY S.A. | Ingecon Sun 1640TL U B630 Outdoor [450V] | Y | N | N | 1640 kW, 450 Vac, 3-phase Outdoor Utility Interactive Inverter | 1640 | 450 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Weighted efficiency includes transformer efficiency of Elettromil ABN0001ICM05/1640. | 90 |  |  | 915 | 1000 | 1110 | 164 | 328 | 492 | 820 | 1230 | 1640 | 96.62 | 97.85 | 98.12 | 98.06 | 97.91 | 97.62 | 97.9 | 96.32 | 97.73 | 98.04 | 97.97 | 97.81 | 97.49 | 97.79 | 96.02 | 97.54 | 97.91 | 97.82 | 97.68 | 97.38 | 97.65 | INGETEAM POWER TECHNOLOGY S.A.1640Ingecon Sun 1640TL U B630 Outdoor [450V] |  | 2018-05-15
Involar | MAC250A-240-NA | Y | N | N | 230W Utility Interactive Inverter | 0.23 |  | 93 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.11 |  |  | 28 | 35 | 40 | 0.02 | 0.05 | 0.07 | 0.12 | 0.17 | 0.23 | 87.6 | 90.5 | 92.8 | 93.3 | 93.7 | 93.4 | 93.1 | 86.1 | 88.9 | 92.4 | 93.8 | 94 | 94 | 93.2 | 83.9 | 87.2 | 92 | 93.9 | 93.9 | 94.2 | 92.9 | Involar0.23MAC250A-240-NA
Involar | MAC500-XX | Y | N | N | 500 W Utility Interactive Inverter | 0.5 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.114 |  |  | 30 | 35 | 40 | 0.05 | 0.1 | 0.15 | 0.25 | 0.375 | 0.5 | 92.8 | 94 | 94.4 | 94.7 | 94.6 | 93.8 | 94.5 | 93 | 94.2 | 94.5 | 94.7 | 94.8 | 94.2 | 94.6 | 92.8 | 94.2 | 94.5 | 94.7 | 94.9 | 94.4 | 94.6 | Involar0.5MAC500-XX
iPower | SHO-1.1 [120V] | Y | N | N | 1100W (120Vac) Utility Interactive Inverter | 1.1 | 120 | 90.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 182 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 81.8 | 89 | 90.9 | 92.1 | 92.4 | 92.5 | 91.6 | 79.9 | 88 | 90.1 | 91.7 | 92.2 | 92.3 | 91.1 | 74.8 | 84.7 | 87.8 | 90 | 90.8 | 91.1 | 89.3 | iPower1.1SHO-1.1 [120V]
iPower | SHO-2.0 [240V] | Y | N | N | 2000 W 240 Vac Utility Interactive Inverter | 2 | 240 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 199 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.3 | 91.7 | 92.6 | 93.5 | 93.2 | 93 | 92.9 | 85.7 | 90.8 | 92.1 | 92.9 | 92.9 | 92.6 | 92.4 | 82.4 | 88.8 | 90.5 | 91.6 | 91.8 | 91.6 | 91.1 | iPower2SHO-2.0 [240V]
iPower | SHO-2.5 [240V] | Y | N | N | 2500 W 240 Vac Utility Interactive Inverter | 2.5 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2 | iPower2.5SHO-2.5 [240V]
iPower | SHO-3.0 [240V] | Y | N | N | 3000 W 240 Vac Utility Interactive Inverter | 3 | 240 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.63 |  |  | 100 | 222.5 | 380 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 88.9 | 92.9 | 93.8 | 94.3 | 94.2 | 93.9 | 93.9 | 87.9 | 92.5 | 93.5 | 94.1 | 94 | 93.8 | 93.7 | 84.9 | 90.9 | 92.4 | 93.3 | 93.2 | 93 | 92.7 | iPower3SHO-3.0 [240V]
iPower | SHO-3.5 [240V] | Y | N | N | 3500 W 240 Vac Utility Interactive Inverter | 3.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.86 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.625 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5 | iPower3.5SHO-3.5 [240V]
iPower | SHO-4.6 [208V] | Y | N | N | 4600 W 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 |  |  | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95 | iPower4.6SHO-4.6 [208V]
iPower | SHO-4.8 [240V] | Y | N | N | 4800 W 240 Vac Utility Interactive Inverter | 4.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.1 |  |  | 100 | 263 | 400 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 86.8 | 93.5 | 95.5 | 97 | 97.2 | 97.1 | 96.4 | 85.5 | 92.9 | 95 | 96.7 | 96.9 | 96.8 | 96 | 84.5 | 91.5 | 93.9 | 95.9 | 96.2 | 96.1 | 95.1 | iPower4.8SHO-4.8 [240V]
iPower | SHO-5.2 [240V] | Y | N | N | 5200 W 240 Vac Utility Interactive Inverter | 5.2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 |  |  | 240 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5 | iPower5.2SHO-5.2 [240V]
Jema Energy | JAE7140 | Y | N | N | 100 kW Utility Interactive Inverter | 100 |  | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 20.5 |  |  | 290 | 340 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 92.5 | 95.3 | 95.9 | 96.1 | 96 | 95.5 | 95.8 | 91 | 94.6 | 95.4 | 95.9 | 95.8 | 95.3 | 95.5 | 87.1 | 92.6 | 94 | 95 | 95.1 | 94.7 | 94.5 | Jema Energy100JAE7140
Jema Energy | JAE7141 | Y | N | N | 100 kW Utility Interactive Inverter | 100 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 20.5 |  |  | 290 | 340 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.1 | 94.8 | 95.5 | 95.8 | 95.7 | 95.2 | 95.5 | 89.7 | 94 | 95 | 95.5 | 95.6 | 95 | 95.1 | 85.9 | 91.9 | 93.4 | 94.5 | 94.8 | 94.4 | 94 | Jema Energy100JAE7141
Jema Energy | IF500TL-UL OUTDOOR | Y | N | N | 500 kW, 3-phase Utility Interactive Inverter with MV NEMA TP1 transformer | 500 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 33.4 |  |  | 495 | 600 | 800 | 50 | 100 | 150 | 250 | 375 | 500 | 94.5 | 96.3 | 96.5 | 96.7 | 96.4 | 95.8 | 96.3 | 93.9 | 95.9 | 96.2 | 96.3 | 96 | 95.4 | 96 | 92.7 | 95.1 | 95.6 | 95.7 | 95.5 | 95 | 95.4 | Jema Energy500IF500TL-UL OUTDOOR
Jema Energy | IF600TL-UL OUTDOOR | Y | N | N | 600 kW, 3-phase Utility Interactive Inverter with MV NEMA TP1 transformer | 600 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 47 |  |  | 595 | 700 | 800 | 60 | 120 | 180 | 300 | 450 | 600 | 94.5 | 96.4 | 96.7 | 96.9 | 96.6 | 96.1 | 96.5 | 93.8 | 95.9 | 96.4 | 96.5 | 96.3 | 95.8 | 96.2 | 93.5 | 95.8 | 95.9 | 96.2 | 96.1 | 95.7 | 96 | Jema Energy600IF600TL-UL OUTDOOR
Jiangsu Zeversolar New Energy | Evershine TL3000-US-208 | Y | N | N | 3 kW Utility Interactive Inverter | 2.98 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 370 | 480 | 0.3 | 0.6 | 0.89 | 1.49 | 2.24 | 2.98 | 90.7 | 93.6 | 94.7 | 95.7 | 95.9 | 95.8 | 95.4 | 93.3 | 95.9 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.9 | 95.2 | 96 | 96.7 | 96.8 | 96.7 | 96.4 | Jiangsu Zeversolar New Energy2.98Evershine TL3000-US-208
Jiangsu Zeversolar New Energy | Evershine TL3000-US-240 | Y | N | N | 3 kW Utility Interactive Inverter | 2.98 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.35 |  |  | 100 | 370 | 480 | 0.3 | 0.6 | 0.89 | 1.49 | 2.24 | 2.98 | 90.3 | 93.4 | 94.3 | 95.5 | 95.9 | 95.9 | 95.3 | 93.8 | 96.3 | 96.9 | 97.2 | 97.2 | 97.2 | 97 | 91.7 | 95.5 | 96.4 | 96.9 | 97.1 | 97.1 | 96.7 | Jiangsu Zeversolar New Energy2.98Evershine TL3000-US-240
Jiangsu Zeversolar New Energy | Evershine TL4000-US-208 | Y | N | N | 4 kW Utility Interactive Inverter | 3.97 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 370 | 480 | 0.4 | 0.79 | 1.19 | 1.99 | 2.98 | 3.97 | 92.3 | 94.5 | 95.2 | 95.8 | 95.8 | 95.6 | 95.5 | 94.9 | 96.4 | 96.7 | 97 | 96.8 | 96.5 | 96.7 | 93.6 | 95.8 | 96.4 | 96.8 | 96.7 | 96.5 | 96.5 | Jiangsu Zeversolar New Energy3.97Evershine TL4000-US-208
Jiangsu Zeversolar New Energy | Evershine TL4000-US-240 | Y | N | N | 4 kW Utility Interactive Inverter | 3.99 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.35 |  |  | 100 | 370 | 480 | 0.4 | 0.79 | 1.19 | 1.99 | 2.98 | 3.97 | 90.9 | 94 | 94.9 | 95.8 | 96 | 95.8 | 95.5 | 94.5 | 96.7 | 97 | 97.3 | 97.2 | 97 | 97.1 | 93.1 | 96.1 | 96.8 | 97.2 | 97.1 | 97 | 96.9 | Jiangsu Zeversolar New Energy3.99Evershine TL4000-US-240
Jiangsu Zeversolar New Energy | Evershine TL5000-US-208 | Y | N | N | 5 kW Utility Interactive Inverter | 5 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.27 |  |  | 100 | 370 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.7 | 94.4 | 95.3 | 95.7 | 95.7 | 95.4 | 95.4 | 94 | 96.1 | 96.5 | 96.7 | 96.6 | 96.2 | 96.4 | 93 | 95.2 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | Jiangsu Zeversolar New Energy5Evershine TL5000-US-208
Jiangsu Zeversolar New Energy | Evershine TL5000-US-240 | Y | N | N | 5 kW Utility Interactive Inverter | 5 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.35 |  |  | 100 | 370 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.7 | 94.3 | 95.3 | 96 | 96 | 95.8 | 95.6 | 94.9 | 96.7 | 97 | 97.1 | 97 | 96.7 | 96.9 | 93.3 | 95.9 | 96.5 | 96.9 | 96.9 | 96.7 | 96.7 | Jiangsu Zeversolar New Energy5Evershine TL5000-US-240
Jiangsu Zeversolar New Energy | Evershine TL6000-US-208 | Y | N | N | 6 kW Utility Interactive Inverter | 5.32 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.27 |  |  | 100 | 370 | 480 | 0.53 | 1.06 | 1.6 | 2.66 | 3.99 | 5.32 | 92.7 | 94.8 | 95.5 | 95.7 | 95.5 | 95.1 | 95.4 | 94.9 | 96.6 | 96.8 | 96.7 | 96.4 | 95.8 | 96.4 | 93.3 | 96 | 96.4 | 96.6 | 96.2 | 95.9 | 96.2 | Jiangsu Zeversolar New Energy5.32Evershine TL6000-US-208
Jiangsu Zeversolar New Energy | Evershine TL6000-US-240 | Y | N | N | 6 kW Utility Interactive Inverter | 5.99 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.35 |  |  | 100 | 370 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.49 | 5.99 | 92.6 | 94.9 | 95.7 | 96 | 95.9 | 95.4 | 95.7 | 95.8 | 96.9 | 97.2 | 97.1 | 96.8 | 96.4 | 96.9 | 94 | 96.5 | 96.9 | 96.9 | 96.7 | 96.4 | 96.6 | Jiangsu Zeversolar New Energy5.99Evershine TL6000-US-240
Jiangyin Hareon Power | HR-240P-AC/Bb [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-240P-AC/Bb [208V]
Jiangyin Hareon Power | HR-240P-AC/Bb [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-240P-AC/Bb [240V]
Jiangyin Hareon Power | HR-240P-AC/BbP [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-240P-AC/BbP [208V]
Jiangyin Hareon Power | HR-240P-AC/BbP [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-240P-AC/BbP [240V]
Jiangyin Hareon Power | HR-245P-AC/Bb [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-245P-AC/Bb [208V]
Jiangyin Hareon Power | HR-245P-AC/Bb [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-245P-AC/Bb [240V]
Jiangyin Hareon Power | HR-245P-AC/BbP [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-245P-AC/BbP [208V]
Jiangyin Hareon Power | HR-245P-AC/BbP [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-245P-AC/BbP [240V]
Jiangyin Hareon Power | HR-250-AC/Cb [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-250-AC/Cb [208V]
Jiangyin Hareon Power | HR-250-AC/Cb [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-250-AC/Cb [240V]
Jiangyin Hareon Power | HR-250P-AC/Bb [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-250P-AC/Bb [208V]
Jiangyin Hareon Power | HR-250P-AC/Bb [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-250P-AC/Bb [240V]
Jiangyin Hareon Power | HR-250P-AC/BbP [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-250P-AC/BbP [208V]
Jiangyin Hareon Power | HR-250P-AC/BbP [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-250P-AC/BbP [240V]
Jiangyin Hareon Power | HR-255-AC/Cb [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-255-AC/Cb [208V]
Jiangyin Hareon Power | HR-255-AC/Cb [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-255-AC/Cb [240V]
Jiangyin Hareon Power | HR-255P-AC/Bb [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-255P-AC/Bb [208V]
Jiangyin Hareon Power | HR-255P-AC/Bb [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-255P-AC/Bb [240V]
Jiangyin Hareon Power | HR-255P-AC/BbP [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-255P-AC/BbP [208V]
Jiangyin Hareon Power | HR-255P-AC/BbP [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-255P-AC/BbP [240V]
Jiangyin Hareon Power | HR-260-AC/Cb [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-260-AC/Cb [208V]
Jiangyin Hareon Power | HR-260-AC/Cb [240V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-260-AC/Cb [240V]
Jiangyin Hareon Power | HR-260P-AC/Bb [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-260P-AC/Bb [208V]
Jiangyin Hareon Power | HR-260P-AC/Bb [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-260P-AC/Bb [240V]
Jiangyin Hareon Power | HR-260P-AC/BbP [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-260P-AC/BbP [208V]
Jiangyin Hareon Power | HR-260P-AC/BbP [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-260P-AC/BbP [240V]
Jiangyin Hareon Power | HR-265-AC/Cb [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-265-AC/Cb [208V]
Jiangyin Hareon Power | HR-265-AC/Cb [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-265-AC/Cb [240V]
Jiangyin Hareon Power | HR-270-AC/Cb [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-270-AC/Cb [208V]
Jiangyin Hareon Power | HR-270-AC/Cb [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Jiangyin Hareon Power0.24HR-270-AC/Cb [240V]
Jinko Solar Co.,Ltd. | JKMS260M-60B-EP [240V] | N | Y | Y | 260 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter | 0.23 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | Jinko Solar Co.,Ltd.0.23JKMS260M-60B-EP | 2017-11-01 | 2018-10-15
Jinko Solar Co.,Ltd. | JKMS265M-60B-EP [240V] | N | Y | Y | 265 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter | 0.23 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | Jinko Solar Co.,Ltd.0.23JKMS265M-60B-EP | 2017-11-01 | 2018-10-15
Jinko Solar Co.,Ltd. | JKMS270M-60B-EP [240V] | N | Y | Y | 270 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter | 0.23 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | Jinko Solar Co.,Ltd.0.23JKMS270M-60B-EP | 2017-11-01 | 2018-10-15
Jinko Solar Co.,Ltd. | JKMS275M-60B-EP [240V] | N | Y | Y | 275 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter | 0.23 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | Jinko Solar Co.,Ltd.0.23JKMS275M-60B-EP | 2017-11-01 | 2018-10-15
Jinko Solar Co.,Ltd. | JKMS275M-60-EP [240V] | N | Y | Y | 275 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter | 0.23 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | Jinko Solar Co.,Ltd.0.23JKMS275M-60-EP | 2017-11-01 | 2018-10-15
Jinko Solar Co.,Ltd. | JKMS280M-60B-EP [240V] | N | Y | Y | 280 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter | 0.23 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | Jinko Solar Co.,Ltd.0.23JKMS280M-60B-EP | 2017-11-01 | 2018-10-15
Jinko Solar Co.,Ltd. | JKMS280M-60-EP [240V] | N | Y | Y | 280 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter | 0.23 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | Jinko Solar Co.,Ltd.0.23JKMS280M-60-EP | 2017-11-01 | 2018-10-15
Jinko Solar Co.,Ltd. | JKMS285M-60B-EP [240V] | N | Y | Y | 285 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter | 0.23 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | Jinko Solar Co.,Ltd.0.23JKMS285M-60B-EP | 2017-11-01 | 2018-10-15
Jinko Solar Co.,Ltd. | JKMS285M-60-EP [240V] | N | Y | Y | 285 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter | 0.23 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | Jinko Solar Co.,Ltd.0.23JKMS285M-60-EP | 2017-11-01 | 2018-10-15
Jinko Solar Co.,Ltd. | JKMS290M-60B-EP [240V] | N | Y | Y | 290 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter | 0.23 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | Jinko Solar Co.,Ltd.0.23JKMS290M-60B-EP | 2017-11-01 | 2018-10-15
Jinko Solar Co.,Ltd. | JKMS290M-60-EP [240V] | N | Y | Y | 290 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter | 0.23 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | Jinko Solar Co.,Ltd.0.23JKMS290M-60-EP | 2017-11-01 | 2018-10-15
Jinko Solar Co.,Ltd. | JKMS295M-60B-EP [240V] | N | Y | Y | 295 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter | 0.23 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | Jinko Solar Co.,Ltd.0.23JKMS295M-60B-EP | 2017-11-01 | 2018-10-15
Jinko Solar Co.,Ltd. | JKMS295M-60-EP [240V] | N | Y | Y | 295 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter | 0.23 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | Jinko Solar Co.,Ltd.0.23JKMS295M-60-EP | 2017-11-01 | 2018-10-15
Jinko Solar Co.,Ltd. | JKMS300M-60-EP [240V] | N | Y | Y | 300 W DC, ACPV module with Enphase IQ6-60-ACM-US (240V) Microinverter | 0.23 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This microinverter is sold as an individual unit but is only for ACPV modules | 0.03 |  |  | 27 | 32 | 37 | 0.023 | 0.046 | 0.069 | 0.115 | 0.1725 | 0.23 | 94.6552 | 96.0377 | 96.6656 | 97.4237 | 97.4849 | 97.2559 | 97.1768 | 95.0606 | 96.3568 | 96.7065 | 97.3927 | 97.5863 | 97.5296 | 97.2747 | 94.745 | 96.1054 | 96.4314 | 97.1967 | 97.4693 | 97.4835 | 97.1111 | Jinko Solar Co.,Ltd.0.23JKMS300M-60-EP | 2017-11-01 | 2018-10-15
KACO | blueplanet Ultraverter 250 | Y | N | N | 250 W Utility Interactive Inverter with the Ultraverter system from 2 to 9 kW | 0.25 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0 |  |  | 29 | 35 | 45 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 92.1 | 96.2 | 97 | 97.4 | 97.2 | 96.8 | 97 | 93.1 | 96.4 | 97.3 | 97.7 | 97.6 | 97.3 | 97.3 | 93 | 96.6 | 97.6 | 98 | 97.9 | 97.7 | 97.6 | KACO0.25blueplanet Ultraverter 250
KACO | blueplanet 1501xi [240V] | Y | N | N | 1.5 kW, 240 Vac, 125-400 Vdc Utility Interactive Inverter | 1.5 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.29 |  |  | 100 | 195 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.125 | 1.5 | 92.6 | 95.1 | 95.5 | 95.5 | 95.2 | 94.4 | 95.1 | 92.4 | 94.7 | 95.1 | 95.3 | 94.9 | 94.2 | 94.9 | 93.5 | 94.6 | 94.7 | 94.8 | 94.5 | 93.8 | 94.5 | KACO1.5blueplanet 1501xi [240V]
KACO | blueplanet 1502x [208V] | Y | N | N | 1.5 kW, 208 Vac, Utility Interactive Inverter | 1.5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.39 |  |  | 100 | 195 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.125 | 1.5 | 92.6 | 95.3 | 95.8 | 95.9 | 95.5 | 95 | 95.5 | 93.2 | 95 | 95.6 | 95.7 | 95.4 | 94.9 | 95.4 | 93.4 | 94.7 | 95.1 | 95.3 | 95 | 94.5 | 95 | KACO1.5blueplanet 1502x [208V]
KACO | blueplanet 1502xi [208V] | Y | N | N | 1.5 kW, 208 Vac, 125-500 Vdc Utility Interactive Inverter | 1.5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.39 |  |  | 100 | 195 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.125 | 1.5 | 92.6 | 95.3 | 95.8 | 95.9 | 95.5 | 95 | 95.5 | 93.2 | 95 | 95.6 | 95.7 | 95.4 | 94.9 | 95.4 | 93.4 | 94.7 | 95.1 | 95.3 | 95 | 94.5 | 95 | KACO1.5blueplanet 1502xi [208V]
KACO | blueplanet 1502x [240V] | Y | N | N | 1.5 kW, 240 Vac, Utility Interactive Inverter | 1.67 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.63 |  |  | 100 | 175 | 300 | 0.17 | 0.33 | 0.5 | 0.83 | 1.25 | 1.67 | 91.5 | 94.3 | 94.8 | 94.7 | 94.3 | 93.5 | 94.3 | 91.6 | 94.2 | 94.7 | 94.5 | 94.3 | 93.5 | 94.3 | 90.7 | 93.4 | 94.1 | 94 | 93.8 | 93.2 | 93.7 | KACO1.67blueplanet 1502x [240V]
KACO | blueplanet 1502xi [240V] | Y | N | N | 1.5 kW, 240 Vac, 125-500 Vdc Utility Interactive Inverter | 1.67 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.63 |  |  | 100 | 175 | 300 | 0.17 | 0.33 | 0.5 | 0.83 | 1.25 | 1.67 | 91.5 | 94.3 | 94.8 | 94.7 | 94.3 | 93.5 | 94.3 | 91.6 | 94.2 | 94.7 | 94.5 | 94.3 | 93.5 | 94.3 | 90.7 | 93.4 | 94.1 | 94 | 93.8 | 93.2 | 93.7 | KACO1.67blueplanet 1502xi [240V]
KACO | blueplanet 2.0 TL1 M1 WM OD US3x [208V] | Y | N | N | 2.0 kW Utility Interactive Inverter (208V), x may be 3, 8, 9, A, C or D | 2.04 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.67 |  |  | 100 | 390 | 510 | 0.2 | 0.41 | 0.61 | 1.02 | 1.53 | 2.04 | 90.7 | 94.3 | 95.4 | 96.2 | 96.3 | 96 | 95.8 | 91.3 | 94.8 | 96.1 | 96.8 | 97 | 96.9 | 96.5 | 89.6 | 94.4 | 95.7 | 96.5 | 96.8 | 96.8 | 96.2 | KACO2.04blueplanet 2.0 TL1 M1 WM OD US3x [208V]
KACO | blueplanet 2.0 TL1 M1 WM OD US3x [240V] | Y | N | N | 2.0 kW Utility Interactive Inverter (240V), x may be 3, 8, 9, A, C or D | 2.07 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.66 |  |  | 100 | 390 | 510 | 0.21 | 0.41 | 0.62 | 1.04 | 1.55 | 2.07 | 89.7 | 94.2 | 95.3 | 96.2 | 96.4 | 96 | 95.8 | 91.4 | 95.3 | 96.2 | 97 | 97.3 | 96.5 | 96.7 | 89.6 | 94.5 | 95.8 | 96.8 | 97.1 | 97.2 | 96.5 | KACO2.07blueplanet 2.0 TL1 M1 WM OD US3x [240V]
KACO | blueplanet 2502x [208V] | Y | N | N | 2.5 kW, 208 Vac, Utility Interactive Inverter | 2.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.29 |  |  | 100 | 265 | 450 | 0.25 | 0.5 | 0.75 | 1.25 | 1.875 | 2.5 | 93.1 | 95.3 | 95.6 | 95.6 | 95.3 | 94.7 | 95.3 | 93.5 | 95 | 95.4 | 95.5 | 95.2 | 94.6 | 95.2 | 94.1 | 94.5 | 94.9 | 95 | 94.7 | 94.2 | 94.7 | KACO2.5blueplanet 2502x [208V]
KACO | blueplanet 2502x [240V] | Y | N | N | 2.5 kW, 240 Vac, Utility Interactive Inverter | 2.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.39 |  |  | 100 | 265 | 450 | 0.25 | 0.5 | 0.75 | 1.25 | 1.875 | 2.5 | 93.2 | 95.5 | 95.9 | 95.9 | 95.6 | 95.1 | 95.6 | 93.6 | 95.2 | 95.7 | 95.8 | 95.6 | 95 | 95.5 | 94.2 | 94.7 | 95.1 | 95.3 | 95.1 | 94.6 | 95 | KACO2.5blueplanet 2502x [240V]
KACO | blueplanet 2502xi [208V] | Y | N | N | 2.5 kW, 208 Vac, 125-500 Vdc Utility Interactive Inverter | 2.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.29 |  |  | 100 | 265 | 450 | 0.25 | 0.5 | 0.75 | 1.25 | 1.875 | 2.5 | 93.1 | 95.3 | 95.6 | 95.6 | 95.3 | 94.7 | 95.3 | 93.5 | 95 | 95.4 | 95.5 | 95.2 | 94.6 | 95.2 | 94.1 | 94.5 | 94.9 | 95 | 94.7 | 94.2 | 94.7 | KACO2.5blueplanet 2502xi [208V]
KACO | blueplanet 2502xi [240V] | Y | N | N | 2.5 kW, 240 Vac, 125-500 Vdc Utility Interactive Inverter | 2.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.39 |  |  | 100 | 265 | 450 | 0.25 | 0.5 | 0.75 | 1.25 | 1.875 | 2.5 | 93.2 | 95.5 | 95.9 | 95.9 | 95.6 | 95.1 | 95.6 | 93.6 | 95.2 | 95.7 | 95.8 | 95.6 | 95 | 95.5 | 94.2 | 94.7 | 95.1 | 95.3 | 95.1 | 94.6 | 95 | KACO2.5blueplanet 2502xi [240V]
KACO | blueplanet 2901xi [240V] | Y | N | N | 2.9 kW, 240 Vac, 125-400 Vdc Utility Interactive Inverter | 2.86 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.77 |  |  | 100 | 175 | 300 | 0.29 | 0.57 | 0.86 | 1.43 | 2.15 | 2.86 | 91.1 | 94.1 | 94.5 | 94.7 | 94.1 | 93.3 | 94.1 | 90.5 | 93.7 | 94.3 | 94.5 | 93.8 | 93 | 93.8 | 90.6 | 93.2 | 94.3 | 93.9 | 93.2 | 92.5 | 93.4 | KACO2.86blueplanet 2901xi [240V]
KACO | blueplanet 3.0 TL1 M1 WM OD US3x [208V] | Y | N | N | 3.0 kW Utility Interactive Inverter (208V), x may be 3, 8, 9, A, C or D | 3.05 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.42 |  |  | 100 | 390 | 510 | 0.3 | 0.61 | 0.91 | 1.52 | 2.29 | 3.05 | 92 | 94.7 | 95.6 | 95.9 | 95.7 | 95.3 | 95.5 | 93.4 | 95.9 | 96.6 | 97 | 96.9 | 96.7 | 96.7 | 92.3 | 95.5 | 96.2 | 96.7 | 96.7 | 96.5 | 96.4 | KACO3.05blueplanet 3.0 TL1 M1 WM OD US3x [208V]
KACO | blueplanet 3.0 TL1 M1 WM OD US3x [240V] | Y | N | N | 3.0 kW Utility Interactive Inverter (240V), x may be 3, 8, 9, A, C or D | 3.12 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.64 |  |  | 100 | 390 | 510 | 0.31 | 0.62 | 0.94 | 1.56 | 2.34 | 3.12 | 91.4 | 94.5 | 95.5 | 96 | 95.9 | 95.6 | 95.6 | 93.6 | 96 | 96.7 | 97.3 | 97.3 | 96.8 | 97 | 92.2 | 95.5 | 96.4 | 97 | 97.2 | 97 | 96.7 | KACO3.12blueplanet 3.0 TL1 M1 WM OD US3x [240V]
KACO | blueplanet 3502x [208V] | Y | N | N | 3.5 kW, 208 Vac, Utility Interactive with or without integrated wireway | 3.5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 280 | 510 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 93.5 | 95.5 | 95.9 | 95.9 | 95.6 | 95.2 | 95.6 | 93 | 95.1 | 95.6 | 95.7 | 95.5 | 95 | 95.4 | 91.7 | 94.2 | 94.8 | 95.1 | 95.1 | 94.8 | 94.9 | KACO3.5blueplanet 3502x [208V]
KACO | blueplanet 3502x [240V] | Y | N | N | 3.5 kW, 240 Vac, Utility Interactive with or without integrated wireway | 3.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 280 | 510 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 93.5 | 95.7 | 96.2 | 96.2 | 96 | 95.6 | 95.9 | 93 | 95.3 | 95.8 | 96 | 95.8 | 95.4 | 95.7 | 91.6 | 94.4 | 95.1 | 95.3 | 95.4 | 95.1 | 95.1 | KACO3.5blueplanet 3502x [240V]
KACO | blueplanet 3502xi [208V] | Y | N | N | 3.5 kW, 208 Vac, 200-600 Vdc Utility Interactive Inverter | 3.5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 280 | 510 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 93.5 | 95.5 | 95.9 | 95.9 | 95.6 | 95.2 | 95.6 | 93 | 95.1 | 95.6 | 95.7 | 95.5 | 95 | 95.4 | 91.7 | 94.2 | 94.8 | 95.1 | 95.1 | 94.8 | 94.9 | KACO3.5blueplanet 3502xi [208V]
KACO | blueplanet 3502xi [240V] | Y | N | N | 3.5 kW, 240 Vac, 200-600 Vdc Utility Interactive Inverter | 3.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 280 | 510 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 93.5 | 95.7 | 96.2 | 96.2 | 96 | 95.6 | 95.9 | 93 | 95.3 | 95.8 | 96 | 95.8 | 95.4 | 95.7 | 91.6 | 94.4 | 95.1 | 95.3 | 95.4 | 95.1 | 95.1 | KACO3.5blueplanet 3502xi [240V]
KACO | blueplanet 3601xi [240V] | Y | N | N | 3.6 kW, 240 Vac, Utility Interactive Inverter | 3.6 | 240 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.11 |  |  | 100 | 175 | 300 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 89.9 | 93.3 | 94.2 | 94.3 | 94 | 93.3 | 93.8 | 89.7 | 93.1 | 94.1 | 94.2 | 93.9 | 93.2 | 93.7 | 89 | 92.4 | 93.5 | 93.8 | 93.6 | 92.9 | 93.3 | KACO3.6blueplanet 3601xi [240V]
KACO | blueplanet 4.0 TL1 M1 WM OD US3x [208V] | Y | N | N | 4.0 kW Utility Interactive Inverter (208V), x may be 3, 8, 9, A, C or D | 4.06 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.53 |  |  | 100 | 390 | 510 | 0.41 | 0.81 | 1.22 | 2.03 | 3.05 | 4.06 | 93 | 95.4 | 96 | 96.3 | 96 | 95.6 | 95.9 | 93.7 | 96 | 96.6 | 96.9 | 96.8 | 96.5 | 96.6 | 92.5 | 95.3 | 96.1 | 96.6 | 96.6 | 96.3 | 96.3 | KACO4.06blueplanet 4.0 TL1 M1 WM OD US3x [208V]
KACO | blueplanet 4.0 TL1 M1 WM OD US3x [240V] | Y | N | N | 4.0 kW Utility Interactive Inverter (240V), x may be 3, 8, 9, A, C or D | 4.15 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.65 |  |  | 100 | 390 | 510 | 0.42 | 0.83 | 1.25 | 2.08 | 3.11 | 4.15 | 92.7 | 95.4 | 95.9 | 96.4 | 96.3 | 96 | 96 | 94.3 | 96.3 | 96.9 | 97.3 | 97.3 | 96.6 | 97 | 92.8 | 95.8 | 96.4 | 96.9 | 97 | 96.7 | 96.7 | KACO4.15blueplanet 4.0 TL1 M1 WM OD US3x [240V]
KACO | blueplanet 5.0 TL1 M1 WM OD US3x [208V] | Y | N | N | 5.0 kW Utility Interactive Inverter (208V), x may be 3, 8, 9, A, C or D | 4.65 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.58 |  |  | 100 | 390 | 510 | 0.47 | 0.93 | 1.4 | 2.33 | 3.49 | 4.65 | 93.6 | 95.8 | 96.2 | 96.4 | 96 | 95.4 | 96 | 94.4 | 96.3 | 96.8 | 96.9 | 96.6 | 96.2 | 96.6 | 93.4 | 95.7 | 96.3 | 96.6 | 96.4 | 96.1 | 96.3 | KACO4.65blueplanet 5.0 TL1 M1 WM OD US3x [208V]
KACO | blueplanet 5002x [208V] | Y | N | N | 5 kW, 208 Vac, Utility Interactive with or without integrated wireway | 5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 280 | 510 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 94.3 | 95.8 | 96 | 95.7 | 95.2 | 94.4 | 95.3 | 94 | 95.5 | 95.8 | 95.6 | 95.1 | 94.3 | 95.2 | 92.7 | 94.6 | 95 | 95.2 | 94.8 | 94.1 | 94.8 | KACO5blueplanet 5002x [208V]
KACO | blueplanet 5002x [240V] | Y | N | N | 5 kW, 240 Vac, Utility Interactive with or without integrated wireway | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 280 | 510 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 94.6 | 96.2 | 96.3 | 96.1 | 95.6 | 94.9 | 95.7 | 94.4 | 95.8 | 96 | 95.9 | 95.5 | 94.9 | 95.6 | 93.2 | 94.9 | 95.3 | 95.6 | 95.2 | 94.6 | 95.2 | KACO5blueplanet 5002x [240V]
KACO | blueplanet 5002xi [208V] | Y | N | N | 5 kW, 208 Vac, 200-600 Vdc Utility Interactive Inverter | 5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 280 | 510 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 94.3 | 95.8 | 96 | 95.7 | 95.2 | 94.4 | 95.3 | 94 | 95.5 | 95.8 | 95.6 | 95.1 | 94.3 | 95.2 | 92.7 | 94.6 | 95 | 95.2 | 94.8 | 94.1 | 94.8 | KACO5blueplanet 5002xi [208V]
KACO | blueplanet 5002xi [240V] | Y | N | N | 5 kW, 240 Vac, 200-600 Vdc Utility Interactive Inverter | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 280 | 510 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 94.6 | 96.2 | 96.3 | 96.1 | 95.6 | 94.9 | 95.7 | 94.4 | 95.8 | 96 | 95.9 | 95.5 | 94.9 | 95.6 | 93.2 | 94.9 | 95.3 | 95.6 | 95.2 | 94.6 | 95.2 | KACO5blueplanet 5002xi [240V]
KACO | blueplanet 5.0 TL1 M1 WM OD US3x [240V] | Y | N | N | 5.0 kW Utility Interactive Inverter (240V), x may be 3, 8, 9, A, C or D | 5.17 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.44 |  |  | 100 | 390 | 510 | 0.52 | 1.03 | 1.55 | 2.58 | 3.88 | 5.17 | 94 | 95.8 | 96.4 | 96.6 | 96.2 | 95.9 | 96.2 | 95.2 | 96.8 | 97.2 | 97.3 | 97.1 | 96.3 | 97 | 94 | 96.1 | 96.8 | 97.1 | 96.9 | 96.6 | 96.8 | KACO5.17blueplanet 5.0 TL1 M1 WM OD US3x [240V]
KACO | blueplanet 6400M [208V] | Y | N | N | 6.4 kW 208 Vac Utility Interactive Inverter with Tigo Management Unit | 6.4 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 369 | 510 | 0.64 | 1.28 | 1.92 | 3.2 | 4.8 | 6.4 | 94.4 | 96.6 | 96.9 | 97 | 96.9 | 96.6 | 96.8 | 93.5 | 96.1 | 96.5 | 96.8 | 96.7 | 96.5 | 96.5 | 89.5 | 94.3 | 95.4 | 96.1 | 96.1 | 96 | 95.7 | KACO6.4blueplanet 6400M [208V]
KACO | blueplanet 6400M [240V] | Y | N | N | 6.4 kW 240 Vac Utility Interactive Inverter with Tigo Management Unit | 6.4 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.45 |  |  | 100 | 402 | 510 | 0.64 | 1.28 | 1.92 | 3.2 | 4.8 | 6.4 | 94.6 | 96.7 | 96.7 | 97.1 | 97.1 | 97 | 96.9 | 93.8 | 96.3 | 96.9 | 97.1 | 97.1 | 97 | 96.9 | 90 | 94.7 | 95.7 | 96.4 | 96.5 | 96.5 | 96.1 | KACO6.4blueplanet 6400M [240V]
KACO | blueplanet 6400x [208V] | Y | N | N | 6.4 kW, 208 Vac, Utility Interactive with or without integrated wireway | 6.4 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 369 | 510 | 0.64 | 1.28 | 1.92 | 3.2 | 4.8 | 6.4 | 94.4 | 96.6 | 96.9 | 97 | 96.9 | 96.6 | 96.8 | 93.5 | 96.1 | 96.5 | 96.8 | 96.7 | 96.5 | 96.5 | 89.5 | 94.3 | 95.4 | 96.1 | 96.1 | 96 | 95.7 | KACO6.4blueplanet 6400x [208V]
KACO | blueplanet 6400x [240V] | Y | N | N | 6.4 kW, 240 Vac, Utility Interactive with or without integrated wireway | 6.4 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.45 |  |  | 100 | 402 | 510 | 0.64 | 1.28 | 1.92 | 3.2 | 4.8 | 6.4 | 94.6 | 96.7 | 96.7 | 97.1 | 97.1 | 97 | 96.9 | 93.8 | 96.3 | 96.9 | 97.1 | 97.1 | 97 | 96.9 | 90 | 94.7 | 95.7 | 96.4 | 96.5 | 96.5 | 96.1 | KACO6.4blueplanet 6400x [240V]
KACO | blueplanet 6400xi [208V] | Y | N | N | 6.4 kW, 208 Vac, Utility Interactive Inverter | 6.4 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 369 | 510 | 0.64 | 1.28 | 1.92 | 3.2 | 4.8 | 6.4 | 94.4 | 96.6 | 96.9 | 97 | 96.9 | 96.6 | 96.8 | 93.5 | 96.1 | 96.5 | 96.8 | 96.7 | 96.5 | 96.5 | 89.5 | 94.3 | 95.4 | 96.1 | 96.1 | 96 | 95.7 | KACO6.4blueplanet 6400xi [208V]
KACO | blueplanet 6400xi [240V] | Y | N | N | 6.4 kW, 240 Vac, Utility Interactive Inverter | 6.4 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.45 |  |  | 100 | 402 | 510 | 0.64 | 1.28 | 1.92 | 3.2 | 4.8 | 6.4 | 94.6 | 96.7 | 96.7 | 97.1 | 97.1 | 97 | 96.9 | 93.8 | 96.3 | 96.9 | 97.1 | 97.1 | 97 | 96.9 | 90 | 94.7 | 95.7 | 96.4 | 96.5 | 96.5 | 96.1 | KACO6.4blueplanet 6400xi [240V]
KACO | blueplanet 7600M [208V] | Y | N | N | 7.6 kW 208 Vac Utility Interactive Inverter with Tigo Management Unit | 7.6 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 369 | 510 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.1 | 96.7 | 97 | 96.9 | 96.7 | 96.4 | 96.7 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.5 | 90.9 | 94.9 | 95.7 | 96.1 | 96.1 | 95.8 | 95.7 | KACO7.6blueplanet 7600M [208V]
KACO | blueplanet 7600M [240V] | Y | N | N | 7.6 kW 240 Vac Utility Interactive Inverter with Tigo Management Unit | 7.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 402 | 510 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 94.7 | 96.8 | 97.1 | 97.1 | 97 | 96.7 | 96.9 | 94 | 96.5 | 96.9 | 97 | 96.9 | 96.6 | 96.8 | 91.4 | 95.3 | 96.1 | 96.4 | 96.4 | 96.3 | 96.1 | KACO7.6blueplanet 7600M [240V]
KACO | blueplanet 7600x [208V] | Y | N | N | 7.6 kW, 208 Vac, Utility Interactive with or without integrated wireway | 7.6 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 369 | 510 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.1 | 96.7 | 97 | 96.9 | 96.7 | 96.4 | 96.7 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.5 | 90.9 | 94.9 | 95.7 | 96.1 | 96.1 | 95.8 | 95.7 | KACO7.6blueplanet 7600x [208V]
KACO | blueplanet 7600x [240V] | Y | N | N | 7.6 kW, 240 Vac, Utility Interactive with or without integrated wireway | 7.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 402 | 510 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 94.7 | 96.8 | 97.1 | 97.1 | 97 | 96.7 | 96.9 | 94 | 96.5 | 96.9 | 97 | 96.9 | 96.6 | 96.8 | 91.4 | 95.3 | 96.1 | 96.4 | 96.4 | 96.3 | 96.1 | KACO7.6blueplanet 7600x [240V]
KACO | blueplanet 7600xi [208V] | Y | N | N | 7.6 kW, 208 Vac, Utility Interactive Inverter | 7.6 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 369 | 510 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.1 | 96.7 | 97 | 96.9 | 96.7 | 96.4 | 96.7 | 94.3 | 96.3 | 96.7 | 96.8 | 96.6 | 96.3 | 96.5 | 90.9 | 94.9 | 95.7 | 96.1 | 96.1 | 95.8 | 95.7 | KACO7.6blueplanet 7600xi [208V]
KACO | blueplanet 7600xi [240V] | Y | N | N | 7.6 kW, 240 Vac, Utility Interactive Inverter | 7.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 402 | 510 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 94.7 | 96.8 | 97.1 | 97.1 | 97 | 96.7 | 96.9 | 94 | 96.5 | 96.9 | 97 | 96.9 | 96.6 | 96.8 | 91.4 | 95.3 | 96.1 | 96.4 | 96.4 | 96.3 | 96.1 | KACO7.6blueplanet 7600xi [240V]
KACO | blueplanet 10.0 TL3 [480V] | Y | N | N | 10 kW, 480 Vac, Utility Interactive Inverter, 280-600 Vdc input, 2x MPPT channel | 9.99 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.59 |  |  | 100 | 430 | 480 | 1 | 2 | 3 | 4.99 | 7.49 | 9.99 | 93.7 | 95.9 | 96.3 | 96.6 | 96.5 | 96.2 | 96.3 | 93.8 | 96.2 | 96.9 | 97.2 | 97.2 | 97.1 | 97 | 94.3 | 96.4 | 96.9 | 97.3 | 97.3 | 97.2 | 97.1 | KACO9.99blueplanet 10.0 TL3 [480V]
KACO | XP10U-H4 (-PSD) [480V] | Y | N | N | 10 kW, 600 Vdc, 480 Vac, 3-phase Utility Interactive Inverter | 9.99 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.59 |  |  | 100 | 430 | 480 | 1 | 2 | 3 | 4.99 | 7.49 | 9.99 | 93.7 | 95.9 | 96.3 | 96.6 | 96.5 | 96.2 | 96.3 | 93.8 | 96.2 | 96.9 | 97.2 | 97.2 | 97.1 | 97 | 94.3 | 96.4 | 96.9 | 97.3 | 97.3 | 97.2 | 97.1 | KACO9.99XP10U-H4 (-PSD) [480V]
KACO | blueplanet 32.0 TL3 M1 [480V] | Y | N | N | 32 kW, 600 Vdc, 480 Vac, Utility Interactive Inverter | 32 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.42 |  |  | 310 | 530 | 600 | 3.2 | 6.4 | 9.6 | 16 | 24 | 32 | 94.2 | 95.6 | 96.2 | 96.5 | 96.4 | 96.2 | 96.3 | 97.6 | 98 | 98 | 98 | 97.8 | 97.6 | 97.9 | 96 | 96.9 | 97.3 | 97.6 | 97.6 | 97.5 | 97.5 | KACO32blueplanet 32.0 TL3 M1 [480V]
KACO | blueplanet 32.0 TL3 M3 [480V] | Y | N | N | 32 kW, 600 Vdc, 480 Vac, 3-phase, Utility Interactive Inverte,r 3 MPPT | 32 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.42 |  |  | 310 | 530 | 600 | 3.2 | 6.4 | 9.6 | 16 | 24 | 32 | 94.2 | 95.6 | 96.2 | 96.5 | 96.4 | 96.2 | 96.3 | 97.6 | 98 | 98 | 98 | 97.8 | 97.6 | 97.9 | 96 | 96.9 | 97.3 | 97.6 | 97.6 | 97.5 | 97.5 | KACO32blueplanet 32.0 TL3 M3 [480V]
KACO | blueplanet 40.0 TL3 M1 [480V] | Y | N | N | 40 kW, 1000 Vdc, 480 Vac 3-phase, Utility Interactive Inverter | 40 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.42 |  |  | 390 | 760 | 850 | 4 | 8 | 12 | 20 | 30 | 40 | 95.2 | 96.4 | 96.8 | 97 | 96.8 | 96.5 | 96.8 | 97.1 | 97.5 | 97.7 | 97.7 | 97.8 | 97.6 | 97.7 | 96.6 | 97 | 97.4 | 97.7 | 97.8 | 97.7 | 97.6 | KACO40blueplanet 40.0 TL3 M1 [480V]
KACO | blueplanet 40.0 TL3 M3 [480V] | Y | N | N | 40 kW, 1000 Vdc, 480 Vac, 3-phase Utility Interactive Inverter, 3 MPPT | 40 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.42 |  |  | 390 | 760 | 850 | 4 | 8 | 12 | 20 | 30 | 40 | 95.2 | 96.4 | 96.8 | 97 | 96.8 | 96.5 | 96.8 | 97.1 | 97.5 | 97.7 | 97.7 | 97.8 | 97.6 | 97.7 | 96.6 | 97 | 97.4 | 97.7 | 97.8 | 97.7 | 97.6 | KACO40blueplanet 40.0 TL3 M3 [480V]
KACO | XP42U-H2 [208V] | Y | N | N | 42 kW, 208 Vac, 3-phase Utility Interactive Inverter | 41.35 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 48.27 |  |  | 250 | 307.5 | 480 | 4.14 | 8.27 | 12.41 | 20.68 | 31.01 | 41.35 | 92 | 95 | 95.9 | 96.2 | 96.2 | 95.8 | 95.9 | 91.1 | 94.7 | 95.6 | 96 | 96.1 | 95.8 | 95.7 | 88.9 | 93.3 | 94.6 | 95.3 | 95.3 | 95.3 | 94.9 | KACO41.35XP42U-H2 [208V]
KACO | blueplanet 50.0 TL3 M1 [480V] | Y | N | N | 50 kW, 1000 Vdc, 480 Vac, 3-phase Utility Interactive Inverter | 51.28 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.42 |  |  | 480 | 760 | 850 | 5.13 | 10.26 | 15.38 | 25.64 | 38.46 | 51.28 | 95.4 | 97.4 | 97.6 | 97.5 | 97.1 | 96.8 | 97.2 | 95.6 | 97.3 | 97.7 | 98 | 98.1 | 97.6 | 97.9 | 98.3 | 98.4 | 98.2 | 98.1 | 97.9 | 97.7 | 98 | KACO51.28blueplanet 50.0 TL3 M1 [480V]
KACO | blueplanet 50.0 TL3 M3 [480V] | Y | N | N | 50 kW, 1000 Vdc, 480 Vac, 3-phase Utility Interactive Inverter, 3 MPPT | 51.28 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.42 |  |  | 480 | 760 | 850 | 5.13 | 10.26 | 15.38 | 25.64 | 38.46 | 51.28 | 95.4 | 97.4 | 97.6 | 97.5 | 97.1 | 96.8 | 97.2 | 95.6 | 97.3 | 97.7 | 98 | 98.1 | 97.6 | 97.9 | 98.3 | 98.4 | 98.2 | 98.1 | 97.9 | 97.7 | 98 | KACO51.28blueplanet 50.0 TL3 M3 [480V]
KACO | XP50U-H4 [480V] | Y | N | N | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter | 51.3 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 44.68 |  |  | 300 | 345 | 480 | 5.13 | 10.26 | 15.39 | 25.65 | 38.48 | 51.3 | 91.9 | 95.3 | 96.1 | 96.7 | 96.6 | 96.3 | 96.3 | 91.6 | 95 | 95.9 | 96.4 | 96.4 | 96.2 | 96.1 | 89.6 | 94 | 95.1 | 95.9 | 95.9 | 95.7 | 95.5 | KACO51.3XP50U-H4 [480V]
KACO | XP100U-H2 [480V] | Y | N | N | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 60.43 |  |  | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 93 | 95.3 | 95.9 | 96 | 95.8 | 95.4 | 95.7 | 91.5 | 94.8 | 95.7 | 96.2 | 96.1 | 95.8 | 95.8 | 88.5 | 93.6 | 94.8 | 95.5 | 95.7 | 95.5 | 95.2 | KACO100XP100U-H2 [480V]
KACO | XP100U-H4 [480V] | Y | N | N | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 61.75 |  |  | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 92.6 | 95.1 | 96 | 96.5 | 96.4 | 96.1 | 96.1 | 91.7 | 94.7 | 95.8 | 96.4 | 96.3 | 96.1 | 96 | 87.8 | 93.5 | 94.8 | 95.7 | 95.9 | 95.8 | 95.3 | KACO100XP100U-H4 [480V]
KACO | XP500U-TL | Y | N | N | 500 kW Utility Interactive Inverter | 500 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 108.4 |  |  | 550 | 613 | 800 | 50 | 100 | 150 | 250 | 375 | 500 | 97.4 | 98.3 | 98.4 | 98.4 | 98.3 | 98 | 98.3 | 96.9 | 98 | 98.2 | 98.2 | 98.1 | 97.9 | 98.1 | 95.5 | 97.3 | 97.7 | 97.8 | 97.7 | 97.6 | 97.6 | KACO500XP500U-TL
KACO | XP550U-TL | Y | N | N | 550 kW Utility Interactive Inverter | 550 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 108.6 |  |  | 550 | 613 | 800 | 55 | 110 | 165 | 275 | 412.5 | 550 | 97.5 | 98.3 | 98.4 | 98.4 | 98.2 | 97.9 | 98.3 | 97.1 | 98.1 | 98.1 | 98.2 | 98 | 97.6 | 98 | 95.8 | 97.4 | 97.7 | 97.7 | 97.6 | 97.4 | 97.6 | KACO550XP550U-TL
KACO | KACO blueplanet 750 TL3 750 TL3 M1 GM OD USX0 | Y | N | N | 750 kW Utility Interactive Inverter | 749.4 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 149 |  |  | 620 | 665 | 800 | 74.94 | 149.9 | 224.8 | 374.7 | 562.1 | 749.4 | 97.4 | 98.3 | 98.5 | 98.5 | 98.3 | 98.2 | 98.3 | 97.2 | 98.2 | 98.4 | 98.4 | 98.3 | 98.1 | 98.3 | 96.3 | 97.8 | 98 | 98.2 | 98.2 | 98 | 98.1 | KACO749.4KACO blueplanet 750 TL3 750 TL3 M1 GM OD USX0
KACO | KACO blueplanet 875 TL3 875 TL3 M1 GM OD USX0 | Y | N | N | 875 kW Utility Interactive Inverter | 874 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 148.7 |  |  | 620 | 665 | 800 | 87.4 | 174.8 | 262.2 | 437 | 655.5 | 874 | 97.7 | 98.4 | 98.5 | 98.6 | 98.3 | 98 | 98.3 | 97.4 | 98.2 | 98.4 | 98.4 | 98.3 | 97.9 | 98.3 | 96.8 | 97.9 | 98.2 | 98.2 | 98.2 | 97.9 | 98.1 | KACO874KACO blueplanet 875 TL3 875 TL3 M1 GM OD USX0
KACO | KACO blueplanet 1000 TL3 1000 TL3 M1 GM OD USX0 | Y | N | N | 1000 kW Utility Interactive Inverter | 1000 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 148.2 |  |  | 620 | 665 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 97.8 | 98.3 | 98.4 | 98.4 | 98.1 | 97.7 | 98.2 | 97.5 | 98.2 | 98.3 | 98.3 | 98.1 | 97.7 | 98.1 | 97 | 97.9 | 98.1 | 98.1 | 98 | 97.6 | 98 | KACO1000KACO blueplanet 1000 TL3 1000 TL3 M1 GM OD USX0
KACO | KACO blueplanet 1500 TL3 M1 GM OD USX0 | Y | N | N | 1500 kW Utility Interactive Inverter | 1500 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 180.91 |  |  | 580 | 635 | 800 | 150 | 300 | 450 | 750 | 1125 | 1500 | 96.9 | 98.1 | 98.2 | 98.2 | 98.1 | 97.8 | 98 | 96.5 | 97.8 | 98.1 | 98.1 | 98 | 97.7 | 98 | 95.1 | 97.2 | 97.6 | 97.8 | 97.8 | 97.6 | 97.6 | KACO1500KACO blueplanet 1500 TL3 M1 GM OD USX0
KACO | KACO blueplanet 2200 TL3 M1 GM OD USX0 | Y | N | N | 2200 kW Utility Interactive Inverter | 2000 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 176.74 |  |  | 580 | 635 | 800 | 200 | 400 | 600 | 1000 | 1500 | 2000 | 97.5 | 98.2 | 98.3 | 98.2 | 97.8 | 97.4 | 97.9 | 97.2 | 98.1 | 98.2 | 98.1 | 97.8 | 97.4 | 97.9 | 96.1 | 97.6 | 97.8 | 97.9 | 97.7 | 97.3 | 97.6 | KACO2000KACO blueplanet 2200 TL3 M1 GM OD USX0
Kostal Solar Electric | Piko 5.3 US | Y | N | N | 5.3 kW 3-phase Inverter | 5.3 |  | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.96 | 5.3 | 0.96 | 100 | 380 | 480 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 90.5 | 92.9 | 92.9 | 93.4 | 93.4 | 93.2 | 93.2 | 92.6 | 94.3 | 94.9 | 94.8 | 94.8 | 94.2 | 94.7 | 91.3 | 93.5 | 94.1 | 94.6 | 94.2 | 93.7 | 94.1 | Kostal Solar Electric5.3Piko 5.3 US
LeadSolar Energy Co., Ltd | LS560 [240V] | Y | N | N | 500 W, 1-phase Utility Interactive Inverter | 0.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.09 |  |  | 27 | 36 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.375 | 0.5 | 94.6 | 95.4 | 95.6 | 95.6 | 95.4 | 94.9 | 95.4 | 94.2 | 95.6 | 95.2 | 95.9 | 95.7 | 95.3 | 95.6 | 93.7 | 93.8 | 94.8 | 95.9 | 95.7 | 95.5 | 95.5 | LeadSolar Energy Co., Ltd0.5LS560 [240V] |  | 2018-09-04
LeadSolar Energy Co., Ltd | LS600 [240V] | Y | Y | Y | 500 W, 1-phase Grid Support Utility Interactive Inverter | 0.5 | 240 | 95.5 | [9/6/2017] | [V3.0] | 2018-10-15 | N | Y |  | 0.09 |  |  | 27 | 36 | 45 | 0.05 | 0.1 | 0.15 | 0.25 | 0.375 | 0.5 | 94.6 | 95.4 | 95.6 | 95.6 | 95.4 | 94.9 | 95.4 | 94.2 | 95.6 | 95.2 | 95.9 | 95.7 | 95.3 | 95.6 | 93.7 | 93.8 | 94.8 | 95.9 | 95.7 | 95.5 | 95.5 | LeadSolar Energy（Wuxi ）Co.,Ltd.0.5LS600 [SI1] | 2017-10-13 | 2018-10-15
LeadSolar Energy Co., Ltd | LS600T [208V] | Y | N | N | 500 W, 1-phase Utility Interactive Inverter | 0.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 1 |  |  | 27 | 36 | 45 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 93.6 | 95 | 95.1 | 95.3 | 94.7 | 93.8 | 94.8 | 93.7 | 94.2 | 95.1 | 95.7 | 95.5 | 95 | 95.3 | 93.2 | 93.2 | 94.9 | 95.7 | 95.8 | 95.4 | 95.4 | LeadSolar Energy Co., Ltd0.5LS600T [208V] |  | 2018-09-04
LeadSolar Energy Co., Ltd | LS600ES [277V] | Y | N | N | 0.6 kW, 277 Vac, 1-phase Utility Interactive Inverter | 0.6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 |  |  | 52 | 54 | 56 | 0.06 | 0.12 | 0.18 | 0.3 | 0.45 | 0.6 | 92.6 | 95.4 | 96.1 | 95.8 | 96.1 | 96.1 | 95.9 | 92.4 | 95.4 | 96 | 95.8 | 96.1 | 96.1 | 95.9 | 92.3 | 95.3 | 96 | 96 | 96.1 | 96.1 | 95.9 | LeadSolar Energy Co., Ltd0.6LS600ES [277V] |  | 2018-09-04
LeadSolar Energy Co., Ltd | LS700TS-208 [208V] | Y | N | N | 0.6 kW, 208 Vac, 1-phase Utility Interactive Inverter | 0.6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.21 |  |  | 52 | 54 | 56 | 0.06 | 0.12 | 0.18 | 0.3 | 0.45 | 0.6 | 91.2 | 94.3 | 94.9 | 95.5 | 95.6 | 95.3 | 95.2 | 90.1 | 93.7 | 95 | 95.7 | 95.8 | 95.5 | 95.3 | 90.2 | 93.9 | 95 | 95.4 | 95.8 | 95.6 | 95.3 | LeadSolar Energy Co., Ltd0.6LS700TS-208 [208V] |  | 2018-09-04
LeadSolar Energy Co., Ltd | LS650S [277V] | Y | N | N | 0.65 kW, 277 Vac, 1-phase Utility Interactive Inverter | 0.65 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 |  |  | 52 | 54 | 56 | 0.065 | 0.13 | 0.195 | 0.325 | 0.488 | 0.65 | 93 | 95.6 | 96.1 | 95.7 | 96.1 | 96 | 95.9 | 92.9 | 95.5 | 96.1 | 95.8 | 96.1 | 96.1 | 95.9 | 92.7 | 95.5 | 96.1 | 95.9 | 96.1 | 96.1 | 95.9 | LeadSolar Energy Co., Ltd0.65LS650S [277V] |  | 2018-09-04
LeadSolar Energy Co., Ltd | LS700S [277V] | Y | N | N | 0.7 kW, 277 Vac, 1-phase Utility Interactive Inverter | 0.7 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 |  |  | 52 | 54 | 56 | 0.07 | 0.14 | 0.21 | 0.35 | 0.525 | 0.7 | 93.4 | 95.7 | 96.1 | 95.4 | 96 | 95.8 | 95.8 | 93.2 | 95.7 | 96.2 | 95.5 | 96.1 | 96 | 95.8 | 93.1 | 95.6 | 96.2 | 95.8 | 96.1 | 96 | 95.9 | LeadSolar Energy Co., Ltd0.7LS700S [277V] |  | 2018-09-04
LeadSolar Energy Co., Ltd | LS700TS-240 [240V] | Y | N | N | 0.7 kW, 240 Vac, 1-phase Utility Interactive Inverter | 0.7 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.21 |  |  | 52 | 54 | 56 | 0.07 | 0.14 | 0.21 | 0.35 | 0.53 | 0.7 | 91.5 | 94.3 | 94.9 | 95.9 | 96 | 95.6 | 95.6 | 90.8 | 93.8 | 95.2 | 96 | 95.9 | 95.6 | 95.5 | 90.4 | 94.1 | 95.1 | 95.5 | 96 | 95.7 | 95.4 | LeadSolar Energy Co., Ltd0.7LS700TS-240 [240V] |  | 2018-09-04
LeadSolar Energy Co., Ltd | LS600X [240V] | N | Y | Y | 700 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.708 | 240 | 96 | [03/19/2018] | [V105LS700G2HV1.1_789Boot] | 2018-10-15 | N | Y |  | 0.16 |  |  | 50 | 57 | 64 | 0.0708 | 0.1416 | 0.2124 | 0.354 | 0.531 | 0.708 | 89.3868 | 93.5464 | 95.134 | 96.2627 | 96.5776 | 96.3824 | 95.8893 | 90.1881 | 93.8539 | 95.2694 | 96.306 | 96.5948 | 96.5453 | 95.9793 | 87.474 | 92.8944 | 95.0621 | 96.0676 | 96.4861 | 96.4858 | 95.6873 | LeadSolar Energy Co., Ltd0.708LS600X [240V] | 2018-04-16 | 2018-10-15
LeadSolar Energy Co.,Ltd | LS1400-240V [240V] | Y | N | N | 1400 W, 240 Vac Utility Interactive Micro Inverter | 1.4 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.13 |  |  | 37.5 | 40 | 44 | 0.14 | 0.28 | 0.42 | 0.7 | 1.05 | 1.4 | 91.8572 | 94.1762 | 94.9474 | 95.3395 | 95.2958 | 94.6945 | 95.0396 | 91.7584 | 94.1999 | 94.9268 | 95.3636 | 95.3473 | 94.8208 | 95.073 | 91.5513 | 94.2107 | 94.883 | 95.3302 | 95.3488 | 94.956 | 95.0606 | LeadSolar Energy Co.,Ltd1.4LS1400-240V [240V] | 2018-09-04
Leatec Fine Ceramics | CM21-0113 [240V] | Y | N | N | 300 W, 240 Vac, Utility Interactive Inverter | 0.286 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.1 |  |  | 26 | 31 | 43 | 0.03 | 0.06 | 0.09 | 0.14 | 0.22 | 0.29 | 92.1 | 94.4 | 95 | 95.7 | 96.3 | 95.9 | 95.7 | 91.6 | 95.1 | 94.8 | 96.5 | 96.5 | 96.5 | 96.1 | 89.9 | 94.3 | 95.3 | 96.3 | 96.2 | 96.2 | 95.8 | Leatec Fine Ceramics0.286CM21-0113 [240V]
LG Electronics Inc. | LG315E1K-A5 [208V] | Y | Y | Y | 315 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | LG Electronics Inc.0.28LG315E1K-A5 [208V] | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG315E1K-A5 [240V] | Y | Y | Y | 315 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | LG Electronics Inc.0.28LG315E1K-A5 [240V] | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG320E1K-A5 [208V] | Y | Y | Y | 320 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | LG Electronics Inc.0.28LG320E1K-A5 [208V] | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG320E1K-A5 [240V] | Y | Y | Y | 320 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | LG Electronics Inc.0.28LG320E1K-A5 [240V] | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG325E1C-A5 [208V] | Y | Y | Y | 325 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | LG Electronics Inc.0.28LG325E1C-A5 [208V] | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG325E1C-A5 [240V] | Y | Y | Y | 325 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | LG Electronics Inc.0.28LG325E1C-A5 [240V] | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG325E1K-A5 [208V] | Y | Y | Y | 325 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | LG Electronics Inc.0.28LG325E1K-A5 [208V] | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG325E1K-A5 [240V] | Y | Y | Y | 325 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.2531 | 96.1631 | 96.8171 | 97.3026 | 97.1456 | 96.7165 | 96.9529 | 94.5548 | 95.7444 | 96.2814 | 97.2549 | 97.3334 | 97.1701 | 96.9919 | 93.9059 | 95.0901 | 95.7449 | 96.972 | 97.1487 | 97.0384 | 96.705 | LG Electronics Inc.0.28LG325E1K-A5 [240V] | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG330E1C-A5 [208V] | Y | Y | Y | 330 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6361 | 96.3401 | 96.9302 | 97.3761 | 97.1425 | 96.5786 | 96.9975 | 94.5629 | 95.6844 | 96.451 | 97.1497 | 97.092 | 96.6838 | 96.8353 | 93.9289 | 95.0271 | 95.9707 | 96.9185 | 96.9131 | 96.595 | 96.5716 | LG Electronics Inc.0.28LG330E1C-A5 [208V] | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG330E1C-A5 [240V] | Y | Y | Y | 330 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.3 | 96.2 | 96.8 | 97.3 | 97.1 | 96.7 | 97 | 94.6 | 95.7 | 96.3 | 97.3 | 97.3 | 97.2 | 97 | 93.9 | 95.1 | 95.7 | 97 | 97.1 | 97 | 96.7 | LG Electronics Inc.0.28LG330E1C-A5 [240V] | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG335E1C-A5 [208V] | Y | Y | Y | 335 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 208 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.6 | 96.3 | 96.9 | 97.4 | 97.1 | 96.6 | 97 | 94.6 | 95.7 | 96.5 | 97.1 | 97.1 | 96.7 | 96.8 | 93.9 | 95 | 96 | 96.9 | 96.9 | 96.6 | 96.6 | LG Electronics Inc.0.28LG335E1C-A5 [208V] | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG335E1C-A5 [240V] | Y | Y | Y | 335 W DC, ACPV module with Enphase IQ6PLUS72-ACM-US Microinverter | 0.28 | 240 | 97 | [6/29/2017] | [01.06.03] | 2018-10-15 | N | Y | This model is specifically for the ACPV module. The microinverter is also sold as an individual unit. | 0.02 |  |  | 27 | 36 | 45 | 28 | 56 | 84 | 140 | 210 | 280 | 94.3 | 96.2 | 96.8 | 97.3 | 97.1 | 96.7 | 97 | 94.6 | 95.7 | 96.3 | 97.3 | 97.3 | 97.2 | 97 | 93.9 | 95.1 | 95.7 | 97 | 97.1 | 97 | 96.7 | LG Electronics Inc.0.28LG335E1C-A5 [240V] | 2017-08-01 | 2018-10-15
LG Electronics Inc. | LG295A1C-B3 [208V] | Y | N | N | 295W 208Vac Utility Interactive Microinverter | 0.29969 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 27 | 32 | 38 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.29969 | 93.8 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 93.7 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 96.2 | 93.4 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.3 | LG Electronics Inc.299.693LG295A1C-B3 (208V) |  | 2017-11-15
LG Electronics Inc. | LG295A1W-B3 [208V] | Y | N | N | 295W 208Vac Utility Interactive Microinverter | 0.29969 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 27 | 32 | 38 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.29969 | 93.8 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 93.7 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 96.2 | 93.4 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.3 | LG Electronics Inc.299.693 LG295A1W-B3 (208V) |  | 2017-11-15
LG Electronics Inc. | LG300A1C-B3 [208V] | Y | N | N | 300W 208Vac Utility Interactive Microinverter | 0.29969 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 27 | 32 | 38 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.29969 | 93.8 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 93.7 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 96.2 | 93.4 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.3 | LG Electronics Inc.299.693LG300A1C-B3 (208V) |  | 2017-11-15
LG Electronics Inc. | LG300A1W-B3 [208V] | Y | N | N | 300W 208Vac Utility Interactive Microinverter | 0.29969 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 27 | 32 | 38 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.29969 | 93.8 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 93.7 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 96.2 | 93.4 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.3 | LG Electronics Inc.299.693LG300A1W-B3 (208V) |  | 2017-11-15
LG Electronics Inc. | LG305A1C-B3 [208V] | Y | N | N | 305W 208Vac Utility Interactive Microinverter | 0.29969 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 27 | 32 | 38 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.29969 | 93.8 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 93.7 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 96.2 | 93.4 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.3 | LG Electronics Inc.299.693LG305A1C-B3 (208V) |  | 2017-11-15
LG Electronics Inc. | LG305A1W-B3 [208V] | Y | N | N | 305W 208Vac Utility Interactive Microinverter | 0.29969 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 27 | 32 | 38 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.29969 | 93.8 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 93.7 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 96.2 | 93.4 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.3 | LG Electronics Inc.299.693LG305A1W-B3 (208V) |  | 2017-11-15
LG Electronics Inc. | LM305UE-G1 [208V] | Y | N | N | 300W, 208 Vac Utility Interactive Microinverter | 0.29969 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.07 |  |  | 27 | 32 | 38 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.29969 | 93.8 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 93.7 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | 96.2 | 93.4 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.3 | LG Electronics Inc.299.693LM305UE-G1 (208V) |  | 2017-11-15
LG Electronics Inc. | LG295A1C-B3 [240V] | Y | N | N | 295W 240Vac Utility Interactive Microinverter | 0.30497 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.09 |  |  | 27 | 32 | 38 | 0.0305 | 0.061 | 0.0915 | 0.1525 | 0.22875 | 0.30497 | 93.7 | 95.6 | 96.2 | 96.5 | 96.3 | 95.9 | 96.2 | 93.5 | 95.5 | 96.3 | 96.5 | 96.5 | 96.3 | 96.3 | 93.2 | 95.3 | 96.3 | 96.6 | 96.7 | 96.5 | 96.4 | LG Electronics Inc.304.968LG295A1C-B3 (240V) |  | 2017-11-15
LG Electronics Inc. | LG295A1W-B3 [240V] | Y | N | N | 295W 240Vac Utility Interactive Microinverter | 0.30497 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.09 |  |  | 27 | 32 | 38 | 0.0305 | 0.061 | 0.0915 | 0.1525 | 0.22875 | 0.30497 | 93.7 | 95.6 | 96.2 | 96.5 | 96.3 | 95.9 | 96.2 | 93.5 | 95.5 | 96.3 | 96.5 | 96.5 | 96.3 | 96.3 | 93.2 | 95.3 | 96.3 | 96.6 | 96.7 | 96.5 | 96.4 | LG Electronics Inc.304.968LG295A1W-B3 (240V) |  | 2017-11-15
LG Electronics Inc. | LG300A1C-B3 [240V] | Y | N | N | 300W 240Vac Utility Interactive Microinverter | 0.30497 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.09 |  |  | 27 | 32 | 38 | 0.0305 | 0.061 | 0.0915 | 0.1525 | 0.22875 | 0.30497 | 93.7 | 95.6 | 96.2 | 96.5 | 96.3 | 95.9 | 96.2 | 93.5 | 95.5 | 96.3 | 96.5 | 96.5 | 96.3 | 96.3 | 93.2 | 95.3 | 96.3 | 96.6 | 96.7 | 96.5 | 96.4 | LG Electronics Inc.304.968LG300A1C-B3 (240V) |  | 2017-11-15
LG Electronics Inc. | LG300A1W-B3 [240V] | Y | N | N | 300W 240Vac Utility Interactive Microinverter | 0.30497 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.09 |  |  | 27 | 32 | 38 | 0.0305 | 0.061 | 0.0915 | 0.1525 | 0.22875 | 0.30497 | 93.7 | 95.6 | 96.2 | 96.5 | 96.3 | 95.9 | 96.2 | 93.5 | 95.5 | 96.3 | 96.5 | 96.5 | 96.3 | 96.3 | 93.2 | 95.3 | 96.3 | 96.6 | 96.7 | 96.5 | 96.4 | LG Electronics Inc.304.968LG300A1W-B3 (240V) |  | 2017-11-15
LG Electronics Inc. | LG305A1C-B3 [240V] | Y | N | N | 305W 240Vac Utility Interactive Microinve | 0.30497 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.09 |  |  | 27 | 32 | 38 | 0.0305 | 0.061 | 0.0915 | 0.1525 | 0.22875 | 0.30497 | 93.7 | 95.6 | 96.2 | 96.5 | 96.3 | 95.9 | 96.2 | 93.5 | 95.5 | 96.3 | 96.5 | 96.5 | 96.3 | 96.3 | 93.2 | 95.3 | 96.3 | 96.6 | 96.7 | 96.5 | 96.4 | LG Electronics Inc.304.968LG305A1C-B3 (240V) |  | 2017-11-15
LG Electronics Inc. | LG305A1W-B3 [240V] | Y | N | N | 305W 240Vac Utility Interactive Microinve | 0.30497 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.09 |  |  | 27 | 32 | 38 | 0.0305 | 0.061 | 0.0915 | 0.1525 | 0.22875 | 0.30497 | 93.7 | 95.6 | 96.2 | 96.5 | 96.3 | 95.9 | 96.2 | 93.5 | 95.5 | 96.3 | 96.5 | 96.5 | 96.3 | 96.3 | 93.2 | 95.3 | 96.3 | 96.6 | 96.7 | 96.5 | 96.4 | LG Electronics Inc.304.968LG305A1W-B3 (240V) |  | 2017-11-15
LG Electronics Inc. | LM305UE-G1 [240V] | Y | N | N | 305W, 240 Vac Utility Interactive Microinverter | 0.30497 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.09 |  |  | 27 | 32 | 38 | 0.0305 | 0.061 | 0.0915 | 0.1525 | 0.22875 | 0.30497 | 93.7 | 95.6 | 96.2 | 96.5 | 96.3 | 95.9 | 96.2 | 93.5 | 95.5 | 96.3 | 96.5 | 96.5 | 96.3 | 96.3 | 93.2 | 95.3 | 96.3 | 96.6 | 96.7 | 96.5 | 96.4 | LG Electronics Inc.304.968LM305UE-G1 (240V) |  | 2017-11-15
LG Electronics Inc. | LG355A1C-A5 [208V] | N | Y | N | 355 W, 208 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG355Q1C-A5. Microinverter: LM320UE-A2. | 0.32 | 208 | 96 | [12/15/2017] | [A320UD260C] | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.85 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 91.3 | 94.9 | 95.8 | 96.5 | 96.4 | 95.3 | 96 | 90.8 | 94.9 | 95.4 | 96.4 | 96.3 | 95.6 | 95.9 | 90.2 | 94.5 | 95.3 | 96.2 | 96.2 | 95.8 | 95.7 | LG Electronics Inc.0.32LG355A1C-A5 [208V] | 2018-02-15
LG Electronics Inc. | LG355A1C-A5 [240V] | N | Y | N | 355 W, 240 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG355Q1C-A5. Microinverter: LM320UE-A2. | 0.32 | 240 | 97 | [12/15/2017] | [A320UD260C] | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.16 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 92.6 | 95.9 | 96.6 | 97.2 | 97.2 | 96.8 | 96.9 | 92.6 | 95.9 | 96.6 | 97.1 | 97.2 | 96.8 | 96.8 | 92.1 | 95.6 | 96.4 | 96.9 | 97 | 96.8 | 96.6 | LG Electronics Inc.0.32LG355A1C-A5 [240V] | 2018-02-15
LG Electronics Inc. | LG360A1C-A5 [208V] | N | Y | N | 360 W, 208 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG360Q1C-A5. Microinverter: LM320UE-A2. | 0.32 | 208 | 96 | [12/15/2017] | [A320UD260C] | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.85 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 91.3 | 94.9 | 95.8 | 96.5 | 96.4 | 95.3 | 96 | 90.8 | 94.9 | 95.4 | 96.4 | 96.3 | 95.6 | 95.9 | 90.2 | 94.5 | 95.3 | 96.2 | 96.2 | 95.8 | 95.7 | LG Electronics Inc.0.32LG360A1C-A5 [208V] | 2018-02-15
LG Electronics Inc. | LG360A1C-A5 [240V] | N | Y | N | 360 W, 240 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG360Q1C-A5. Microinverter: LM320UE-A2. | 0.32 | 240 | 97 | [12/15/2017] | [A320UD260C] | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.16 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 92.6 | 95.9 | 96.6 | 97.2 | 97.2 | 96.8 | 96.9 | 92.6 | 95.9 | 96.6 | 97.1 | 97.2 | 96.8 | 96.8 | 92.1 | 95.6 | 96.4 | 96.9 | 97 | 96.8 | 96.6 | LG Electronics Inc.0.32LG360A1C-A5 [240V] | 2018-02-15
LG Electronics Inc. | LG365A1C-A5 [208V] | N | Y | N | 365 W, 208 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG365Q1C-A5. Microinverter: LM320UE-A2. | 0.32 | 208 | 96 | [12/15/2017] | [A320UD260C] | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.85 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 91.3 | 94.9 | 95.8 | 96.5 | 96.4 | 95.3 | 96 | 90.8 | 94.9 | 95.4 | 96.4 | 96.3 | 95.6 | 95.9 | 90.2 | 94.5 | 95.3 | 96.2 | 96.2 | 95.8 | 95.7 | LG Electronics Inc.0.32LG365A1C-A5 [208V] | 2018-02-15
LG Electronics Inc. | LG365A1C-A5 [240V] | N | Y | N | 365 W, 240 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG365Q1C-A5. Microinverter: LM320UE-A2. | 0.32 | 240 | 97 | [12/15/2017] | [A320UD260C] | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.16 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 92.6 | 95.9 | 96.6 | 97.2 | 97.2 | 96.8 | 96.9 | 92.6 | 95.9 | 96.6 | 97.1 | 97.2 | 96.8 | 96.8 | 92.1 | 95.6 | 96.4 | 96.9 | 97 | 96.8 | 96.6 | LG Electronics Inc.0.32LG365A1C-A5 [240V] | 2018-02-15
LG Electronics Inc. | LG370A1C-A5 [208V] | N | Y | N | 370 W, 208 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG370Q1C-A5. Microinverter: LM320UE-A2. | 0.32 | 208 | 96 | [12/15/2017] | [A320UD260C] | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.85 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 91.3 | 94.9 | 95.8 | 96.5 | 96.4 | 95.3 | 96 | 90.8 | 94.9 | 95.4 | 96.4 | 96.3 | 95.6 | 95.9 | 90.2 | 94.5 | 95.3 | 96.2 | 96.2 | 95.8 | 95.7 | LG Electronics Inc.0.32LG370A1C-A5 [208V] | 2018-02-15
LG Electronics Inc. | LG370A1C-A5 [240V] | N | Y | N | 370 W, 240 Vac Grid Support Utility Interactive, Monocrystalline ACPV module. DC Module: LG370Q1C-A5. Microinverter: LM320UE-A2. | 0.32 | 240 | 97 | [12/15/2017] | [A320UD260C] | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.16 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 92.6 | 95.9 | 96.6 | 97.2 | 97.2 | 96.8 | 96.9 | 92.6 | 95.9 | 96.6 | 97.1 | 97.2 | 96.8 | 96.8 | 92.1 | 95.6 | 96.4 | 96.9 | 97 | 96.8 | 96.6 | LG Electronics Inc.0.32LG370A1C-A5 [240V] | 2018-02-15
LG Electronics Inc. | LM320UE-A2 [208V] | N | Y | N | 320 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.32 | 208 | 96 | [01/04/2018] | [A320UD260C] | Not Applicable | N | Y |  | 0.85 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 91.3 | 94.9 | 95.8 | 96.5 | 96.4 | 95.3 | 96 | 90.8 | 94.9 | 95.4 | 96.4 | 96.3 | 95.6 | 95.9 | 90.2 | 94.5 | 95.3 | 96.2 | 96.2 | 95.8 | 95.7 | LG Electronics Inc.0.32LM320UE-A2 [208V] | 2018-02-15
LG Electronics Inc. | LM320UE-A2 [240V] | N | Y | N | 320 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.32 | 240 | 97 | [01/04/2018] | [A320UD260C] | Not Applicable | N | Y |  | 0.16 |  |  | 32 | 35 | 42 | 0.032 | 0.064 | 0.096 | 0.16 | 0.24 | 0.32 | 92.6 | 95.9 | 96.6 | 97.2 | 97.2 | 96.8 | 96.9 | 92.6 | 95.9 | 96.6 | 97.1 | 97.2 | 96.8 | 96.8 | 92.1 | 95.6 | 96.4 | 96.9 | 97 | 96.8 | 96.6 | LG Electronics Inc.0.32LM320UE-A2 [240V] | 2018-02-15
LG Electronics Inc. | A005KEEN261 [208V] | N | Y | Y | 5000 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Energy Storage Inverter | 5 | 208 | 98 | [08/30/2018] | [1.4.1] | 2018-10-15 | N | N |  | 1.85 |  |  | 350 | 400 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 96.3576 | 97.7104 | 98.1201 | 98.2082 | 98.0337 | 97.6876 | 97.9802 | 95.6974 | 97.377 | 97.8682 | 98.0571 | 97.92 | 97.611 | 97.8111 | 95.112 | 97.0074 | 97.61 | 97.87 | 97.8014 | 97.5053 | 97.6308 | LG Electronics Inc.5A005KEEN261 [208V] | 2018-10-01 | 2018-10-15
LG Electronics Inc. | A005KEEN261 [240V] | N | Y | Y | 5000 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode, Grid Support Utility Interactive Energy Storage Inverter | 5 | 240 | 98 | [08/30/2018] | [1.4.1] | 2018-10-15 | N | N |  | 2.05 |  |  | 350 | 400 | 450 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 96.4809 | 97.5846 | 98.1167 | 98.4736 | 98.3238 | 97.9351 | 98.2003 | 95.8938 | 97.5508 | 98.0084 | 98.4507 | 98.3503 | 98.1238 | 98.1808 | 95.244 | 97.1576 | 97.7531 | 98.2952 | 98.2453 | 98.0333 | 98.0117 | LG Electronics Inc.5A005KEEN261 [240V] | 2018-10-01 | 2018-10-15
LG Electronics Inc. | D007KEEN261 [208V] | N | Y | Y | 6656W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter | 6.656 | 208 | 97.5 | [08/30/2018] | [1.4.1] | 2018-10-15 | N | N |  | 1.15 |  |  | 270 | 380 | 450 | 0.6656 | 1.3312 | 1.9968 | 3.328 | 4.992 | 6.656 | 94.5771 | 96.3015 | 96.9963 | 97.3878 | 97.2948 | 96.929 | 97.1019 | 95.9053 | 97.3314 | 97.7633 | 97.8619 | 97.5862 | 97.2138 | 97.5667 | 95.0392 | 96.9541 | 97.466 | 97.7308 | 97.5103 | 97.1462 | 97.4064 | LG Electronics Inc.6.656D007KEEN261 [208V] | 2018-10-01 | 2018-10-15
LG Electronics Inc. | D007KEEN261 [240V] | N | Y | Y | 7680 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter | 7.68 | 240 | 97.5 | [08/30/2018] | [1.4.1] | 2018-10-15 | N | N |  | 1.19 |  |  | 270 | 380 | 450 | 0.768 | 1.536 | 2.304 | 3.84 | 5.76 | 7.68 | 95.1418 | 96.5566 | 97.3325 | 97.5972 | 97.5104 | 97.1304 | 97.3459 | 96.4957 | 97.6782 | 98.0328 | 98.0644 | 97.7762 | 97.4311 | 97.7942 | 95.7683 | 97.3217 | 97.8155 | 97.9581 | 97.748 | 97.4471 | 97.6847 | LG Electronics Inc.7.68D007KEEN261 [240V] | 2018-10-01 | 2018-10-15
Lixma Tech | LSI4000 [240V] | Y | N | N | 4000 W, 240 Vac Utility Interactive Inverter | 4.03 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.19 |  |  | 250 | 310 | 440 | 0.4 | 0.81 | 1.21 | 2.02 | 3.02 | 4.03 | 91.6 | 94.5 | 95.2 | 95.3 | 95 | 93.9 | 94.9 | 90.2 | 94.5 | 95.5 | 95.8 | 95.6 | 95 | 95.3 | 87.4 | 92.8 | 94 | 95 | 95.2 | 94.6 | 94.5 | Lixma Tech4.03LSI4000 [240V]
Mage Solar | POWERTEC Plus 240 / 6 PL-US AC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.0238 | 0.0476 | 0.0714 | 0.119 | 0.1785 | 0.238 | 88.74 | 93.68 | 94.03 | 94.87 | 94.98 | 94.74 | 94.52 | 87.73 | 93.5 | 94.82 | 95.13 | 95.52 | 95.46 | 94.94 | 86.91 | 93.18 | 94.64 | 95.08 | 95.65 | 95.69 | 94.94 | Mage Solar0.24POWERTEC Plus 240 / 6 PL-US AC [240V]
Mage Solar | POWERTEC Plus 245 / 6 PL US AC [240V] | Y | N | N | 245W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.22 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Mage Solar0.24POWERTEC Plus 245 / 6 PL US AC [240V]
Mage Solar USA | POWERTEC Plus 250 / 6 PL US AC [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.22 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Mage Solar USA0.24POWERTEC Plus 250 / 6 PL US AC [208V]
Mage Solar USA | POWERTEC Plus 250 / 6 PL US AC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.22 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | Mage Solar USA0.24POWERTEC Plus 250 / 6 PL US AC [240V]
Ming Shen Energy Technology | EnerBridge Emi_301RD [240V] | Y | N | N | 300 W 240 Vac Utility Interactive Inverter | 0.29 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.1 |  |  | 26 | 31 | 43 | 0.03 | 0.06 | 0.09 | 0.14 | 0.22 | 0.29 | 92.1 | 94.4 | 95 | 95.7 | 96.3 | 95.9 | 95.7 | 91.6 | 95.1 | 94.8 | 96.5 | 96.5 | 96.5 | 96.1 | 89.9 | 94.3 | 95.3 | 96.3 | 96.2 | 96.2 | 95.8 | Ming Shen Energy Technology0.29EnerBridge Emi_301RD [240V]
Mohr Power | MPS1100EVR [120V] | Y | N | N | 1100 W, 120 Vac Utility Interactive Inverter | 1.1 | 120 | 90.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 182 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 81.8 | 89 | 90.9 | 92.1 | 92.4 | 92.5 | 91.6 | 79.9 | 88 | 90.1 | 91.7 | 92.2 | 92.3 | 91.1 | 74.8 | 84.7 | 87.8 | 90 | 90.8 | 91.1 | 89.3 | Mohr Power1.1MPS1100EVR [120V]
Mohr Power | MPS2000EVR [240V] | Y | N | N | 2000 W, 240 Vac Utility Interactive Inverter | 2 | 240 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 199 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.3 | 91.7 | 92.6 | 93.5 | 93.2 | 93 | 92.9 | 85.7 | 90.8 | 92.1 | 92.9 | 92.9 | 92.6 | 92.4 | 82.4 | 88.8 | 90.5 | 91.6 | 91.8 | 91.6 | 91.1 | Mohr Power2MPS2000EVR [240V]
Mohr Power | MPS2500 [240V] | Y | N | N | 2500 W, 240 Vac Utility Interactive Inverter | 2.5 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2 | Mohr Power2.5MPS2500 [240V]
Mohr Power | MPS3000 [240V] | Y | N | N | 3000 W, 240 Vac Utility Interactive Inverter | 3 | 240 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.63 |  |  | 100 | 222.5 | 380 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 88.9 | 92.9 | 93.8 | 94.3 | 94.2 | 93.9 | 93.9 | 87.9 | 92.5 | 93.5 | 94.1 | 94 | 93.8 | 93.7 | 84.9 | 90.9 | 92.4 | 93.3 | 93.2 | 93 | 92.7 | Mohr Power3MPS3000 [240V]
Mohr Power | MPS3500 [240V] | Y | N | N | 3500 W, 240 Vac Utility Interactive Inverter | 3.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.86 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.625 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5 | Mohr Power3.5MPS3500 [240V]
Mohr Power | MPS4600 [208V] | Y | N | N | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 |  |  | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95 | Mohr Power4.6MPS4600 [208V]
Mohr Power | MPS4800 [240V] | Y | N | N | 4800 W, 240 Vac Utility Interactive Inverter | 4.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.1 |  |  | 100 | 263 | 400 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 86.8 | 93.5 | 95.5 | 97 | 97.2 | 97.1 | 96.4 | 85.5 | 92.9 | 95 | 96.7 | 96.9 | 96.8 | 96 | 84.5 | 91.5 | 93.9 | 95.9 | 96.2 | 96.1 | 95.1 | Mohr Power4.8MPS4800 [240V]
Mohr Power | MPS5200 [240V] | Y | N | N | 5200 W, 240 Vac Utility Interactive Inverter | 5.2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 |  |  | 100 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5 | Mohr Power5.2MPS5200 [240V]
Motech Industries | PVMate 2900U [208V] | Y | N | N | 2.7 kW, 208 Vac Utility Interactive Inverter | 2.7 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 90.7 | 94.5 | 95.8 | 96.4 | 96.3 | 95.9 | 95.9 | 89.8 | 94.1 | 95.5 | 96.2 | 96.2 | 95.8 | 95.7 | 88.2 | 92.5 | 94.3 | 95.5 | 95.6 | 95.3 | 94.9 | Motech Industries2.7PVMate 2900U [208V]
Motech Industries | PVMate 2900U-POS [208V] | Y | N | N | 2.7 kW, 208 Vac Utility Interactive Inverter | 2.7 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 90.7 | 94.5 | 95.8 | 96.4 | 96.3 | 95.9 | 95.9 | 89.8 | 94.1 | 95.5 | 96.2 | 96.2 | 95.8 | 95.7 | 88.2 | 92.5 | 94.3 | 95.5 | 95.6 | 95.3 | 94.9 | Motech Industries2.7PVMate 2900U-POS [208V]
Motech Industries | PVMate 3000U [208V] | Y | N | N | 2.7 kW, 208 Vac Utility Interactive Inverter | 2.81 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.35 |  |  | 100 | 275 | 400 | 0.28 | 0.56 | 0.84 | 1.41 | 2.11 | 2.81 | 89.4 | 94.4 | 95.5 | 96.2 | 96.2 | 95.9 | 95.8 | 88.7 | 93.8 | 95.2 | 95.9 | 96 | 95.7 | 95.5 | 86.5 | 92.1 | 94 | 95.1 | 95.3 | 95.2 | 94.6 | Motech Industries2.81PVMate 3000U [208V]
Motech Industries | PVMate 3000U-PG [208V] | Y | N | N | 2.7 kW, 208 Vac Utility Interactive Inverter | 2.81 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.35 |  |  | 100 | 275 | 400 | 0.28 | 0.56 | 0.84 | 1.41 | 2.11 | 2.81 | 89.4 | 94.4 | 95.5 | 96.2 | 96.2 | 95.9 | 95.8 | 88.7 | 93.8 | 95.2 | 95.9 | 96 | 95.7 | 95.5 | 86.5 | 92.1 | 94 | 95.1 | 95.3 | 95.2 | 94.6 | Motech Industries2.81PVMate 3000U-PG [208V]
Motech Industries | PVMate 2900U [240V] | Y | N | N | 2.9 kW, 240 Vac Utility Interactive Inverter | 2.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.9 | 91.9 | 95.1 | 96.2 | 96.7 | 96.5 | 96.1 | 96.3 | 91.3 | 94.7 | 95.9 | 96.5 | 96.4 | 96 | 96.1 | 89.3 | 93.3 | 94.8 | 95.8 | 95.8 | 95.4 | 95.3 | Motech Industries2.9PVMate 2900U [240V]
Motech Industries | PVMate 2900U-POS [240V] | Y | N | N | 2.9 kW, 240 Vac Utility Interactive Inverter | 2.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.9 | 91.9 | 95.1 | 96.2 | 96.7 | 96.5 | 96.1 | 96.3 | 91.3 | 94.7 | 95.9 | 96.5 | 96.4 | 96 | 96.1 | 89.3 | 93.3 | 94.8 | 95.8 | 95.8 | 95.4 | 95.3 | Motech Industries2.9PVMate 2900U-POS [240V]
Motech Industries | PVMate 3000U [240V] | Y | N | N | 2.9 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 90.6 | 95 | 96 | 96.6 | 96.6 | 96.2 | 96.2 | 89.8 | 94.4 | 95.6 | 96.4 | 96.4 | 96 | 95.9 | 87.7 | 92.9 | 94.5 | 95.6 | 95.8 | 95.5 | 95.1 | Motech Industries3.01PVMate 3000U [240V]
Motech Industries | PVMate 3000U-PG [240V] | Y | N | N | 2.9 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 90.6 | 95 | 96 | 96.6 | 96.6 | 96.2 | 96.2 | 89.8 | 94.4 | 95.6 | 96.4 | 96.4 | 96 | 95.9 | 87.7 | 92.9 | 94.5 | 95.6 | 95.8 | 95.5 | 95.1 | Motech Industries3.01PVMate 3000U-PG [240V]
Motech Industries | PVMate 3840U [208V] | Y | N | N | Same unit as PVMate 3900U with max power for use with 20-A breaker | 3.32 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2 | Motech Industries3.32PVMate 3840U [208V]
Motech Industries | PVMate 3840U-POS [208V] | Y | N | N | Same unit as PVMate 3900U with max power for use with 20-A breaker | 3.32 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2 | Motech Industries3.32PVMate 3840U-POS [208V]
Motech Industries | PVMate 3900U [208V] | Y | N | N | 3.4 kW 208 Vac Utility Interactive Inverter | 3.4 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2 | Motech Industries3.4PVMate 3900U [208V]
Motech Industries | PVMate 3900U-POS [208V] | Y | N | N | 3.4 kW 208 Vac Utility Interactive Inverter | 3.4 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2 | Motech Industries3.4PVMate 3900U-POS [208V]
Motech Industries | PVMate 4000U [208V] | Y | N | N | 3.4 kW 208 Vac Utility Interactive Inverter | 3.51 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.35 |  |  | 100 | 275 | 400 | 0.35 | 0.7 | 1.05 | 1.76 | 2.63 | 3.51 | 91.3 | 95.1 | 96 | 96.3 | 96.1 | 95.4 | 95.9 | 90.4 | 94.7 | 95.7 | 96 | 95.9 | 95.3 | 95.6 | 88.4 | 93.3 | 94.7 | 95.3 | 95.3 | 94.7 | 94.8 | Motech Industries3.51PVMate 4000U [208V]
Motech Industries | PVMate 4000U-PG [208V] | Y | N | N | 3.4 kW 208 Vac Utility Interactive Inverter | 3.51 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.35 |  |  | 100 | 275 | 400 | 0.35 | 0.7 | 1.05 | 1.76 | 2.63 | 3.51 | 91.3 | 95.1 | 96 | 96.3 | 96.1 | 95.4 | 95.9 | 90.4 | 94.7 | 95.7 | 96 | 95.9 | 95.3 | 95.6 | 88.4 | 93.3 | 94.7 | 95.3 | 95.3 | 94.7 | 94.8 | Motech Industries3.51PVMate 4000U-PG [208V]
Motech Industries | PVMate 3840U [240V] | Y | N | N | Same unit as PVMate 3900U with max power for use with 20-A breaker | 3.84 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2 | Motech Industries3.84PVMate 3840U [240V]
Motech Industries | PVMate 3840U-POS [240V] | Y | N | N | Same unit as PVMate 3900U with max power for use with 20-A breaker | 3.84 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2 | Motech Industries3.84PVMate 3840U-POS [240V]
Motech Industries | PVMate 3900U [240V] | Y | N | N | 3.9 kW, 240 Vac Utility Interactive Inverter | 3.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2 | Motech Industries3.9PVMate 3900U [240V]
Motech Industries | PVMate 3900U-POS [240V] | Y | N | N | 3.9 kW, 240 Vac Utility Interactive Inverter | 3.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2 | Motech Industries3.9PVMate 3900U-POS [240V]
Motech Industries | PVMate 4000U [240V] | Y | N | N | 3.9 kW, 240 Vac Utility Interactive Inverter | 4.02 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.4 | 0.8 | 1.21 | 2.01 | 3.02 | 4.02 | 92.6 | 95.7 | 96.4 | 96.5 | 96.3 | 95.5 | 96.1 | 91.8 | 95.3 | 96.1 | 96.3 | 96.1 | 95.4 | 95.9 | 90 | 94.1 | 95.2 | 95.7 | 95.5 | 94.9 | 95.2 | Motech Industries4.02PVMate 4000U [240V]
Motech Industries | PVMate 4000U-PG [240V] | Y | N | N | 3.9 kW, 240 Vac Utility Interactive Inverter | 4.02 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.4 | 0.8 | 1.21 | 2.01 | 3.02 | 4.02 | 92.6 | 95.7 | 96.4 | 96.5 | 96.3 | 95.5 | 96.1 | 91.8 | 95.3 | 96.1 | 96.3 | 96.1 | 95.4 | 95.9 | 90 | 94.1 | 95.2 | 95.7 | 95.5 | 94.9 | 95.2 | Motech Industries4.02PVMate 4000U-PG [240V]
Motech Industries | PVMate 4900U [208V] | Y | N | N | 4.3 kW, 208 Vac Utility Interactive Inverter | 4.3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.43 | 0.86 | 1.29 | 2.15 | 3.23 | 4.3 | 93.3 | 95.5 | 96.2 | 96.4 | 96.1 | 95.6 | 96 | 92.7 | 95.2 | 95.9 | 96.2 | 96 | 95.5 | 95.8 | 91.4 | 94.2 | 95.2 | 95.8 | 95.7 | 95.2 | 95.4 | Motech Industries4.3PVMate 4900U [208V]
Motech Industries | PVMate 4900U-POS [208V] | Y | N | N | 4.3 kW, 208 Vac Utility Interactive Inverter | 4.3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.43 | 0.86 | 1.29 | 2.15 | 3.23 | 4.3 | 93.3 | 95.5 | 96.2 | 96.4 | 96.1 | 95.6 | 96 | 92.7 | 95.2 | 95.9 | 96.2 | 96 | 95.5 | 95.8 | 91.4 | 94.2 | 95.2 | 95.8 | 95.7 | 95.2 | 95.4 | Motech Industries4.3PVMate 4900U-POS [208V]
Motech Industries | PVMate 5000U [208V] | Y | N | N | 4.3 kW, 208 Vac Utility Interactive Inverter | 4.4 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 92.9 | 95.8 | 96.5 | 96.8 | 96.6 | 95.9 | 96.4 | 92.2 | 95.3 | 96.2 | 96.4 | 96.2 | 95.5 | 96 | 90.1 | 93.9 | 95 | 95.7 | 95.6 | 95.2 | 95.2 | Motech Industries4.4PVMate 5000U [208V]
Motech Industries | PVMate 5000U-PG [208V] | Y | N | N | 4.3 kW, 208 Vac Utility Interactive Inverter | 4.4 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 92.9 | 95.8 | 96.5 | 96.8 | 96.6 | 95.9 | 96.4 | 92.2 | 95.3 | 96.2 | 96.4 | 96.2 | 95.5 | 96 | 90.1 | 93.9 | 95 | 95.7 | 95.6 | 95.2 | 95.2 | Motech Industries4.4PVMate 5000U-PG [208V]
Motech Industries | PVMate 5300U [208V] | Y | N | N | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.5 | 95.6 | 96.2 | 96.1 | 95.9 | 95.3 | 95.9 | 93 | 95.3 | 96 | 95.9 | 95.9 | 95.2 | 95.7 | 91.7 | 94.4 | 95.2 | 95.7 | 95.5 | 95 | 95.3 | Motech Industries4.6PVMate 5300U [208V]
Motech Industries | PVMate 5300U-POS [208V] | Y | N | N | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.5 | 95.6 | 96.2 | 96.1 | 95.9 | 95.3 | 95.9 | 93 | 95.3 | 96 | 95.9 | 95.9 | 95.2 | 95.7 | 91.7 | 94.4 | 95.2 | 95.7 | 95.5 | 95 | 95.3 | Motech Industries4.6PVMate 5300U-POS [208V]
Motech Industries | PVMate 4900U [240V] | Y | N | N | 4.9 kW, 240 Vac Utility Interactive Inverter | 4.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.49 | 0.98 | 1.47 | 2.45 | 3.68 | 4.9 | 93.9 | 96 | 96.5 | 96.6 | 96.2 | 95.6 | 96.2 | 93.4 | 95.7 | 96.3 | 96.5 | 96 | 95.4 | 96 | 92.1 | 94.8 | 95.7 | 96 | 95.8 | 95.2 | 95.6 | Motech Industries4.9PVMate 4900U [240V]
Motech Industries | PVMate 4900U-POS [240V] | Y | N | N | 4.9 kW, 240 Vac Utility Interactive Inverter | 4.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.49 | 0.98 | 1.47 | 2.45 | 3.68 | 4.9 | 93.9 | 96 | 96.5 | 96.6 | 96.2 | 95.6 | 96.2 | 93.4 | 95.7 | 96.3 | 96.5 | 96 | 95.4 | 96 | 92.1 | 94.8 | 95.7 | 96 | 95.8 | 95.2 | 95.6 | Motech Industries4.9PVMate 4900U-POS [240V]
Motech Industries | PVMate 5000U [240V] | Y | N | N | 4.9 kW, 240 Vac Utility Interactive Inverter | 5.01 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.5 | 1 | 1.5 | 2.51 | 3.76 | 5.01 | 93.9 | 96.1 | 96.6 | 96.7 | 96.4 | 95.7 | 96.3 | 92.7 | 95.8 | 96.4 | 96.5 | 96.2 | 95.6 | 96.1 | 91.2 | 94.7 | 95.7 | 96.1 | 95.9 | 95.4 | 95.7 | Motech Industries5.01PVMate 5000U [240V]
Motech Industries | PVMate 5000U-PG [240V] | Y | N | N | 4.9 kW, 240 Vac Utility Interactive Inverter | 5.01 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.5 | 1 | 1.5 | 2.51 | 3.76 | 5.01 | 93.9 | 96.1 | 96.6 | 96.7 | 96.4 | 95.7 | 96.3 | 92.7 | 95.8 | 96.4 | 96.5 | 96.2 | 95.6 | 96.1 | 91.2 | 94.7 | 95.7 | 96.1 | 95.9 | 95.4 | 95.7 | Motech Industries5.01PVMate 5000U-PG [240V]
Motech Industries | PVMate 5300U [240V] | Y | N | N | 5.3 kW, 240 Vac Utility Interactive Inverter | 5.3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 94.3 | 96.1 | 96.3 | 96.4 | 96 | 95.2 | 96 | 93.8 | 95.9 | 96.1 | 96.3 | 95.8 | 95.2 | 95.8 | 92.5 | 95 | 95.7 | 96 | 95.5 | 94.9 | 95.4 | Motech Industries5.3PVMate 5300U [240V]
Motech Industries | PVMate 5300U-POS [240V] | Y | N | N | 5.3 kW, 240 Vac Utility Interactive Inverter | 5.3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 94.3 | 96.1 | 96.3 | 96.4 | 96 | 95.2 | 96 | 93.8 | 95.9 | 96.1 | 96.3 | 95.8 | 95.2 | 95.8 | 92.5 | 95 | 95.7 | 96 | 95.5 | 94.9 | 95.4 | Motech Industries5.3PVMate 5300U-POS [240V]
Motech Industries | PVMate 6500U [208V] | Y | N | N | 6.43 kW, 208 Vac Utility Interactive Inverter | 6.43 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.643 | 1.286 | 1.929 | 3.215 | 4.823 | 6.43 | 93.3 | 95.6 | 96 | 96 | 95.6 | 94.8 | 95.6 | 92.9 | 95.4 | 95.9 | 95.9 | 95.5 | 94.8 | 95.5 | 91.6 | 94.8 | 95.4 | 95.6 | 95.2 | 94.6 | 95.1 | Motech Industries6.43PVMate 6500U [208V]
Motech Industries | PVMate 6500U [240V] | Y | N | N | 6.45 kW, 240 Vac Utility Interactive Inverter | 6.45 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.65 |  |  | 100 | 275 | 400 | 0.645 | 1.29 | 1.935 | 3.225 | 4.838 | 6.45 | 93.5 | 95.9 | 96.3 | 96.3 | 96 | 95.4 | 96 | 93.1 | 95.7 | 96.2 | 96.3 | 96 | 95.3 | 95.9 | 91.8 | 95 | 95.6 | 95.9 | 95.7 | 95.2 | 95.5 | Motech Industries6.45PVMate 6500U [240V]
Motech Industries | PVMate 6500U [277V] | Y | N | N | 6.45 kW, 277 Vac Utility Interactive Inverter | 6.45 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 100 | 275 | 400 | 0.645 | 1.29 | 1.935 | 3.225 | 4.838 | 6.45 | 93.8 | 96.1 | 96.5 | 96.7 | 96.4 | 95.8 | 96.3 | 93.4 | 95.9 | 96.4 | 96.5 | 96.3 | 95.8 | 96.2 | 92 | 95.3 | 95.9 | 96.2 | 96 | 95.6 | 95.8 | Motech Industries6.45PVMate 6500U [277V]
Motech Industries | PVMate 7500U [208V] | Y | N | N | 7.43 kW, 208 Vac Utility Interactive Inverter | 7.43 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.52 |  |  | 100 | 275 | 400 | 0.743 | 1.486 | 2.229 | 3.715 | 5.573 | 7.43 | 94.1 | 96 | 96.2 | 96.1 | 95.4 | 94.6 | 95.6 | 93.7 | 95.7 | 96 | 96 | 95.3 | 94.5 | 95.5 | 92.5 | 95.1 | 95.6 | 95.6 | 95.1 | 94.3 | 95.1 | Motech Industries7.43PVMate 7500U [208V]
Motech Industries | PVMate 7500U [240V] | Y | N | N | 7.45 kW, 240 Vac Utility Interactive Inverter | 7.45 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.68 |  |  | 100 | 275 | 400 | 0.745 | 1.49 | 2.235 | 3.725 | 5.588 | 7.45 | 94.3 | 96.2 | 96.5 | 96.5 | 95.9 | 95.2 | 96 | 93.9 | 96 | 96.3 | 96.3 | 95.8 | 95.1 | 95.9 | 92.7 | 95.4 | 95.9 | 96 | 95.5 | 94.9 | 95.5 | Motech Industries7.45PVMate 7500U [240V]
Motech Industries | PVMate 7500U [277V] | Y | N | N | 7.46 kW, 277 Vac Utility Interactive Inverter | 7.46 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 100 | 275 | 400 | 0.746 | 1.492 | 2.238 | 3.73 | 5.595 | 7.46 | 94.4 | 96.4 | 96.7 | 96.6 | 96.2 | 95.5 | 96.3 | 94 | 96.1 | 96.5 | 96.6 | 96.2 | 95.5 | 96.2 | 92.9 | 95.5 | 96.1 | 96.2 | 95.9 | 95.3 | 95.8 | Motech Industries7.46PVMate 7500U [277V]
Nextronex Energy Systems | Ray-Max 150 | Y | N | N | 150 kW, Utility Interactive Inverter with medium voltage transformer | 150 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 507.8 |  |  | 600 | 620 | 730 | 15 | 30 | 45 | 75 | 112.5 | 150 | 93.1 | 94.2 | 95.6 | 96.7 | 96.7 | 96.7 | 96.3 | 93.9 | 94.4 | 94.8 | 96.5 | 96.6 | 96.7 | 96.1 | 87.5 | 92 | 93.8 | 95.5 | 96.2 | 96.1 | 95.2 | Nextronex Energy Systems150Ray-Max 150
Ningbo Ginlong Technologies Co.,Ltd. | GCI-1K-2G-H-US [208V] | Y | N | N | 1 kW, 208 Vac Utility Interactive Inverter | 0.99 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.1 | 0.2 | 0.3 | 0.5 | 0.74 | 0.99 | 91.8 | 94.1 | 95.2 | 96 | 95.8 | 95.5 | 95.5 | 92.2 | 94.4 | 95.4 | 96.1 | 96 | 95.8 | 95.7 | 93.3 | 94.9 | 95.6 | 96.4 | 96.3 | 96.1 | 96.1 | Ningbo Ginlong Technologies Co.,Ltd.0.99GCI-1K-2G-H-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-1K-2G-H-US [240V] | Y | N | N | 1 kW, 240 Vac Utility Interactive Inverter | 0.99 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.1 | 0.2 | 0.3 | 0.5 | 0.74 | 0.99 | 91.8 | 94 | 95 | 96 | 95.6 | 95.4 | 95.4 | 93.3 | 94.8 | 95.5 | 96.3 | 96 | 95.4 | 95.8 | 93.5 | 95 | 95.8 | 96.8 | 96.7 | 96 | 96.3 | Ningbo Ginlong Technologies Co.,Ltd.0.99GCI-1K-2G-H-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-1K-2G-W-US [208V] | Y | N | N | 1 kW, 208 Vac Utility Interactive Inverter | 0.99 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.1 | 0.2 | 0.3 | 0.5 | 0.74 | 0.99 | 91.8 | 94.1 | 95.2 | 96 | 95.8 | 95.5 | 95.5 | 92.2 | 94.4 | 95.4 | 96.1 | 96 | 95.8 | 95.7 | 93.3 | 94.9 | 95.6 | 96.4 | 96.3 | 96.1 | 96.1 | Ningbo Ginlong Technologies Co.,Ltd.0.99GCI-1K-2G-W-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-1K-2G-W-US [240V] | Y | N | N | 1 kW, 240 Vac Utility Interactive Inverter | 0.99 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.1 | 0.2 | 0.3 | 0.5 | 0.74 | 0.99 | 91.8 | 94 | 95 | 96 | 95.6 | 95.4 | 95.4 | 93.3 | 94.8 | 95.5 | 96.3 | 96 | 95.4 | 95.8 | 93.5 | 95 | 95.8 | 96.8 | 96.7 | 96 | 96.3 | Ningbo Ginlong Technologies Co.,Ltd.0.99GCI-1K-2G-W-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1K-2G-US [208V] | Y | N | N | 1 kW, 208 Vac Utility Interactive Inverter | 0.99 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.1 | 0.2 | 0.3 | 0.5 | 0.74 | 0.99 | 91.8 | 94.1 | 95.2 | 96 | 95.8 | 95.5 | 95.5 | 92.2 | 94.4 | 95.4 | 96.1 | 96 | 95.8 | 95.7 | 93.3 | 94.9 | 95.6 | 96.4 | 96.3 | 96.1 | 96.1 | Ningbo Ginlong Technologies Co.,Ltd.0.99Solis-1K-2G-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1K-2G-US [240V] | Y | N | N | 1 kW, 240 Vac Utility Interactive Inverter | 0.99 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.1 | 0.2 | 0.3 | 0.5 | 0.74 | 0.99 | 91.8 | 94 | 95 | 96 | 95.6 | 95.4 | 95.4 | 93.3 | 94.8 | 95.5 | 96.3 | 96 | 95.4 | 95.8 | 93.5 | 95 | 95.8 | 96.8 | 96.7 | 96 | 96.3 | Ningbo Ginlong Technologies Co.,Ltd.0.99Solis-1K-2G-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-1.5K-2G-H-US [208V] | Y | N | N | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.49 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.12 | 1.49 | 92 | 94.1 | 95.4 | 96.3 | 96.1 | 95.7 | 95.7 | 93.2 | 94.8 | 95.8 | 96.6 | 96.2 | 96 | 96.1 | 93.3 | 95.1 | 95.9 | 96.8 | 96.4 | 96.1 | 96.2 | Ningbo Ginlong Technologies Co.,Ltd.1.49GCI-1.5K-2G-H-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-1.5K-2G-H-US [240V] | Y | N | N | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.49 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.12 | 1.49 | 91.8 | 93.9 | 95.2 | 96.1 | 96 | 95.2 | 95.6 | 93.3 | 95 | 95.9 | 96.6 | 96.3 | 96.1 | 96.1 | 93.6 | 95.3 | 96.1 | 96.8 | 96.4 | 96 | 96.3 | Ningbo Ginlong Technologies Co.,Ltd.1.49GCI-1.5K-2G-H-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-1.5K-2G-W-US [208V] | Y | N | N | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.49 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.12 | 1.49 | 92 | 94.1 | 95.4 | 96.3 | 96.1 | 95.7 | 95.7 | 93.2 | 94.8 | 95.8 | 96.6 | 96.2 | 96 | 96.1 | 93.3 | 95.1 | 95.9 | 96.8 | 96.4 | 96.1 | 96.2 | Ningbo Ginlong Technologies Co.,Ltd.1.49GCI-1.5K-2G-W-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-1.5K-2G-W-US [240V] | Y | N | N | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.49 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.12 | 1.49 | 91.8 | 93.9 | 95.2 | 96.1 | 96 | 95.2 | 95.6 | 93.3 | 95 | 95.9 | 96.6 | 96.3 | 96.1 | 96.1 | 93.6 | 95.3 | 96.1 | 96.8 | 96.4 | 96 | 96.3 | Ningbo Ginlong Technologies Co.,Ltd.1.49GCI-1.5K-2G-W-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1.5K-2G-US [208V] | Y | N | N | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.49 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.12 | 1.49 | 92 | 94.1 | 95.4 | 96.3 | 96.1 | 95.7 | 95.7 | 93.2 | 94.8 | 95.8 | 96.6 | 96.2 | 96 | 96.1 | 93.3 | 95.1 | 95.9 | 96.8 | 96.4 | 96.1 | 96.2 | Ningbo Ginlong Technologies Co.,Ltd.1.49Solis-1.5K-2G-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1.5K-2G-US [240V] | Y | N | N | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.49 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.15 | 0.3 | 0.45 | 0.75 | 1.12 | 1.49 | 91.8 | 93.9 | 95.2 | 96.1 | 96 | 95.2 | 95.6 | 93.3 | 95 | 95.9 | 96.6 | 96.3 | 96.1 | 96.1 | 93.6 | 95.3 | 96.1 | 96.8 | 96.4 | 96 | 96.3 | Ningbo Ginlong Technologies Co.,Ltd.1.49Solis-1.5K-2G-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2K-2G-H-US [208V] | Y | N | N | 2 kW, 208 Vac Utility Interactive Inverter | 1.99 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.49 | 1.99 | 92.1 | 94.1 | 95.2 | 96.5 | 96.6 | 96 | 96.1 | 93.2 | 94.8 | 95.8 | 96.9 | 96.7 | 96.4 | 96.4 | 93.4 | 95.1 | 96.3 | 97.1 | 96.8 | 96.6 | 96.6 | Ningbo Ginlong Technologies Co.,Ltd.1.99GCI-2K-2G-H-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2K-2G-H-US [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter | 1.99 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.49 | 1.99 | 92.3 | 94 | 95.1 | 96.5 | 96.2 | 96 | 95.8 | 93.1 | 94.6 | 95.7 | 97.1 | 96.8 | 96.5 | 96.5 | 93.4 | 94.8 | 95.8 | 97.2 | 97.2 | 96.9 | 96.8 | Ningbo Ginlong Technologies Co.,Ltd.1.99GCI-2K-2G-H-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2K-2G-W-US [208V] | Y | N | N | 2 kW, 208 Vac Utility Interactive Inverter | 1.99 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.49 | 1.99 | 92.1 | 94.1 | 95.2 | 96.5 | 96.6 | 96 | 96.1 | 93.2 | 94.8 | 95.8 | 96.9 | 96.7 | 96.4 | 96.4 | 93.4 | 95.1 | 96.3 | 97.1 | 96.8 | 96.6 | 96.6 | Ningbo Ginlong Technologies Co.,Ltd.1.99GCI-2K-2G-W-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2K-2G-W-US [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter | 1.99 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.49 | 1.99 | 92.3 | 94 | 95.1 | 96.5 | 96.2 | 96 | 95.8 | 93.1 | 94.6 | 95.7 | 97.1 | 96.8 | 96.5 | 96.5 | 93.4 | 94.8 | 95.8 | 97.2 | 97.2 | 96.9 | 96.8 | Ningbo Ginlong Technologies Co.,Ltd.1.99GCI-2K-2G-W-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-2K-2G-US [208V] | Y | N | N | 2 kW, 208 Vac Utility Interactive Inverter | 1.99 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.49 | 1.99 | 92.1 | 94.1 | 95.2 | 96.5 | 96.6 | 96 | 96.1 | 93.2 | 94.8 | 95.8 | 96.9 | 96.7 | 96.4 | 96.4 | 93.4 | 95.1 | 96.3 | 97.1 | 96.8 | 96.6 | 96.6 | Ningbo Ginlong Technologies Co.,Ltd.1.99Solis-2K-2G-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-2K-2G-US [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter | 1.99 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 280 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.49 | 1.99 | 92.3 | 94 | 95.1 | 96.5 | 96.2 | 96 | 95.8 | 93.1 | 94.6 | 95.7 | 97.1 | 96.8 | 96.5 | 96.5 | 93.4 | 94.8 | 95.8 | 97.2 | 97.2 | 96.9 | 96.8 | Ningbo Ginlong Technologies Co.,Ltd.1.99Solis-2K-2G-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2K [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter | 2 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 6.53 |  |  | 100 | 520 | 650 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 88.38 | 92.36 | 93.22 | 94.04 | 94.22 | 93.94 | 93.72 | 89.12 | 92.88 | 93.65 | 94.43 | 94.45 | 94.41 | 94.06 | 89.37 | 93.29 | 94.09 | 94.88 | 94.99 | 94.76 | 94.53 | Ningbo Ginlong Technologies Co.,Ltd.2GCI-2K [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2.5K-2G-H-US [208V] | Y | N | N | 2.5 kW, 208 Vac Utility Interactive Inverter | 2.49 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.87 | 2.49 | 92.2 | 94.4 | 95.6 | 97 | 96.5 | 96.2 | 96.2 | 93.1 | 95.2 | 96.4 | 97.5 | 97.3 | 96.9 | 96.9 | 93 | 95.1 | 96.3 | 97.3 | 96.9 | 96.6 | 96.6 | Ningbo Ginlong Technologies Co.,Ltd.2.49GCI-2.5K-2G-H-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2.5K-2G-H-US [240V] | Y | N | N | 2.5 kW, 240 Vac Utility Interactive Inverter | 2.49 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.87 | 2.49 | 92.3 | 94.6 | 95.7 | 96.9 | 96.7 | 96.4 | 96.3 | 93.4 | 95.5 | 96.6 | 97.6 | 97.4 | 97 | 97 | 93.1 | 95.1 | 96.3 | 97.4 | 96.9 | 96.7 | 96.7 | Ningbo Ginlong Technologies Co.,Ltd.2.49GCI-2.5K-2G-H-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2.5K-2G-W-US [208V] | Y | N | N | 2.5 kW, 208 Vac Utility Interactive Inverter | 2.49 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.87 | 2.49 | 92.2 | 94.4 | 95.6 | 97 | 96.5 | 96.2 | 96.2 | 93.1 | 95.2 | 96.4 | 97.5 | 97.3 | 96.9 | 96.9 | 93 | 95.1 | 96.3 | 97.3 | 96.9 | 96.6 | 96.6 | Ningbo Ginlong Technologies Co.,Ltd.2.49GCI-2.5K-2G-W-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-2.5K-2G-W-US [240V] | Y | N | N | 2.5 kW, 240 Vac Utility Interactive Inverter | 2.49 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.87 | 2.49 | 92.3 | 94.6 | 95.7 | 96.9 | 96.7 | 96.4 | 96.3 | 93.4 | 95.5 | 96.6 | 97.6 | 97.4 | 97 | 97 | 93.1 | 95.1 | 96.3 | 97.4 | 96.9 | 96.7 | 96.7 | Ningbo Ginlong Technologies Co.,Ltd.2.49GCI-2.5K-2G-W-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-2.5K-2G-US [208V] | Y | N | N | 2.5 kW, 208 Vac Utility Interactive Inverter | 2.49 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.87 | 2.49 | 92.2 | 94.4 | 95.6 | 97 | 96.5 | 96.2 | 96.2 | 93.1 | 95.2 | 96.4 | 97.5 | 97.3 | 96.9 | 96.9 | 93 | 95.1 | 96.3 | 97.3 | 96.9 | 96.6 | 96.6 | Ningbo Ginlong Technologies Co.,Ltd.2.49Solis-2.5K-2G-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-2.5K-2G-US [240V] | Y | N | N | 2.5 kW, 240 Vac Utility Interactive Inverter | 2.49 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.87 | 2.49 | 92.3 | 94.6 | 95.7 | 96.9 | 96.7 | 96.4 | 96.3 | 93.4 | 95.5 | 96.6 | 97.6 | 97.4 | 97 | 97 | 93.1 | 95.1 | 96.3 | 97.4 | 96.9 | 96.7 | 96.7 | Ningbo Ginlong Technologies Co.,Ltd.2.49Solis-2.5K-2G-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P2.5K-4G-US [240V] | Y | Y | Y | 2.5 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 2.5 | 240 | 97 | [8/14/2017] | [08_01] | 2018-10-15 | N | N |  | 3.2 |  |  | 120 | 330 | 500 | 0.25 | 0.5 | 0.75 | 1.25 | 1.875 | 2.5 | 93.6401 | 94.6457 | 95.692 | 96.8363 | 96.713 | 96.4833 | 96.3786 | 93.9159 | 95.5043 | 96.5921 | 97.6896 | 97.4379 | 97.114 | 97.1355 | 93.7984 | 95.1685 | 96.3297 | 97.4269 | 96.9989 | 96.8047 | 96.7792 | Ningbo Ginlong Technologies Co.,Ltd.2.5Solis-1P2.5K-4G-US (240V) [SI1] | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-3K-2G-H-US [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 2.99 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.24 | 2.99 | 93 | 94.9 | 95.8 | 97.1 | 96.8 | 96.5 | 96.5 | 93.6 | 95.3 | 96.2 | 97.6 | 97.4 | 96.8 | 97 | 93.3 | 95.1 | 96.1 | 97.3 | 97.1 | 96.6 | 96.7 | Ningbo Ginlong Technologies Co.,Ltd.2.99GCI-3K-2G-H-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-3K-2G-H-US [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 2.99 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.24 | 2.99 | 93.1 | 94.7 | 95.6 | 97.1 | 96.8 | 96.4 | 96.4 | 93.7 | 95.5 | 96.4 | 97.6 | 97.4 | 96.9 | 97 | 93.6 | 95.3 | 96.2 | 97.4 | 97.2 | 96.7 | 96.8 | Ningbo Ginlong Technologies Co.,Ltd.2.99GCI-3K-2G-H-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-3K-2G-W-US [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 2.99 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.24 | 2.99 | 93 | 94.9 | 95.8 | 97.1 | 96.8 | 96.5 | 96.5 | 93.6 | 95.3 | 96.2 | 97.6 | 97.4 | 96.8 | 97 | 93.3 | 95.1 | 96.1 | 97.3 | 97.1 | 96.6 | 96.7 | Ningbo Ginlong Technologies Co.,Ltd.2.99GCI-3K-2G-W-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-3K-2G-W-US [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 2.99 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.24 | 2.99 | 93.1 | 94.7 | 95.6 | 97.1 | 96.8 | 96.4 | 96.4 | 93.7 | 95.5 | 96.4 | 97.6 | 97.4 | 96.9 | 97 | 93.6 | 95.3 | 96.2 | 97.4 | 97.2 | 96.7 | 96.8 | Ningbo Ginlong Technologies Co.,Ltd.2.99GCI-3K-2G-W-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-3K-2G-US [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 2.99 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.24 | 2.99 | 93 | 94.9 | 95.8 | 97.1 | 96.8 | 96.5 | 96.5 | 93.6 | 95.3 | 96.2 | 97.6 | 97.4 | 96.8 | 97 | 93.3 | 95.1 | 96.1 | 97.3 | 97.1 | 96.6 | 96.7 | Ningbo Ginlong Technologies Co.,Ltd.2.99Solis-3K-2G-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-3K-2G-US [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 2.99 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.24 | 2.99 | 93.1 | 94.7 | 95.6 | 97.1 | 96.8 | 96.4 | 96.4 | 93.7 | 95.5 | 96.4 | 97.6 | 97.4 | 96.9 | 97 | 93.6 | 95.3 | 96.2 | 97.4 | 97.2 | 96.7 | 96.8 | Ningbo Ginlong Technologies Co.,Ltd.2.99Solis-3K-2G-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P3K-4G-US [240V] | Y | Y | Y | 3 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 3 | 240 | 97 | [8/14/2017] | [08_01] | 2018-10-15 | N | N |  | 3.3 |  |  | 140 | 330 | 500 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.8664 | 94.7136 | 95.6114 | 97.0574 | 96.8122 | 96.477 | 96.4801 | 94.0667 | 95.6697 | 96.5539 | 97.7675 | 97.4264 | 97.0012 | 97.1499 | 93.845 | 95.2969 | 96.1758 | 97.4408 | 97.1733 | 96.697 | 96.859 | Ningbo Ginlong Technologies Co.,Ltd.3Solis-1P3K-4G-US (240V) [SI1] | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-3.6K-2G-H-US [208V] | Y | N | N | 3.6 kW, 208 Vac Utility Interactive Inverter | 3.59 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.69 | 3.59 | 92 | 94.5 | 95.7 | 96.7 | 96.7 | 96.2 | 96.2 | 92.9 | 95.4 | 96.4 | 97.2 | 97.4 | 96.6 | 96.9 | 92.5 | 95 | 96 | 97.2 | 97.1 | 96.3 | 96.6 | Ningbo Ginlong Technologies Co.,Ltd.3.59GCI-3.6K-2G-H-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-3.6K-2G-H-US [240V] | Y | N | N | 3.6 kW, 240 Vac Utility Interactive Inverter | 3.59 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.69 | 3.59 | 92.8 | 94.7 | 95.9 | 97 | 96.6 | 96.4 | 96.3 | 93.8 | 95.6 | 96.8 | 97.7 | 97.3 | 97.1 | 97.1 | 93.6 | 95.4 | 96.6 | 97.5 | 96.9 | 96.7 | 96.8 | Ningbo Ginlong Technologies Co.,Ltd.3.59GCI-3.6K-2G-H-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-3.6K-2G-W-US [208V] | Y | N | N | 3.6 kW, 208 Vac Utility Interactive Inverter | 3.59 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.69 | 3.59 | 92 | 94.5 | 95.7 | 96.7 | 96.7 | 96.2 | 96.2 | 92.9 | 95.4 | 96.4 | 97.2 | 97.4 | 96.6 | 96.9 | 92.5 | 95 | 96 | 97.2 | 97.1 | 96.3 | 96.6 | Ningbo Ginlong Technologies Co.,Ltd.3.59GCI-3.6K-2G-W-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-3.6K-2G-W-US [240V] | Y | N | N | 3.6 kW, 240 Vac Utility Interactive Inverter | 3.59 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.69 | 3.59 | 92.8 | 94.7 | 95.9 | 97 | 96.6 | 96.4 | 96.3 | 93.8 | 95.6 | 96.8 | 97.7 | 97.3 | 97.1 | 97.1 | 93.6 | 95.4 | 96.6 | 97.5 | 96.9 | 96.7 | 96.8 | Ningbo Ginlong Technologies Co.,Ltd.3.59GCI-3.6K-2G-W-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-3.6K-2G-US [208V] | Y | N | N | 3.6 kW, 208 Vac Utility Interactive Inverter | 3.59 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.69 | 3.59 | 92 | 94.5 | 95.7 | 96.7 | 96.7 | 96.2 | 96.2 | 92.9 | 95.4 | 96.4 | 97.2 | 97.4 | 96.6 | 96.9 | 92.5 | 95 | 96 | 97.2 | 97.1 | 96.3 | 96.6 | Ningbo Ginlong Technologies Co.,Ltd.3.59Solis-3.6K-2G-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-3.6K-2G-US [240V] | Y | N | N | 3.6 kW, 240 Vac Utility Interactive Inverter | 3.59 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.69 | 3.59 | 92.8 | 94.7 | 95.9 | 97 | 96.6 | 96.4 | 96.3 | 93.8 | 95.6 | 96.8 | 97.7 | 97.3 | 97.1 | 97.1 | 93.6 | 95.4 | 96.6 | 97.5 | 96.9 | 96.7 | 96.8 | Ningbo Ginlong Technologies Co.,Ltd.3.59Solis-3.6K-2G-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P3.6K-4G-US [240V] | Y | Y | Y | 3.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 3.6 | 240 | 97 | [8/14/2017] | [08_01] | 2018-10-15 | N | N |  | 3.5 |  |  | 180 | 330 | 500 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 93.8804 | 94.7446 | 95.6302 | 97.0904 | 96.8386 | 96.4907 | 96.506 | 93.9017 | 95.6722 | 96.8973 | 97.7959 | 97.4214 | 97.0622 | 97.1909 | 93.8792 | 95.4947 | 96.5522 | 97.4831 | 97.1511 | 96.7645 | 96.9159 | Ningbo Ginlong Technologies Co.,Ltd.3.6Solis-1P3.6K-4G-US (240V) [SI1] | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-4K-2G-H-US [208V] | Y | N | N | 4 kW, 208 Vac Utility Interactive Inverter | 3.99 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 92.8 | 94.8 | 96 | 97.2 | 96.8 | 96.4 | 96.5 | 93.6 | 95.4 | 96.5 | 97.8 | 97.3 | 96.8 | 97 | 93.6 | 95.2 | 96.3 | 97.5 | 97.1 | 96.6 | 96.8 | Ningbo Ginlong Technologies Co.,Ltd.3.99GCI-4K-2G-H-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-4K-2G-H-US [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 93.1 | 94.8 | 96 | 97.1 | 96.7 | 96.3 | 96.4 | 93.7 | 95.5 | 96.6 | 97.8 | 97.4 | 96.9 | 97.1 | 93.5 | 95.3 | 96.4 | 97.6 | 97.2 | 96.7 | 96.9 | Ningbo Ginlong Technologies Co.,Ltd.3.99GCI-4K-2G-H-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-4K-2G-W-US [208V] | Y | N | N | 4 kW, 208 Vac Utility Interactive Inverter | 3.99 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 92.8 | 94.8 | 96 | 97.2 | 96.8 | 96.4 | 96.5 | 93.6 | 95.4 | 96.5 | 97.8 | 97.3 | 96.8 | 97 | 93.6 | 95.2 | 96.3 | 97.5 | 97.1 | 96.6 | 96.8 | Ningbo Ginlong Technologies Co.,Ltd.3.99GCI-4K-2G-W-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-4K-2G-W-US [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 93.1 | 94.8 | 96 | 97.1 | 96.7 | 96.3 | 96.4 | 93.7 | 95.5 | 96.6 | 97.8 | 97.4 | 96.9 | 97.1 | 93.5 | 95.3 | 96.4 | 97.6 | 97.2 | 96.7 | 96.9 | Ningbo Ginlong Technologies Co.,Ltd.3.99GCI-4K-2G-W-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-4K-2G-US [208V] | Y | N | N | 4 kW, 208 Vac Utility Interactive Inverter | 3.99 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 92.8 | 94.8 | 96 | 97.2 | 96.8 | 96.4 | 96.5 | 93.6 | 95.4 | 96.5 | 97.8 | 97.3 | 96.8 | 97 | 93.6 | 95.2 | 96.3 | 97.5 | 97.1 | 96.6 | 96.8 | Ningbo Ginlong Technologies Co.,Ltd.3.99Solis-4K-2G-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-4K-2G-US [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 93.1 | 94.8 | 96 | 97.1 | 96.7 | 96.3 | 96.4 | 93.7 | 95.5 | 96.6 | 97.8 | 97.4 | 96.9 | 97.1 | 93.5 | 95.3 | 96.4 | 97.6 | 97.2 | 96.7 | 96.9 | Ningbo Ginlong Technologies Co.,Ltd.3.99Solis-4K-2G-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P4K-4G-US [240V] | Y | Y | Y | 4 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 4 | 240 | 97 | [8/14/2017] | [08_01] | 2018-10-15 | N | N |  | 3.5 |  |  | 190 | 330 | 500 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 93.8715 | 94.7255 | 96.0908 | 97.0869 | 96.8217 | 96.404 | 96.546 | 94.0293 | 95.7206 | 96.9837 | 97.9192 | 97.4909 | 97.3216 | 97.2845 | 93.8761 | 95.4725 | 96.5568 | 97.5311 | 97.1444 | 96.7796 | 96.9225 | Ningbo Ginlong Technologies Co.,Ltd.4Solis-1P4K-4G-US (240V) [SI1] | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-4.6K-2G-H-US [208V] | Y | N | N | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.59 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 92.8 | 94.4 | 95.9 | 97 | 96.9 | 96.6 | 96.5 | 93.4 | 95.1 | 96.6 | 97.7 | 97.5 | 96.9 | 97.1 | 93.3 | 94.8 | 96.3 | 97.4 | 97.2 | 96.8 | 96.8 | Ningbo Ginlong Technologies Co.,Ltd.4.59GCI-4.6K-2G-H-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-4.6K-2G-H-US [240V] | Y | N | N | 4.6 kW, 240 Vac Utility Interactive Inverter | 4.59 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 93.1 | 94.4 | 95.7 | 96.9 | 96.8 | 96.5 | 96.4 | 93.8 | 95.3 | 96.7 | 97.8 | 97.5 | 97 | 97.2 | 93.7 | 95.1 | 96.5 | 97.4 | 97.2 | 96.9 | 96.9 | Ningbo Ginlong Technologies Co.,Ltd.4.59GCI-4.6K-2G-H-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-4.6K-2G-W-US [208V] | Y | N | N | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.59 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 92.8 | 94.4 | 95.9 | 97 | 96.9 | 96.6 | 96.5 | 93.4 | 95.1 | 96.6 | 97.7 | 97.5 | 96.9 | 97.1 | 93.3 | 94.8 | 96.3 | 97.4 | 97.2 | 96.8 | 96.8 | Ningbo Ginlong Technologies Co.,Ltd.4.59GCI-4.6K-2G-W-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-4.6K-2G-W-US [240V] | Y | N | N | 4.6 kW, 240 Vac Utility Interactive Inverter | 4.59 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 93.1 | 94.4 | 95.7 | 96.9 | 96.8 | 96.5 | 96.4 | 93.8 | 95.3 | 96.7 | 97.8 | 97.5 | 97 | 97.2 | 93.7 | 95.1 | 96.5 | 97.4 | 97.2 | 96.9 | 96.9 | Ningbo Ginlong Technologies Co.,Ltd.4.59GCI-4.6K-2G-W-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-4.6K-2G-US [208V] | Y | N | N | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.59 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 92.8 | 94.4 | 95.9 | 97 | 96.9 | 96.6 | 96.5 | 93.4 | 95.1 | 96.6 | 97.7 | 97.5 | 96.9 | 97.1 | 93.3 | 94.8 | 96.3 | 97.4 | 97.2 | 96.8 | 96.8 | Ningbo Ginlong Technologies Co.,Ltd.4.59Solis-4.6K-2G-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-4.6K-2G-US [240V] | Y | N | N | 4.6 kW, 240 Vac Utility Interactive Inverter | 4.59 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 93.1 | 94.4 | 95.7 | 96.9 | 96.8 | 96.5 | 96.4 | 93.8 | 95.3 | 96.7 | 97.8 | 97.5 | 97 | 97.2 | 93.7 | 95.1 | 96.5 | 97.4 | 97.2 | 96.9 | 96.9 | Ningbo Ginlong Technologies Co.,Ltd.4.59Solis-4.6K-2G-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P4.6K-4G-US [240V] | Y | Y | Y | 4.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 4.6 | 240 | 97 | [8/14/2017] | [08_01] | 2018-10-15 | N | N |  | 3.6 |  |  | 200 | 360 | 500 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.0282 | 94.3391 | 95.7359 | 96.9043 | 96.8001 | 96.5325 | 96.407 | 94.0655 | 95.5741 | 96.9074 | 97.9375 | 97.5427 | 97.3118 | 97.3003 | 93.7876 | 95.1009 | 96.5461 | 97.4374 | 97.2666 | 96.964 | 96.9534 | Ningbo Ginlong Technologies Co.,Ltd.4.6Solis-1P4.6K-4G-US (240V) [SI1] | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-5K-2G-H-US [208V] | Y | N | N | 5 kW, 208 Vac Utility Interactive Inverter | 4.99 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 93.4 | 94.6 | 95.5 | 97 | 96.9 | 96.3 | 96.5 | 94.4 | 95.5 | 96.4 | 97.7 | 97.6 | 96.7 | 97.2 | 94 | 94.9 | 96.1 | 97.5 | 97.3 | 96.5 | 96.9 | Ningbo Ginlong Technologies Co.,Ltd.4.99GCI-5K-2G-H-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-5K-2G-H-US [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter | 4.99 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 93.5 | 94.6 | 95.6 | 97 | 96.9 | 96.5 | 96.5 | 94.3 | 95.5 | 96.4 | 97.7 | 97.6 | 97.1 | 97.2 | 94.1 | 95 | 96.1 | 97.5 | 97.3 | 97 | 97 | Ningbo Ginlong Technologies Co.,Ltd.4.99GCI-5K-2G-H-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-5K-2G-W-US [208V] | Y | N | N | 5 kW, 208 Vac Utility Interactive Inverter | 4.99 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 93.4 | 94.6 | 95.5 | 97 | 96.9 | 96.3 | 96.5 | 94.4 | 95.5 | 96.4 | 97.7 | 97.6 | 96.7 | 97.2 | 94 | 94.9 | 96.1 | 97.5 | 97.3 | 96.5 | 96.9 | Ningbo Ginlong Technologies Co.,Ltd.4.99GCI-5K-2G-W-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-5K-2G-W-US [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter | 4.99 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 93.5 | 94.6 | 95.6 | 97 | 96.9 | 96.5 | 96.5 | 94.3 | 95.5 | 96.4 | 97.7 | 97.6 | 97.1 | 97.2 | 94.1 | 95 | 96.1 | 97.5 | 97.3 | 97 | 97 | Ningbo Ginlong Technologies Co.,Ltd.4.99GCI-5K-2G-W-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-5K-2G-US [208V] | Y | N | N | 5 kW, 208 Vac Utility Interactive Inverter | 4.99 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 93.4 | 94.6 | 95.5 | 97 | 96.9 | 96.3 | 96.5 | 94.4 | 95.5 | 96.4 | 97.7 | 97.6 | 96.7 | 97.2 | 94 | 94.9 | 96.1 | 97.5 | 97.3 | 96.5 | 96.9 | Ningbo Ginlong Technologies Co.,Ltd.4.99Solis-5K-2G-US [208V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-5K-2G-US [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter | 4.99 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 360 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 93.5 | 94.6 | 95.6 | 97 | 96.9 | 96.5 | 96.5 | 94.3 | 95.5 | 96.4 | 97.7 | 97.6 | 97.1 | 97.2 | 94.1 | 95 | 96.1 | 97.5 | 97.3 | 97 | 97 | Ningbo Ginlong Technologies Co.,Ltd.4.99Solis-5K-2G-US [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-5K-DB [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.45 |  |  | 100 | 410 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.1 | 94.9 | 95.5 | 95.5 | 94.8 | 94.1 | 94.9 | 93.8 | 96.1 | 96.8 | 96.7 | 96.1 | 95.5 | 96.2 | 92.2 | 95.4 | 96.4 | 96.3 | 95.9 | 95.3 | 95.8 | Ningbo Ginlong Technologies Co.,Ltd.5GCI-5K-DB [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | GCI-5K-W [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.45 |  |  | 100 | 410 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.1 | 94.9 | 95.5 | 95.5 | 94.8 | 94.1 | 94.9 | 93.8 | 96.1 | 96.8 | 96.7 | 96.1 | 95.5 | 96.2 | 92.2 | 95.4 | 96.4 | 96.3 | 95.9 | 95.3 | 95.8 | Ningbo Ginlong Technologies Co.,Ltd.5GCI-5K-W [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis 5000-DB [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.45 |  |  | 100 | 410 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.1 | 94.9 | 95.5 | 95.5 | 94.8 | 94.1 | 94.9 | 93.8 | 96.1 | 96.8 | 96.7 | 96.1 | 95.5 | 96.2 | 92.2 | 95.4 | 96.4 | 96.3 | 95.9 | 95.3 | 95.8 | Ningbo Ginlong Technologies Co.,Ltd.5Solis 5000-DB [240V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P5K-4G-US [240V] | Y | Y | Y | 5 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 5 | 240 | 97 | [8/14/2017] | [08_01] | 2018-10-15 | N | N |  | 3.6 |  |  | 240 | 360 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.9967 | 94.5979 | 95.7172 | 97.3161 | 97.0155 | 96.5167 | 96.6563 | 94.5418 | 95.7374 | 96.5953 | 97.9319 | 97.6168 | 97.433 | 97.3342 | 94.0094 | 94.9752 | 96.145 | 97.4705 | 97.3308 | 96.8481 | 96.9431 | Ningbo Ginlong Technologies Co.,Ltd.5Solis-1P5K-4G-US (240V) [SI1] | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P6K2-4G-US [240V] | Y | Y | Y | 6 kW, 240 Vac, 1-phase Utility Interactive Inverter, 2 channel | 6 | 240 | 97 | [8/14/2017] | [08_01] | 2018-10-15 | N | N |  | 3.5 |  |  | 300 | 360 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.1975 | 94.8034 | 95.9161 | 97.4325 | 97.2123 | 96.7122 | 96.837 | 94.4335 | 95.6416 | 96.5269 | 97.8303 | 97.7139 | 97.3363 | 97.3422 | 94.2126 | 95.1763 | 96.3489 | 97.6663 | 97.5266 | 97.0427 | 97.1403 | Ningbo Ginlong Technologies Co.,Ltd.6Solis-1P6K2-4G-US (240V) [SI1] | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P6K-4G-US | Y | N | N | 6.0 kW, transformerless Utility Interactive Inverter | 6 |  | 97.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 6 |  |  | 200 | 380 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.8998 | 96.1208 | 96.7645 | 97.3045 | 97.3234 | 96.4761 | 97.0529 | 95.5487 | 96.9813 | 97.3964 | 97.4228 | 97.3717 | 97.9525 | 97.322 | 95.3083 | 96.9146 | 97.4794 | 97.5873 | 97.5795 | 97.5828 | 97.4452 | Ningbo Ginlong Technologies Co.,Ltd.6Solis-1P6K-4G-US |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P6K-4G-US [240V] | N | Y | Y | 6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, 3 channel | 6 | 240 | 97.5 | [9/11/2017] | [0C] | 2018-10-15 | N | N | Multiple Listing of Flextronics Industrial Ltd, FLV-IA-6.0S1UA | 6 |  |  | 200 | 380 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.8998 | 96.1208 | 96.7645 | 97.3045 | 97.3234 | 96.4761 | 97.0529 | 95.5487 | 96.9813 | 97.3964 | 97.4228 | 97.3717 | 97.9525 | 97.322 | 95.3083 | 96.9146 | 97.4794 | 97.5873 | 97.5795 | 97.5828 | 97.4452 | Ningbo Ginlong Technologies Co.,Ltd.6Solis-1P6K-4G-US (240V) [SI1] | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-6K-US 480 Vac [480V] | Y | N | N | 6.0 kW, 480 Vac Utility Interactive Inverter | 6 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 7 |  |  | 100 | 650 | 780 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.9 | 94.8 | 95.6 | 96.5 | 97 | 96.5 | 96.5 | 95 | 96.1 | 96.7 | 97.3 | 97.6 | 97.3 | 97.2 | 94.5 | 95.8 | 96.5 | 97.2 | 97.4 | 96.7 | 97 | Ningbo Ginlong Technologies Co.,Ltd.6Solis-6K-US 480 Vac [480V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P7K-4G-US [240V] | Y | Y | Y | 7 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 7 | 240 | 97.5 | [9/11/2017] | [0C] | 2018-10-15 | Y | N | Multiple Listing of Flextronics Industrial Ltd, FLV-IA-7.0S1UA | 7 |  |  | 250 | 380 | 500 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 94.9607 | 96.155 | 96.8314 | 97.3565 | 97.3538 | 96.5398 | 97.0953 | 95.5846 | 97.0123 | 97.429 | 97.5 | 97.509 | 97.0437 | 97.3725 | 95.3208 | 96.9551 | 97.5201 | 97.6639 | 97.5988 | 97.5959 | 97.4796 | Ningbo Ginlong Technologies Co.,Ltd.7Solis-1P7K-4G-US (240V) [SI1] | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P7.6K-4G-US | Y | N | N | 7.6 kW, transformerless Utility Interactive Inverter | 7.6 |  | 97.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 7 |  |  | 200 | 380 | 500 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.0545 | 96.1601 | 96.8885 | 97.3433 | 97.1468 | 96.576 | 96.9955 | 95.631 | 97.1836 | 97.4753 | 97.7794 | 97.347 | 97.8962 | 97.4038 | 95.3586 | 96.7534 | 97.606 | 97.8242 | 97.8541 | 97.7094 | 97.6559 | Ningbo Ginlong Technologies Co.,Ltd.7.6Solis-1P7.6K-4G-US |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P7.6K-4G-US [240V] | N | Y | Y | 7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 7.6 | 240 | 97.5 | [9/11/2017] | [0C] | 2018-10-15 | N | N | Multiple Listing of Flextronics Industrial Ltd, FLV-IA-7.6S1UA | 7 |  |  | 200 | 380 | 500 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.0545 | 96.1601 | 96.8885 | 97.3433 | 97.1468 | 96.576 | 96.9955 | 95.631 | 97.1836 | 97.4753 | 97.7794 | 97.347 | 97.8962 | 97.4038 | 95.3586 | 96.7534 | 97.606 | 97.8242 | 97.8541 | 97.7094 | 97.6559 | Ningbo Ginlong Technologies Co.,Ltd.7.6Solis-1P7.6K-4G-US (240V) [SI1] | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P8K-4G-US | Y | N | N | 8.0 kW, transformerless Utility Interactive Inverter | 8 |  | 97.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 6 |  |  | 250 | 380 | 500 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.1153 | 96.1755 | 96.939 | 97.3693 | 97.1827 | 96.6319 | 97.0321 | 95.6565 | 97.2399 | 97.4217 | 97.5479 | 97.7024 | 96.9559 | 97.494 | 95.3757 | 96.7466 | 97.6107 | 97.8173 | 97.8528 | 97.7053 | 97.6545 | Ningbo Ginlong Technologies Co.,Ltd.8Solis-1P8K-4G-US |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P8K-4G-US [240V] | N | Y | Y | 8 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 8 | 240 | 97.5 | [9/11/2017] | [0C] | 2018-10-15 | N | N | Multiple Listing of Flextronics Industrial Ltd, FLV-IA-8.0S1UA | 6 |  |  | 250 | 380 | 500 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.1153 | 96.1755 | 96.939 | 97.3693 | 97.1827 | 96.6319 | 97.0321 | 95.6565 | 97.2399 | 97.4217 | 97.5479 | 97.7024 | 96.9559 | 97.494 | 95.3757 | 96.7466 | 97.6107 | 97.8173 | 97.8528 | 97.7053 | 97.6545 | Ningbo Ginlong Technologies Co.,Ltd.8Solis-1P8K-4G-US (240V) [SI1] | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P9K-4G-US | Y | N | N | 9.0 kW, transformerless Utility Interactive Inverter | 9 |  | 97.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 7 |  |  | 250 | 380 | 500 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 95.142 | 96.7533 | 96.9992 | 97.4866 | 97.373 | 96.9957 | 97.2129 | 95.718 | 97.2744 | 97.4478 | 97.6088 | 97.7501 | 97.1064 | 97.5469 | 95.5774 | 96.7392 | 97.6611 | 97.8213 | 97.8215 | 97.7076 | 97.6526 | Ningbo Ginlong Technologies Co.,Ltd.9Solis-1P9K-4G-US |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P9K-4G-US [240V] | N | Y | Y | 9 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 9 | 240 | 97.5 | [9/11/2017] | [0C] | 2018-10-15 | N | N | Multiple Listing of Flextronics Industrial Ltd, FLV-IA-9.0S1UA | 7 |  |  | 250 | 380 | 500 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 95.142 | 96.7533 | 96.9992 | 97.4866 | 97.373 | 96.9957 | 97.2129 | 95.718 | 97.2744 | 97.4478 | 97.6088 | 97.7501 | 97.1064 | 97.5469 | 95.5774 | 96.7392 | 97.6611 | 97.8213 | 97.8215 | 97.7076 | 97.6526 | Ningbo Ginlong Technologies Co.,Ltd.9Solis-1P9K-4G-US (240V) [SI1] | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-10K-US [480V] | Y | N | N | 10.0 kW, 480 Vac Utility Interactive Inverter | 10 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 12 |  |  | 450 | 650 | 780 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.2 | 95.2 | 96.3 | 97.1 | 97.5 | 96.8 | 97 | 95.2 | 96.3 | 96.9 | 97.6 | 98.1 | 97.5 | 97.6 | 94.7 | 96.1 | 96.7 | 97.5 | 97.8 | 97.4 | 97.4 | Ningbo Ginlong Technologies Co.,Ltd.10Solis-10K-US [480V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P10K-4G-US | Y | N | N | 10.0 kW, transformerless Utility Interactive Inverter | 10 |  | 97.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 7 |  |  | 250 | 380 | 500 | 1 | 2 | 3 | 5 | 7.5 | 10 | 95.1813 | 96.7793 | 97.0795 | 97.5465 | 97.6095 | 97.0578 | 97.3665 | 95.3043 | 96.3202 | 97.584 | 97.6578 | 97.7307 | 97.2052 | 97.5039 | 95.5999 | 96.7961 | 97.6824 | 97.7928 | 97.8088 | 97.7069 | 97.6462 | Ningbo Ginlong Technologies Co.,Ltd.10Solis-1P10K-4G-US |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-1P10K-4G-US [240V] | N | Y | Y | 10 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 10 | 240 | 97.5 | [9/11/2017] | [0C] | 2018-10-15 | N | N | Multiple Listing of Flextronics Industrial Ltd, FLV-IA-10.0S1UA | 7 |  |  | 250 | 380 | 500 | 1 | 2 | 3 | 5 | 7.5 | 10 | 95.2 | 96.8 | 97.1 | 97.5 | 97.6 | 97.1 | 97.4 | 95.3 | 96.3 | 97.6 | 97.7 | 97.7 | 97.2 | 97.5 | 95.6 | 96.8 | 97.7 | 97.8 | 97.8 | 97.7 | 97.6 | Ningbo Ginlong Technologies Co.,Ltd.10Solis-1P10K-4G-US (240V) [SI1] | 2017-10-16 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-15K-US [480V] | Y | N | N | 15.0 kW, 480 Vac Utility Interactive Inverter | 15 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 15 |  |  | 450 | 650 | 780 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 94.2 | 95.3 | 96.4 | 97.2 | 97.6 | 96.9 | 97.1 | 95.2 | 96.3 | 96.9 | 97.6 | 98.1 | 97.5 | 97.6 | 94.7 | 96.1 | 96.7 | 97.5 | 97.8 | 97.4 | 97.4 | Ningbo Ginlong Technologies Co.,Ltd.15Solis-15K-US [480V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-20K-US [480V] | Y | N | N | 20.0 kW, 480 Vac Utility Interactive Inverter | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 15 |  |  | 580 | 650 | 780 | 2 | 4 | 6 | 10 | 15 | 20 | 94.2 | 95.3 | 96.4 | 97.2 | 97.6 | 96.9 | 97.1 | 95.3 | 96.4 | 97 | 97.8 | 98.2 | 97.6 | 97.7 | 94.9 | 96.3 | 96.9 | 97.7 | 98 | 97.6 | 97.5 | Ningbo Ginlong Technologies Co.,Ltd.20Solis-20K-US [480V] |  | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-25K-US [480V] | Y | Y | Y | 25 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, | 25.05 | 480 | 98 | [01/29/2018] | [1D] | 2018-10-15 | N | N |  | 14 |  |  | 580 | 650 | 780 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 97.1 | 97.4 | 97.6 | 97.9 | 98 | 97.8 | 97.9 | 97.1 | 97.3 | 97.6 | 97.8 | 98.3 | 97.6 | 98 | 97.2 | 97.4 | 97.7 | 97.8 | 98 | 97.5 | 97.9 | Ningbo Ginlong Technologies Co.,Ltd.25.05Solis-25K-US [480V] | 2018-02-15 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-30K-US [480V] | Y | Y | Y | 30 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, | 30.05 | 480 | 98 | [01/29/2018] | [1D] | 2018-10-15 | N | N |  | 15 |  |  | 580 | 650 | 780 | 3 | 6 | 9 | 15 | 22.5 | 30 | 97.1 | 97.9 | 97.9 | 98.3 | 97.5 | 97.9 | 97.8 | 97.4 | 98.1 | 98.1 | 98.4 | 98.1 | 97.9 | 98.1 | 97.1 | 97.9 | 98 | 98.3 | 98 | 97.8 | 98 | Ningbo Ginlong Technologies Co.,Ltd.30.05Solis-30K-US [480V] | 2018-02-15 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-36K-US [480V] | Y | Y | Y | 36 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, | 36.05 | 480 | 98 | [01/29/2018] | [1D] | 2018-10-15 | N | N |  | 15 |  |  | 580 | 650 | 780 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 97.3 | 98.2 | 98.1 | 98.4 | 97.6 | 98.1 | 97.9 | 97.7 | 98.3 | 98.3 | 98.4 | 98.3 | 98.1 | 98.3 | 97.4 | 98.1 | 98.2 | 98.3 | 98.2 | 98.1 | 98.2 | Ningbo Ginlong Technologies Co.,Ltd.36.05Solis-36K-US [480V] | 2018-02-15 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-40K-US-F [480V] | Y | N | N | It's a series of 3 phase inverter , with rated output from 40--66kW for roof top commerical and ground commerical PV site. | 40 | 480 | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 1 |  |  | 580 | 650 | 780 | 4 | 8 | 12 | 20 | 30 | 40 | 97.5 | 98 | 98.1 | 98.2 | 98.1 | 97.7 | 98.1 | 97.8 | 98.3 | 98.4 | 98.6 | 98.5 | 98.3 | 98.5 | 97.6 | 98.1 | 98.2 | 98.4 | 98.3 | 98 | 98.3 | Ningbo Ginlong Technologies Co.,Ltd.50Solis-40K-US-F | 2017-10-16 | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-40K-US [480V] | Y | Y | Y | 40 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, | 40.05 | 480 | 98.5 | [01/29/2018] | [1D] | 2018-10-15 | N | N |  | 1 |  |  | 580 | 650 | 780 | 4 | 8 | 12 | 20 | 30 | 40 | 97.5 | 98 | 98.1 | 98.2 | 98.1 | 98 | 98.1 | 97.9 | 98.3 | 98.4 | 98.7 | 98.6 | 98.3 | 98.5 | 97.6 | 98.2 | 98.2 | 98.4 | 98.3 | 98.2 | 98.3 | Ningbo Ginlong Technologies Co.,Ltd.40.05Solis-40K-US [480V] | 2018-02-15 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-40K-US-F [480V] | N | Y | Y | 40 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, with external Fan. | 40.05 | 480 | 98.5 | [01/29/2018] | [1D] | 2018-10-15 | N | N |  | 1 |  |  | 580 | 650 | 780 | 4 | 8 | 12 | 20 | 30 | 40 | 97.5 | 98 | 98.1 | 98.2 | 98.1 | 97.7 | 98.1 | 97.8 | 98.3 | 98.4 | 98.6 | 98.5 | 98.3 | 98.5 | 97.6 | 98.1 | 98.2 | 98.4 | 98.3 | 98 | 98.3 | Ningbo Ginlong Technologies Co.,Ltd.40.05Solis-40K-US-F [480V] | 2018-02-15 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-50K-US [480V] | Y | N | N | It's a series of 3 phase inverter , with rated output from 40--66kW for roof top commerical and ground commerical PV site. | 50 | 480 | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.52 | 98.53 | 98.44 | 98.56 | 98.32 | 98.45 | 98.37 | 97.75 | 98.55 | 98.52 | 98.65 | 98.43 | 98.49 | 98.47 | 97.98 | 98.7 | 98.8 | 98.79 | 98.57 | 98.5 | 98.62 | Ningbo Ginlong Technologies Co.,Ltd.50Solis-40K-US-F | 2017-10-16 | 2018-02-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-50K-US-F [480V] | Y | Y | Y | 50 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, | 50.083 | 480 | 98.5 | [12/23/2017] | [19/01] | 2018-10-15 | N | N | Multiple Listing of Canadian Solar Incorporated. CSI-50KTL-GS | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.74 | 98.44 | 98.46 | 98.58 | 98.45 | 98.35 | 98.44 | 97.8 | 98.53 | 98.55 | 98.7 | 98.51 | 98.4 | 98.52 | 97.88 | 98.58 | 98.65 | 98.76 | 98.57 | 98.46 | 98.59 | Ningbo Ginlong Technologies Co., LTD 50.083Solis-50K-US-F [480V] [SI1] | 2018-02-01 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-50K-US-F-SW [480V] | N | Y | Y | 50 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, | 50.083 | 480 | 98.5 | [12/25/2017] | [19/01] | 2018-10-15 | N | N | Multiple Listing of Canadian Solar Incorporated. CSI-50KTL-GS-B | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.7362 | 98.4442 | 98.4559 | 98.5822 | 98.45 | 98.3475 | 98.4445 | 97.7983 | 98.5313 | 98.5521 | 98.7004 | 98.5123 | 98.3959 | 98.5232 | 97.8768 | 98.5781 | 98.6506 | 98.7596 | 98.5678 | 98.4644 | 98.5857 | Ningbo Ginlong Technologies Co., LTD 50.083Solis-50K-US-F-SW [480V] [SI1] | 2018-02-01 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-50K-US-SW [480V] | N | Y | Y | 50 kW, 480 Vac, Fanless, 3-phase Grid Support Utility Interactive Inverter, | 50.083 | 480 | 98.5 | [12/25/2017] | [19/01] | 2018-10-15 | N | N | Multiple Listing of Canadian Solar Incorporated. CSI-50KTL-GS-FLB | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.5167 | 98.5279 | 98.441 | 98.5562 | 98.3221 | 98.4464 | 98.3698 | 97.7469 | 98.5505 | 98.5222 | 98.6539 | 98.4338 | 98.4888 | 98.4718 | 97.9805 | 98.7 | 98.8047 | 98.7919 | 98.5679 | 98.5006 | 98.6231 | Ningbo Ginlong Technologies Co., LTD 50.083Solis-50K-US-SW [480V] [SI1] | 2018-02-01 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-50K-US [480V] | N | Y | Y | 50 kW, 480 Vac, Fanless, 3-phase Grid Support Utility Interactive Inverter, | 50.084 | 480 | 98.5 | [12/23/2017] | [19/01] | 2018-10-15 | N | N | Multiple Listing of Canadian Solar Incorporated. CSI-50KTL-GS-FL | 1 |  |  | 580 | 650 | 720 | 5 | 10 | 15 | 25 | 37.5 | 50 | 97.5 | 98.5 | 98.4 | 98.6 | 98.3 | 98.5 | 98.4 | 97.8 | 98.6 | 98.5 | 98.7 | 98.4 | 98.5 | 98.5 | 98 | 98.7 | 98.8 | 98.8 | 98.6 | 98.5 | 98.6 | Ningbo Ginlong Technologies Co., LTD 50.084Solis-50K-US [480V] [SI1] | 2018-02-01 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-60K-US-F [480V] | Y | Y | Y | 60 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, | 60.086 | 480 | 98.5 | [12/23/2017] | [19/01] | 2018-10-15 | N | N | Multiple Listing of Canadian Solar Incorporated. CSI-60KTL-GS | 1 |  |  | 580 | 650 | 720 | 6 | 12 | 18 | 30 | 45 | 60 | 97.73 | 98.31 | 98.42 | 98.55 | 98.37 | 98.22 | 98.38 | 97.82 | 98.45 | 98.54 | 98.63 | 98.5 | 98.33 | 98.49 | 97.86 | 98.53 | 98.59 | 98.7 | 98.55 | 98.45 | 98.55 | Ningbo Ginlong Technologies Co., LTD 60.086Solis-60K-US-F [480V] [SI1] | 2018-02-01 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-60K-US-F-SW [480V] | N | Y | Y | 60 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter, | 60.086 | 480 | 98.5 | [12/25/2017] | [19/01] | 2018-10-15 | N | N | Multiple Listing of Canadian Solar Incorporated. CSI-60KTL-GS-B | 1 |  |  | 580 | 650 | 720 | 6 | 12 | 18 | 30 | 45 | 60 | 97.7251 | 98.3108 | 98.4189 | 98.5501 | 98.3711 | 98.2238 | 98.3782 | 97.8227 | 98.4496 | 98.5404 | 98.6262 | 98.499 | 98.3294 | 98.4926 | 97.8622 | 98.5252 | 98.5865 | 98.7 | 98.5526 | 98.4499 | 98.5535 | Ningbo Ginlong Technologies Co., LTD 60.086Solis-60K-US-F-SW [480V] [SI1] | 2018-02-01 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-66K-US-F [480V] | Y | Y | Y | 66 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter. | 66.07 | 480 | 98.5 | [12/23/2017] | [19/01] | 2018-10-15 | N | N | Multiple Listing of Canadian Solar Incorporated. CSI-66KTL-GS | 1 |  |  | 580 | 650 | 720 | 6.6 | 13.2 | 19.8 | 33 | 49.5 | 66 | 97.57 | 98.38 | 98.48 | 98.56 | 98.42 | 98.31 | 98.42 | 97.74 | 98.5 | 98.55 | 98.7 | 98.5 | 98.39 | 98.51 | 97.77 | 98.67 | 98.65 | 98.77 | 98.56 | 98.49 | 98.58 | Ningbo Ginlong Technologies Co., LTD 66.07Solis-66K-US-F [480V] [SI1] | 2018-02-01 | 2018-10-15
Ningbo Ginlong Technologies Co.,Ltd. | Solis-66K-US-F-SW [480V] | N | Y | Y | 66 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 66.07 | 480 | 98.5 | [12/25/2017] | [19/01] | 2018-10-15 | N | N | Multiple Listing of Canadian Solar Incorporated. CSI-66KTL-GS-B | 1 |  |  | 580 | 650 | 720 | 6.6 | 13.2 | 19.8 | 33 | 49.5 | 66 | 97.5717 | 98.3763 | 98.4763 | 98.5633 | 98.4214 | 98.3118 | 98.416 | 97.7441 | 98.5006 | 98.5537 | 98.7042 | 98.4989 | 98.3902 | 98.513 | 97.7721 | 98.6713 | 98.6538 | 98.7738 | 98.5561 | 98.4918 | 98.5847 | Ningbo Ginlong Technologies Co., LTD 66.07Solis-66K-US-F-SW [480V] [SI1] | 2018-02-01 | 2018-10-15
Northern Electric | BDM-300X2-208A [208V] | Y | N | N | 500 W, 208 Vac Utility Interactive Inverter | 0.508 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.11 |  |  | 22 | 33 | 48 | 0.05 | 0.1 | 0.15 | 0.25 | 0.38 | 0.51 | 92.8 | 94.1 | 94.8 | 95.4 | 95.4 | 94.6 | 95.1 | 94.1 | 95.6 | 95.5 | 95.8 | 96.3 | 95.4 | 95.9 | 94.6 | 95.4 | 95.3 | 95.9 | 95.7 | 95.6 | 95.6 | Northern Electric0.508BDM-300X2-208A [208V]
Northern Electric | BDM-300X2-240A [240V] | Y | N | N | 500 W, 240 Vac Utility Interactive Inverter | 0.51 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.11 |  |  | 22 | 33 | 48 | 0.05 | 0.1 | 0.15 | 0.26 | 0.38 | 0.51 | 92.7 | 93.5 | 94.7 | 95.4 | 95.4 | 95.1 | 95.1 | 94.5 | 93.9 | 94.9 | 95.8 | 96.1 | 95.5 | 95.7 | 94.5 | 94.2 | 94.4 | 95.4 | 95.9 | 95.6 | 95.4 | Northern Electric0.51BDM-300X2-240A [240V]
Northern Electric & Power | BDM-250-208A [208V] | Y | N | N | 217 W, 208 Vac Utility Interactive Inverter | 0.217 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.17 |  |  | 22 | 28.5 | 44 | 0.22 | 0.43 | 0.65 | 1.08 | 1.63 | 2.17 | 89.6 | 95.5 | 95.3 | 95.7 | 95 | 94.1 | 94.9 | 90.8 | 95.2 | 94.8 | 95.5 | 95.4 | 95 | 95.2 | 85.8 | 91.5 | 93.5 | 94.4 | 95.1 | 95.5 | 94.2 | Northern Electric & Power0.217BDM-250-208A [208V]
Northern Electric & Power | BDM-250-240A [240V] | Y | N | N | 225 W, 240 Vac Utility Interactive Inverter | 0.225 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.17 |  |  | 22 | 28.5 | 44 | 0.23 | 0.45 | 0.68 | 1.13 | 1.69 | 2.25 | 90.1 | 94.5 | 94.9 | 95.1 | 95.9 | 95.4 | 95.3 | 89.7 | 93.9 | 95.2 | 95.1 | 96.2 | 96.2 | 95.5 | 85.2 | 91.4 | 93.7 | 92.5 | 95.2 | 96.3 | 93.9 | Northern Electric & Power0.225BDM-250-240A [240V]
Northern Electric & Power Co., Ltd | BDM-300-208A [208V] | Y | N | N | 250 W, 208 Vac Utility Interactive Inverter | 0.25 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.06 |  |  | 22 | 29 | 38 | 0.0251 | 0.05019 | 0.07529 | 0.12548 | 0.18821 | 0.25095 | 93.3 | 94.8 | 96.1 | 95.2 | 95.5 | 95.3 | 95.4 | 94.1 | 95.7 | 96.2 | 95.6 | 95.7 | 95.6 | 95.7 | 94.2 | 96.1 | 95.9 | 95.8 | 95.5 | 96 | 95.6 | Northern Electric & Power Co., Ltd0.25BDM-300-208A [208V] |  | 2018-03-01
Northern Electric & Power Co., Ltd | BDM-300-240A [240V] | Y | N | N | 250 W, 240 Vac Utility Interactive Inverter | 0.25 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.08 |  |  | 22 | 29 | 38 | 0.0251 | 0.05019 | 0.07529 | 0.12548 | 0.18821 | 0.25095 | 92.2 | 94.1 | 94.9 | 95.2 | 96.1 | 95.7 | 95.5 | 92.9 | 94.7 | 94.5 | 95.7 | 96.1 | 96.3 | 95.7 | 92.7 | 94.6 | 93.2 | 95.7 | 95.4 | 96.4 | 95.1 | Northern Electric & Power Co., Ltd0.25BDM-300-240A [240V] |  | 2018-03-01
Open Energy | Solar Save 1100 [240V] | Y | N | N | 1100 W, 240 Vac Utility Interactive Inverter | 1.1 | 240 | 90.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 182 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 81.8 | 89 | 90.9 | 92.1 | 92.4 | 92.5 | 91.6 | 79.9 | 88 | 90.1 | 91.7 | 92.2 | 92.3 | 91.1 | 74.8 | 84.7 | 87.8 | 90 | 90.8 | 91.1 | 89.3 | Open Energy1.1Solar Save 1100 [240V]
Open Energy | Solar Save 2000 [240V] | Y | N | N | 2000 W, 240 Vac Utility Interactive Inverter | 2 | 240 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 199 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.3 | 91.7 | 92.6 | 93.5 | 93.2 | 93 | 92.9 | 85.7 | 90.8 | 92.1 | 92.9 | 92.9 | 92.6 | 92.4 | 82.4 | 88.8 | 90.5 | 91.6 | 91.8 | 91.6 | 91.1 | Open Energy2Solar Save 2000 [240V]
Open Energy | Solar Save 2500 [240V] | Y | N | N | 2500 W, 240 Vac Utility Interactive Inverter | 2.5 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2 | Open Energy2.5Solar Save 2500 [240V]
Open Energy | Solar Save 3500 [240V] | Y | N | N | 3500 W, 240 Vac Utility Interactive Inverter | 3.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.86 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.625 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5 | Open Energy3.5Solar Save 3500 [240V]
Open Energy | Solar Save 4600 [208V] | Y | N | N | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 |  |  | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95 | Open Energy4.6Solar Save 4600 [208V]
Open Energy | Solar Save 4800 [240V] | Y | N | N | 4800 W, 240 Vac Utility Interactive Inverter | 4.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.1 |  |  | 100 | 263 | 400 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 86.8 | 93.5 | 95.5 | 97 | 97.2 | 97.1 | 96.4 | 85.5 | 92.9 | 95 | 96.7 | 96.9 | 96.8 | 96 | 84.5 | 91.5 | 93.9 | 95.9 | 96.2 | 96.1 | 95.1 | Open Energy4.8Solar Save 4800 [240V]
Open Energy | Solar Save 5200 [240V] | Y | N | N | 5200 W, 240 Vac Utility Interactive Inverter | 5.2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 |  |  | 100 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5 | Open Energy5.2Solar Save 5200 [240V]
OPTI International | GT 1500 [208V] | Y | N | N | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.46 | 90.49 | 92.52 | 94.25 | 94.92 | 95.02 | 93.86 | 85.04 | 91.04 | 93.19 | 94.79 | 95.41 | 95.53 | 94.38 | 85.31 | 91.19 | 93.54 | 95.02 | 95.55 | 95.76 | 94.58 | OPTI International1.55GT 1500 [208V]
OPTI International | GT 1500 [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.62 | 90.46 | 92.57 | 94.42 | 95.07 | 95.25 | 93.99 | 84.89 | 90.97 | 93.04 | 94.81 | 95.51 | 95.73 | 94.42 | 85.22 | 91.38 | 93.44 | 95.12 | 95.65 | 95.93 | 94.66 | OPTI International1.55GT 1500 [240V]
OPTI International | GT 2000 [208V] | Y | N | N | 2 kW, 208 Vac Utility Interactive Inverter | 2.06 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.29 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 88.28 | 93.12 | 94.41 | 95.27 | 95.43 | 95.37 | 94.87 | 89.63 | 93.68 | 94.91 | 95.73 | 95.84 | 95.8 | 95.34 | 89.74 | 94.01 | 95.11 | 96.13 | 96.38 | 96.07 | 95.77 | OPTI International2.06GT 2000 [208V]
OPTI International | GT 2000 [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter | 2.06 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 86.91 | 92.14 | 93.78 | 94.94 | 95.3 | 95.37 | 94.55 | 87.84 | 92.87 | 94.26 | 95.56 | 95.79 | 95.73 | 95.09 | 88.1 | 93.05 | 94.37 | 95.71 | 96 | 95.94 | 95.28 | OPTI International2.06GT 2000 [240V]
OPTI International | GT 3000 [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.57 | 94.41 | 95.16 | 95.47 | 95.31 | 94.62 | 95.1 | 92.05 | 94.92 | 95.58 | 95.89 | 95.76 | 95.37 | 95.56 | 92.22 | 95.17 | 95.79 | 96.25 | 95.93 | 95.8 | 95.78 | OPTI International3GT 3000 [208V]
OPTI International | GT 3000 [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.301 | 0.602 | 0.903 | 1.505 | 2.258 | 3.01 | 90 | 93.9 | 94.85 | 95.4 | 95.31 | 94.83 | 94.97 | 90.64 | 94.34 | 95.34 | 95.79 | 95.87 | 95.6 | 95.49 | 91 | 94.59 | 95.44 | 95.97 | 96.01 | 95.77 | 95.65 | OPTI International3.01GT 3000 [240V]
OPTI-Solar | GT-4000 [208V] | Y | N | N | 4 kW, 208 Vac Utility Interactive Inverter | 3.98 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.4 | 0.8 | 1.19 | 1.99 | 2.99 | 3.98 | 90.5 | 94.3 | 95.2 | 95.4 | 95.4 | 95.2 | 95.1 | 91.6 | 94.9 | 95.6 | 96 | 96 | 95.5 | 95.7 | 91.8 | 95 | 95.8 | 96.5 | 96.3 | 95.8 | 96 | OPTI-Solar3.98GT-4000 [208V]
OPTI-Solar | GT-4000 [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 90.6 | 94.3 | 95.2 | 95.7 | 95.7 | 95.6 | 95.4 | 91.5 | 95 | 95.8 | 96.3 | 96.3 | 96 | 96 | 91.9 | 95.2 | 96 | 96.4 | 96.5 | 96.3 | 96.1 | OPTI-Solar3.99GT-4000 [240V]
OutBack Power Technologies, Inc. | FXR3048A | Y | N | N | 2.5 kW, 48 Vdc Utility Interactive Inverter with battery backup | 2.56 |  | 91 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0 |  |  | 40 | 52 | 60 | 0.26 | 0.51 | 0.77 | 1.28 | 1.92 | 2.56 | 83.7 | 90.2 | 92.2 | 93.3 | 92.6 | 91.6 | 92.2 | 79.8 | 87.1 | 90 | 92 | 92 | 91.2 | 91 | 77.3 | 85.1 | 88.1 | 90.6 | 91 | 90.7 | 89.7 | OutBack Power Technologies, Inc.2.56FXR3048A |  | 2018-09-17
OutBack Power Technologies, Inc. | FXR3048A [120V] | N | Y | Y | 2.5 kW, 120 VAC Grid Support Utility Interactive Inverter with external battery backup | 2.56 | 120 | 91 | [11/7/2017] | [001.006.063] | 2018-10-15 | Y | N |  | 0 |  |  | 40 | 52 | 60 | 0.26 | 0.51 | 0.77 | 1.28 | 1.92 | 2.56 | 83.7 | 90.2 | 92.2 | 93.3 | 92.6 | 91.6 | 92.2 | 79.8 | 87.1 | 90 | 92 | 92 | 91.2 | 91 | 77.3 | 85.1 | 88.1 | 90.6 | 91 | 90.7 | 89.7 | OutBack Power Technologies, Inc.2.56FXR3048A [SI1] | 2017-12-15 | 2018-10-15
OutBack Power Technologies, Inc. | GTFX3048 | Y | N | N | 2.5 kW, 48 Vdc Utility Interactive Inverter with battery backup | 2.56 |  | 91 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  |  |  |  | 40 | 52 | 60 | 0.2562 | 0.5124 | 0.7686 | 1.281 | 1.922 | 2.562 | 83.8 | 90 | 92.2 | 93.4 | 92.7 | 91.5 | 92.2 | 80 | 87.2 | 90 | 92 | 92 | 91.5 | 91 | 77.2 | 84.9 | 88.2 | 90.7 | 91.1 | 90.6 | 89.8 | OutBack Power Technologies, Inc.2.56GTFX3048 |  | 2018-09-17
OutBack Power Technologies, Inc. | GVFX3524 | Y | N | N | Utility Interactive Inverter | 2.96 |  | 90.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0 |  |  | 22 | 24 | 28 | 0.3 | 0.59 | 0.89 | 1.48 | 2.22 | 2.96 | 88.3 | 91.9 | 92.9 | 93 | 91.3 | 88.7 | 91.6 | 87.2 | 90.8 | 92.1 | 92.1 | 91 | 88.6 | 91.1 | 83.7 | 87.1 | 89.1 | 90.6 | 90 | 87.8 | 89.5 | OutBack Power Technologies, Inc.2.96GVFX3524 |  | 2018-09-17
OutBack Power Technologies, Inc. | VFXR3524A | Y | N | N | 3 kW Utility Interactive Inverter | 2.96 |  | 90.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0 |  |  | 22 | 24 | 28 | 0.3 | 0.59 | 0.89 | 1.48 | 2.22 | 2.96 | 88.3 | 91.9 | 92.9 | 93 | 91.3 | 88.7 | 91.6 | 87.2 | 90.8 | 92.1 | 92.1 | 91 | 88.6 | 91.1 | 83.7 | 87.1 | 89.1 | 90.6 | 90 | 87.8 | 89.5 | OutBack Power Technologies, Inc.2.96VFXR3524A |  | 2018-09-17
OutBack Power Technologies, Inc. | VFXR3524A [120V] | N | Y | Y | 3 kW, 120 VAC Grid Support Utility Interactive Inverter with external battery backup | 2.96 | 120 | 90.5 | [11/7/2017] | [001.006.063] | 2018-10-15 | Y | N |  | 0 |  |  | 22 | 24 | 28 | 0.3 | 0.59 | 0.89 | 1.48 | 2.22 | 2.96 | 88.3 | 91.9 | 92.9 | 93 | 91.3 | 88.7 | 91.6 | 87.2 | 90.8 | 92.1 | 92.1 | 91 | 88.6 | 91.1 | 83.7 | 87.1 | 89.1 | 90.6 | 90 | 87.8 | 89.5 | OutBack Power Technologies, Inc.2.96VFXR3524A [SI1] | 2017-12-15 | 2018-10-15
OutBack Power Technologies, Inc. | GVFX3648 | Y | N | N | 3 kW, 48 Vdc Utility Interactive Inverter (with battery backup | 3.037 |  | 91 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0 |  |  | 40 | 51.2 | 60 | 0.3037 | 0.6075 | 0.9112 | 1.519 | 2.278 | 3.037 | 88 | 92.2 | 93.2 | 94 | 93 | 91.3 | 92.9 | 82.1 | 88.5 | 90.7 | 91.8 | 91.6 | 89.7 | 90.9 | 80.4 | 86.1 | 87.9 | 90.3 | 90.5 | 88.4 | 89.4 | OutBack Power Technologies, Inc.3.037GVFX3648 |  | 2018-09-17
OutBack Power Technologies, Inc. | VFXR3648A | Y | N | N | 4 kW, 48 Vdc Utility Interactive Inverter (with battery backup | 3.037 |  | 91 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0 |  |  | 40 | 51.2 | 60 | 0.3 | 0.61 | 0.91 | 1.52 | 2.28 | 3.04 | 88 | 92.2 | 93.5 | 94 | 93 | 91.2 | 92.9 | 82.2 | 88.5 | 90.7 | 91.8 | 91.6 | 89.7 | 90.9 | 80.3 | 86.1 | 87.9 | 90.3 | 90.4 | 88.3 | 89.4 | OutBack Power Technologies, Inc.3.037VFXR3648A |  | 2018-09-17
OutBack Power Technologies, Inc. | VFXR3648A [120V] | N | Y | Y | 4 kW, 120 VAC Grid Support Utility Interactive Inverter with external battery backup | 3.037 | 120 | 91 | [11/7/2017] | [001.006.063] | 2018-10-15 | Y | N |  | 0 |  |  | 40 | 51.2 | 60 | 0.3 | 0.61 | 0.91 | 1.52 | 2.28 | 3.04 | 88 | 92.2 | 93.5 | 94 | 93 | 91.2 | 92.9 | 82.2 | 88.5 | 90.7 | 91.8 | 91.6 | 89.7 | 90.9 | 80.3 | 86.1 | 87.9 | 90.3 | 90.4 | 88.3 | 89.4 | OutBack Power Technologies, Inc.3.037VFXR3648A [SI1] | 2017-12-15 | 2018-10-15
OutBack Power Technologies, Inc. | GS4048A | Y | N | N | Utility Interactive Inverter with battery backup | 3.6 |  | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 44 | 48 | 56 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 88.3 | 92.6 | 94.1 | 94.4 | 93.2 | 91.2 | 93.3 | 87.1 | 91.5 | 92.9 | 93.3 | 93 | 90.8 | 92.6 | 84 | 89 | 90.9 | 92.1 | 91.9 | 90.2 | 91.3 | OutBack Power Technologies, Inc.3.6GS4048A |  | 2018-09-17
OutBack Power Technologies, Inc. | GS4048A [240V] | N | Y | Y | 3.6 kW, 240 Vac Grid Support Utility Interactive Inverter with external battery backup and accessible neutral to allow 120 VAC loads to be backed up. | 3.6 | 240 | 92.5 | [11/7/2017] | [001.006.063] | 2018-10-15 | Y | N |  | 0.1 |  |  | 44 | 48 | 56 | 0.72 | 1.44 | 2.16 | 3.6 | 5.4 | 7.2 | 92.6 | 94.4 | 93.7 | 94.4 | 93 | 90.4 | 93.3 | 91.5 | 93.4 | 93 | 93.3 | 92.7 | 90.8 | 92.7 | 89 | 91.6 | 92.2 | 92.1 | 91.5 | 89.9 | 91.5 | OutBack Power Technologies, Inc.3.6GS4048A [SI1] | 2017-12-15 | 2018-10-15
OutBack Power Technologies, Inc. | SBX5048-120/240 [240V] | Y | Y | N | 5.0kW, 240Vac Grid Support Utility Interactive Multimode Inverter | 4.985 | 240 | 94 | [08/08/2018] | [NPC:0.0.0.2.2.0.9352,PBM:0.3.1.0.0.0.9359] | Not Applicable | Y | N |  | 24.85 |  |  | 250 | 420 | 550 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 85.9112 | 91.8786 | 93.404 | 94.206 | 94.0833 | 93.7751 | 93.575 | 87.0418 | 92.4308 | 94.1918 | 94.8976 | 95.0953 | 94.8942 | 94.4799 | 85.3624 | 91.926 | 93.5091 | 94.4779 | 94.7418 | 94.6173 | 94.0163 | OutBack Power Technologies, Inc.4.985SBX5048-120/240 [240V] | 2018-09-17
OutBack Power Technologies, Inc. | GS8048A | Y | N | N | Utility Interactive Inverter with battery backup | 7.2 |  | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 44 | 48 | 56 | 0.72 | 1.44 | 2.16 | 3.6 | 5.4 | 7.2 | 92.6 | 94.4 | 93.7 | 94.4 | 93 | 90.4 | 93.3 | 91.5 | 93.4 | 93 | 93.3 | 92.7 | 90.8 | 92.7 | 89 | 91.6 | 92.2 | 92.1 | 91.5 | 89.9 | 91.5 | OutBack Power Technologies, Inc.7.2GS8048A |  | 2018-09-17
OutBack Power Technologies, Inc. | GS8048A [240V] | N | Y | Y | 7.2 kW, 240 Vac Grid Support Utility Interactive Inverter with external battery backup and accessible neutral to allow 120 VAC loads to be backed up. | 7.2 | 240 | 92.5 | [11/7/2017] | [001.006.063] | 2018-10-15 | Y | N |  | 0.1 |  |  | 44 | 48 | 56 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 88.3 | 92.6 | 94.1 | 94.4 | 93.2 | 91.2 | 93.3 | 87.1 | 91.5 | 92.9 | 93.3 | 93 | 90.8 | 92.6 | 84 | 89 | 90.9 | 92.1 | 91.9 | 90.2 | 91.3 | OutBack Power Technologies, Inc.7.2GS8048A [SI1] | 2017-12-15 | 2018-10-15
OutBack Power Technologies, Inc. | GS8048 | Y | N | N | Utility Interactive Inverter with battery backup | 7.65 |  | 90 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0 |  |  | 40 | 52 | 64 | 0.76 | 1.53 | 2.29 | 3.82 | 5.74 | 7.65 | 87.4 | 91.8 | 92 | 93.3 | 92 | 90.5 | 92 | 83.4 | 88.4 | 89.2 | 90.4 | 89.7 | 88.3 | 89.4 | 79.9 | 87 | 88.5 | 89.7 | 89.2 | 88.3 | 88.7 | OutBack Power Technologies, Inc.7.65GS8048 |  | 2018-09-17
Perfect Galaxy | AE-30-60-PV-A [480V] | Y | N | N | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter | 30 | 480 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 59 |  |  | 330 | 410 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 82.9 | 89.8 | 92 | 93.5 | 94.2 | 94.3 | 93.1 | 83.5 | 89.7 | 91.9 | 93.5 | 93.9 | 93.8 | 93 | 81 | 88.6 | 91 | 93 | 93.5 | 93.6 | 92.3 | Perfect Galaxy30AE-30-60-PV-A [480V]
Perfect Galaxy | AE-30-60-PV-D [208V] | Y | N | N | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter | 30 | 208 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 54 |  |  | 330 | 410 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 82.1 | 89.2 | 91.4 | 93.1 | 93.4 | 93.2 | 92.5 | 81.5 | 88.7 | 91.2 | 92.8 | 93.2 | 93 | 92.1 | 85.2 | 90.5 | 92.5 | 93.5 | 93.8 | 93.5 | 93.1 | Perfect Galaxy30AE-30-60-PV-D [208V]
Perfect Galaxy | AE-30-60-PV-E [240V] | Y | N | N | 30 kW, 240 Vac, 1-phase Utility Interactive Inverter | 30 | 240 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 68 |  |  | 330 | 410 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 85.1 | 90.7 | 92.6 | 93.7 | 93.8 | 93.5 | 93.1 | 84.7 | 90.3 | 92.2 | 93.4 | 93.4 | 92.9 | 92.8 | 83.6 | 89.8 | 91.7 | 93 | 93.1 | 92.8 | 92.4 | Perfect Galaxy30AE-30-60-PV-E [240V]
Perfect Galaxy | AE-30-60-PV-F [240V] | Y | N | N | 30 kW, 240 Vac, 3-phase Utility Interactive Inverter | 30 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 59 |  |  | 340 | 375 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 91.6 | 92.5 | 93.9 | 95.2 | 95.5 | 95.6 | 94.9 | 91.8 | 91.9 | 93.6 | 95 | 95.3 | 95.4 | 94.7 | 89.9 | 91.2 | 92.9 | 94.5 | 94.9 | 95 | 94.2 | Perfect Galaxy30AE-30-60-PV-F [240V]
Perfect Galaxy | PVS-30 [208V] | Y | N | N | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter | 30 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 75.62 |  |  | 305 | 350 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 88.8 | 93.5 | 94.8 | 95.7 | 95.6 | 95.4 | 95.1 | 88 | 93.1 | 94.7 | 95.4 | 95.5 | 95.3 | 95 | 87 | 92.4 | 94.2 | 95 | 95.1 | 95.1 | 94.5 | Perfect Galaxy30PVS-30 [208V]
Perfect Galaxy | PVS-30 [240V] | Y | N | N | 30 kW, 240 Vac, 3-phase Utility Interactive Inverter | 30 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 64.58 |  |  | 305 | 355 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 88.2 | 93.8 | 95 | 96 | 95.8 | 95.6 | 95.3 | 88.2 | 93.3 | 94.8 | 95.7 | 95.7 | 95.6 | 95.1 | 86.1 | 92.5 | 94.4 | 95.3 | 95.5 | 95.2 | 94.8 | Perfect Galaxy30PVS-30 [240V]
Perfect Galaxy | PVS-30 [480V] | Y | N | N | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter | 30 | 480 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 72.3 |  |  | 305 | 350 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 88.4 | 93.5 | 94.6 | 95.6 | 95.6 | 95.3 | 95.1 | 87.7 | 93.1 | 94.6 | 95.4 | 95.5 | 95.3 | 95 | 86.3 | 92.1 | 93.9 | 94.9 | 95 | 94.8 | 94.3 | Perfect Galaxy30PVS-30 [480V]
Perfect Galaxy | AE-50-60-PV-D [208V] | Y | N | N | 50 kW, 208 Vac, 3-phase Utility Interactive Inverter | 50 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 90 |  |  | 327.2 | 410.9 | 474.9 | 5 | 10 | 15 | 25 | 37.5 | 50 | 88.2 | 93 | 94.4 | 95.4 | 95.2 | 95.2 | 94.7 | 86.7 | 92 | 93.8 | 94.9 | 94.8 | 94.8 | 94.2 | 85.8 | 91.2 | 93.2 | 94.6 | 94.5 | 94.6 | 93.8 | Perfect Galaxy50AE-50-60-PV-D [208V]
Perfect Galaxy | AE-50-60-PV-F [240V] | Y | N | N | 50 kW, 240 Vac, 3-phase Utility Interactive Inverter | 50 | 240 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 68 |  |  | 340 | 430 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 84.3 | 90.6 | 92.7 | 94.4 | 94.4 | 94.5 | 93.6 | 81.8 | 89.1 | 91.8 | 93.6 | 93.8 | 94 | 92.8 | 80.2 | 88.2 | 91 | 93.2 | 93.5 | 93.8 | 92.3 | Perfect Galaxy50AE-50-60-PV-F [240V]
Perfect Galaxy | PVS-50 [208V] | Y | N | N | 50 kW, 208 Vac, 3-phase Utility Interactive Inverter | 50 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 76.5 |  |  | 305 | 350 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.4 | 93.8 | 95.4 | 95.9 | 95.9 | 95.7 | 95.5 | 89.7 | 94.1 | 95.2 | 95.8 | 95.8 | 95.6 | 95.4 | 88.7 | 93 | 94.5 | 95.3 | 95.4 | 95.3 | 94.9 | Perfect Galaxy50PVS-50 [208V]
Perfect Galaxy | PVS-50 [240V] | Y | N | N | 50 kW, 240 Vac, 3-phase Utility Interactive Inverter | 50 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 93.97 |  |  | 310 | 365 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.8 | 95 | 95.9 | 96.2 | 96 | 95.5 | 95.7 | 90.4 | 94.8 | 95.3 | 96 | 95.7 | 95.5 | 95.5 | 89.6 | 93.3 | 95.2 | 95.5 | 95.4 | 95 | 95.1 | Perfect Galaxy50PVS-50 [240V]
Perfect Galaxy | PVS-50 [480V] | Y | N | N | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter | 50 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 76.5 |  |  | 305 | 350 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.5 | 95 | 95.9 | 96.3 | 96.4 | 96 | 96 | 89.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.7 | 89.5 | 94.2 | 95.1 | 95.8 | 95.6 | 95.4 | 95.3 | Perfect Galaxy50PVS-50 [480V]
Perfect Galaxy | PVS-50-S-MT [208V] | Y | N | N | 50 kW, 208 Vac, 3-phase Utility Interactive Inverter | 50 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 81 | 50 | 81 | 265 | 320 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 91.6 | 95.4 | 96.1 | 96.3 | 96.1 | 95.7 | 95.9 | 91.3 | 95.3 | 96 | 96.2 | 96 | 95.6 | 95.8 | 89 | 94.8 | 95.4 | 95.5 | 95.5 | 95.1 | 95.2 | Perfect Galaxy50PVS-50-S-MT [208V]
Perfect Galaxy | PVS-50-S-MT [240V] | Y | N | N | 50 kW, 240 Vac, 3-phase Utility Interactive Inverter | 50 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 78 | 50 | 78 | 265 | 320 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 91.6 | 95.3 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 91 | 95.1 | 95.8 | 96.2 | 95.8 | 95.5 | 95.7 | 87.8 | 94.7 | 95.3 | 95.7 | 95.4 | 95.2 | 95.1 | Perfect Galaxy50PVS-50-S-MT [240V]
Perfect Galaxy | PVS-50-S-MT [480V] | Y | N | N | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter | 50 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 78 | 50 | 78 | 265 | 320 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 92.1 | 95.3 | 96 | 96.2 | 96 | 95.7 | 95.9 | 91.5 | 95 | 95.7 | 96.1 | 95.9 | 95.6 | 95.7 | 88.7 | 94.3 | 95.3 | 95.6 | 95.4 | 95.2 | 95.1 | Perfect Galaxy50PVS-50-S-MT [480V]
Perfect Galaxy | AE-50-60-PV-A [480V] | Y | N | N | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter | 50.25 | 480 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 100.8 |  |  | 330 | 420 | 480 | 5.03 | 10.05 | 15.08 | 25.13 | 37.69 | 50.25 | 81.1 | 88.9 | 91.7 | 93.7 | 94.6 | 94.7 | 93.2 | 79.9 | 88.2 | 91.1 | 93.3 | 94.3 | 94.7 | 92.8 | 79.3 | 87.7 | 90.6 | 93 | 93.9 | 94.2 | 92.5 | Perfect Galaxy50.25AE-50-60-PV-A [480V]
Perfect Galaxy | AE-75-60-PV-A [480V] | Y | N | N | 75 kW, 480 Vac, 3-phase Utility Interactive Inverter | 75 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 99 |  |  | 318.9 | 405.6 | 479.5 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 91.1 | 94.4 | 95.5 | 96.1 | 96 | 95.9 | 95.7 | 90.3 | 93.9 | 95.1 | 95.8 | 95.6 | 95.5 | 95.3 | 89.5 | 93.4 | 94.6 | 95.5 | 95.4 | 95.3 | 95 | Perfect Galaxy75AE-75-60-PV-A [480V]
Perfect Galaxy | AE-75-60-PV-D [208V] | Y | N | N | 75 kW, 208 Vac, 3-phase Utility Interactive Inverter | 75 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 99 |  |  | 330 | 415 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 90.9 | 94.4 | 95.5 | 96.1 | 96 | 95.9 | 95.7 | 90.5 | 94 | 95.1 | 95.9 | 95.7 | 95.6 | 95.4 | 89.6 | 93.6 | 94.9 | 95.6 | 95.5 | 95.4 | 95.1 | Perfect Galaxy75AE-75-60-PV-D [208V]
Perfect Galaxy | PVS-75 [208V] | Y | N | N | 73 kW, 208 Vac, 3-phase Utility Interactive Inverter | 75 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 65.36 |  |  | 315 | 365 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 91 | 95.5 | 96.1 | 96.6 | 96.4 | 96.1 | 96.1 | 90.9 | 95.3 | 95.9 | 96.4 | 96.3 | 96 | 96 | 89.7 | 94.6 | 95.4 | 96.1 | 95.9 | 95.7 | 95.5 | Perfect Galaxy75PVS-75 [208V]
Perfect Galaxy | PVS-75 [240V] | Y | N | N | 74 kW, 240 Vac, 3-phase Utility Interactive Inverter | 75 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 71.84 |  |  | 315 | 365 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.3 | 95.5 | 96.3 | 96.6 | 96.6 | 96.3 | 96.3 | 91.2 | 95.5 | 96 | 96.5 | 96.5 | 96.2 | 96.1 | 90.6 | 94.8 | 95.4 | 96.1 | 96 | 96 | 95.7 | Perfect Galaxy75PVS-75 [240V]
Perfect Galaxy | PVS-75 [480V] | Y | N | N | 75 kW, 480 Vac, 3-phase Utility Interactive Inverter | 75 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 69.5 |  |  | 315 | 365 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.6 | 95.6 | 96.3 | 96.7 | 96.6 | 96.3 | 96.3 | 92.1 | 95.3 | 96 | 96.5 | 96.4 | 96.2 | 96.2 | 91.3 | 94.9 | 95.7 | 96.1 | 96.1 | 96 | 95.8 | Perfect Galaxy75PVS-75 [480V]
Perfect Galaxy | AE-100-60-PV-A [480V] | Y | N | N | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 97.7 |  |  | 330 | 410 | 470 | 10 | 20 | 30 | 50 | 75 | 100 | 88.7 | 93.1 | 94.6 | 95.6 | 95.8 | 95.7 | 95.2 | 87.3 | 92.3 | 93.9 | 95 | 95.3 | 95.2 | 94.6 | 86.6 | 91.8 | 93.6 | 94.8 | 95.1 | 95.1 | 94.4 | Perfect Galaxy100AE-100-60-PV-A [480V]
Perfect Galaxy | AE-100-60-PV-A-HE [480V] | Y | N | N | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 97.7 |  |  | 330 | 400 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 93.2 | 95.5 | 96 | 96.1 | 95.6 | 95.3 | 95.7 | 93.3 | 95.3 | 95.8 | 95.9 | 95.9 | 95.2 | 95.7 | 92.9 | 94.7 | 95.5 | 95.4 | 95.2 | 94.8 | 95.2 | Perfect Galaxy100AE-100-60-PV-A-HE [480V]
Perfect Galaxy | AE-100-60-PV-D [208V] | Y | N | N | 100 kW, 208 Vac, 3-phase Utility Interactive Inverter | 100 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 91.5 |  |  | 330 | 402 | 470 | 10 | 20 | 30 | 50 | 75 | 100 | 89.3 | 94.1 | 94.5 | 95.6 | 95.3 | 95.1 | 95 | 88.6 | 92.9 | 94.2 | 95 | 95.1 | 94.9 | 94.6 | 89.7 | 92.8 | 94.2 | 94.7 | 94.7 | 94.5 | 94.4 | Perfect Galaxy100AE-100-60-PV-D [208V]
Perfect Galaxy | AE-100-60-PV-F [240V] | Y | N | N | 100 kW, 240 Vac, 3-phase Utility Interactive Inverter | 100 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 97.7 |  |  | 330 | 408 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.2 | 93.9 | 94.9 | 95.8 | 95.7 | 95.5 | 95.3 | 89.3 | 93.2 | 94.7 | 95.3 | 95.4 | 95.2 | 94.9 | 88.8 | 93.2 | 94.2 | 95 | 95.3 | 94.9 | 94.7 | Perfect Galaxy100AE-100-60-PV-F [240V]
Perfect Galaxy | PVS-100 [208V] | Y | N | N | 98 kW, 208 Vac, 3-phase Utility Interactive Inverter | 100 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 62.34 |  |  | 315 | 365 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 92.6 | 95.7 | 96.4 | 96.6 | 96.5 | 96.2 | 96.3 | 92.4 | 95.5 | 96.2 | 96.5 | 96.4 | 96.1 | 96.2 | 91.3 | 94.9 | 95.7 | 96.1 | 96.1 | 95.8 | 95.8 | Perfect Galaxy100PVS-100 [208V]
Perfect Galaxy | PVS-100 [240V] | Y | N | N | 99 kW, 240 Vac, 3-phase Utility Interactive Inverter | 100 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 61.57 |  |  | 315 | 365 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.1 | 95.3 | 96.1 | 96.5 | 96.5 | 96.2 | 96.1 | 90.6 | 94.9 | 95.9 | 96.4 | 96.3 | 96.1 | 96 | 89.4 | 94.3 | 95.4 | 96 | 96 | 95.8 | 95.6 | Perfect Galaxy100PVS-100 [240V]
Perfect Galaxy | PVS-100 [480V] | Y | N | N | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 66.13 |  |  | 315 | 365 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 93.2 | 96.1 | 96.5 | 96.7 | 96.5 | 96.1 | 96.4 | 93.6 | 95.9 | 96.4 | 96.5 | 96.4 | 96 | 96.3 | 93 | 95.6 | 96.2 | 96.3 | 96.1 | 95.8 | 96 | Perfect Galaxy100PVS-100 [480V]
Perfect Galaxy | SDMS0100208LNIU [208V] | Y | N | N | 100 kW, 208 Vac, 3-phase Inverter with combiner | 100 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 60.38 |  |  | 300 | 430 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.5 | 94.2 | 95.2 | 95.5 | 95.2 | 94.8 | 95 | 89.5 | 92.3 | 95 | 95.8 | 95.6 | 95.3 | 95.1 | 90.1 | 93.5 | 94.7 | 95.9 | 95.8 | 95.5 | 95.3 | Perfect Galaxy100SDMS0100208LNIU [208V]
Perfect Galaxy | SDMS0100240LNIU [240V] | Y | N | N | 100 kW, 240 Vac, 3-phase Inverter with combiner | 100 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 61.79 |  |  | 300 | 430 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.1 | 93.5 | 94.6 | 95.1 | 95.1 | 94.7 | 94.7 | 88.1 | 91.6 | 94.4 | 95.4 | 95.5 | 95.2 | 94.8 | 88.7 | 92.8 | 94.2 | 95.5 | 95.7 | 95.3 | 95 | Perfect Galaxy100SDMS0100240LNIU [240V]
Perfect Galaxy | SDMS0100480LNIU [480V] | Y | N | N | 100 kW, 480 Vac, 3-phase Inverter with combiner | 100 | 480 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 63.88 |  |  | 300 | 430 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 89.5 | 93.4 | 94.4 | 95.1 | 95 | 94.7 | 94.6 | 87.6 | 91.5 | 94.3 | 95.3 | 95.4 | 95.2 | 94.7 | 88.1 | 92.7 | 94 | 95.4 | 95.6 | 95.4 | 94.9 | Perfect Galaxy100SDMS0100480LNIU [480V]
Perfect Galaxy | PVS-110-S-MT [208V] | Y | N | N | 110 kW, 208 Vac, 3-phase Utility Interactive Inverter | 110 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 72.5 |  |  | 265 | 320 | 480 | 11 | 22 | 33 | 55 | 82.5 | 110 | 92.6 | 95.4 | 95.8 | 95.9 | 95.6 | 94.8 | 95.5 | 91.9 | 95 | 95.5 | 95.7 | 95.4 | 94.7 | 95.3 | 89.8 | 93.7 | 94.6 | 95 | 94.8 | 94.1 | 94.5 | Perfect Galaxy110PVS-110-S-MT [208V]
Perfect Galaxy | PVS-110-S-MT [240V] | Y | N | N | 110 kW, 240 Vac, 3-phase Utility Interactive Inverter | 110 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 70.6 |  |  | 265 | 320 | 480 | 11 | 22 | 33 | 55 | 82.5 | 110 | 93 | 95.6 | 96.1 | 96.1 | 95.8 | 95.2 | 95.8 | 92.3 | 95.2 | 95.8 | 95.8 | 95.6 | 95 | 95.5 | 90.4 | 94.1 | 94.9 | 95.2 | 95 | 94.5 | 94.8 | Perfect Galaxy110PVS-110-S-MT [240V]
Perfect Galaxy | PVS-110-S-MT [480V] | Y | N | N | 110 kW, 480 Vac, 3-phase Utility Interactive Inverter | 110 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 74.3 |  |  | 265 | 320 | 480 | 11 | 22 | 33 | 55 | 82.5 | 110 | 93.2 | 95.8 | 96.1 | 96.3 | 96 | 95.5 | 95.9 | 92.6 | 95.4 | 95.8 | 96 | 95.8 | 95.3 | 95.7 | 90.9 | 94.3 | 95 | 95.3 | 95.3 | 94.8 | 95 | Perfect Galaxy110PVS-110-S-MT [480V]
Perfect Galaxy | AE-135-60-PV-A [480V] | Y | N | N | 135 kW, 480 Vac, 3-phase Utility Interactive Inverter | 135 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 98 |  |  | 330 | 415 | 470 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 90.7 | 94.2 | 95.4 | 96.1 | 96.1 | 95.9 | 95.7 | 90 | 93.8 | 95 | 95.6 | 95.7 | 95.5 | 95.3 | 89.4 | 93.4 | 94.7 | 95.4 | 95.5 | 95.4 | 95 | Perfect Galaxy135AE-135-60-PV-A [480V]
Perfect Galaxy | AE-135-60-PV-D [208V] | Y | N | N | 135 kW, 208 Vac, 3-phase Utility Interactive Inverter | 135 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 96 |  |  | 330 | 415 | 470 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 91.6 | 94.9 | 95.6 | 96 | 95.9 | 95.5 | 95.7 | 91.1 | 94.5 | 95.4 | 95.9 | 95.7 | 95.3 | 95.4 | 88.7 | 92.7 | 94.2 | 95 | 95.1 | 94.9 | 94.6 | Perfect Galaxy135AE-135-60-PV-D [208V]
Perfect Galaxy | PVS-135 [208V] | Y | N | N | 135 kW, 208 Vac, 3-phase Utility Interactive Inverter | 135 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 63.12 |  |  | 310 | 355 | 480 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 92.9 | 95.6 | 95.8 | 96.5 | 96.4 | 96.1 | 96.1 | 92.5 | 95.4 | 96.1 | 96.4 | 96.2 | 95.9 | 96 | 91 | 94 | 95 | 95.7 | 95.8 | 95.7 | 95.4 | Perfect Galaxy135PVS-135 [208V]
Perfect Galaxy | PVS-135 [240V] | Y | N | N | 135 kW, 240 Vac, 3-phase Utility Interactive Inverter | 135 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 63.7 |  |  | 320 | 360 | 480 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 92.4 | 95.6 | 95.8 | 96.6 | 96.6 | 96.3 | 96.3 | 92 | 95.3 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | 91 | 94 | 95 | 95.7 | 95.8 | 95.7 | 95.4 | Perfect Galaxy135PVS-135 [240V]
Perfect Galaxy | PVS-135 [480V] | Y | N | N | 135 kW, 480 Vac, 3-phase Utility Interactive Inverter | 135 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 63.67 |  |  | 310 | 355 | 480 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 92.9 | 95.8 | 96.5 | 96.7 | 96.5 | 96.2 | 96.4 | 92.4 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 90.8 | 94.7 | 95.6 | 96 | 95.9 | 95.7 | 95.6 | Perfect Galaxy135PVS-135 [480V]
Perfect Galaxy | PVS-210-S [208V] | Y | N | N | 210 kW, 208 Vac, 3-phase Utility Interactive Inverter | 210 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 160.8 |  |  | 265 | 318 | 480 | 21 | 42 | 63 | 105 | 157.5 | 210 | 93.5 | 95.7 | 96.2 | 96.2 | 96.1 | 95.5 | 96 | 93.1 | 95.5 | 96 | 96 | 95.6 | 95.2 | 95.6 | 91.9 | 94.6 | 95.2 | 95.3 | 95 | 94.6 | 94.9 | Perfect Galaxy210PVS-210-S [208V]
Perfect Galaxy | PVS-210-S [240V] | Y | N | N | 210 kW, 240 Vac, 3-phase Utility Interactive Inverter | 210 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 112.9 |  |  | 265 | 318 | 480 | 21 | 42 | 63 | 105 | 157.5 | 210 | 93.2 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 92.7 | 95.5 | 95.9 | 96 | 95.7 | 95.3 | 95.7 | 91.6 | 94.4 | 95.2 | 95.2 | 95.1 | 94.6 | 95 | Perfect Galaxy210PVS-210-S [240V]
Perfect Galaxy | PVS-210-S [480V] | Y | N | N | 210 kW, 480 Vac, 3-phase Utility Interactive Inverter | 210 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 189.8 |  |  | 265 | 318 | 480 | 21 | 42 | 63 | 105 | 157.5 | 210 | 92 | 95.2 | 95.8 | 96.2 | 96 | 95.7 | 95.8 | 91.7 | 94.9 | 95.7 | 95.9 | 95.5 | 95.4 | 95.4 | 90.8 | 94.1 | 95 | 95.3 | 95.1 | 94.8 | 94.9 | Perfect Galaxy210PVS-210-S [480V]
Perfect Galaxy | AE-225-60-PV-A [480V] | Y | N | N | 225 kW, 480 Vac, 3-phase Utility Interactive Inverter | 225 | 480 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 114 |  |  | 330 | 430 | 480 | 22.5 | 45 | 67.5 | 112.5 | 168.8 | 225 | 90.2 | 93.5 | 94.8 | 95.5 | 95.5 | 95.4 | 95.1 | 89 | 93 | 94.3 | 95 | 95.1 | 94.8 | 94.6 | 88.5 | 92.7 | 94 | 94.8 | 95 | 94.6 | 94.4 | Perfect Galaxy225AE-225-60-PV-A [480V]
Perfect Galaxy | AE-225-60-PV-D [208V] | Y | N | N | 225 kW, 208 Vac, 3-phase Utility Interactive Inverter | 225 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 180 |  |  | 330 | 415 | 470 | 22.5 | 45 | 67.5 | 112.5 | 168.8 | 225 | 92.2 | 95 | 95.7 | 96.1 | 95.9 | 95.5 | 95.7 | 93.2 | 94.7 | 95.5 | 95.8 | 95.7 | 95.3 | 95.5 | 91.8 | 94.4 | 95.2 | 95.6 | 95.5 | 95.2 | 95.2 | Perfect Galaxy225AE-225-60-PV-D [208V]
Perfect Galaxy | EQX0250UV480TN (P) | Y | N | N | 250 kW, Utility Interactive Inverter | 250 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 104.6 |  |  | 500 | 600 | 800 | 25 | 50 | 75 | 125 | 187.5 | 250 | 94.8 | 96.4 | 96.8 | 97 | 96.9 | 96.07 | 96.8 | 94.4 | 96.1 | 96.6 | 96.8 | 96.8 | 96.6 | 96.6 | 93.4 | 95.5 | 96.1 | 96.6 | 96.5 | 96.3 | 96.3 | Perfect Galaxy250EQX0250UV480TN (P)
Perfect Galaxy | PVS-250 | Y | N | N | 250 kW, 3-phase Inverter for Medium Voltage Transformer | 250 |  | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 151.8 |  |  | 330 | 368 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 93.8 | 95.4 | 96 | 96.2 | 96 | 95.4 | 95.9 | 93.3 | 95.2 | 95.8 | 96 | 95.8 | 95.2 | 95.7 | 92.1 | 94.6 | 95.3 | 95.6 | 95.2 | 94.7 | 95.1 | Perfect Galaxy250PVS-250
Perfect Galaxy | PVS-250 [208V] | Y | N | N | 250 kW, 208 Vac, 3-phase Utility Interactive Inverter | 250 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 105.1 | 250 | 105.1 | 320 | 365 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 95.1 | 96.3 | 96.5 | 96.4 | 96.5 | 96 | 96.4 | 94.4 | 95.9 | 96.4 | 96.3 | 96.3 | 95.8 | 96.2 | 93.7 | 95.9 | 96.2 | 95.9 | 95.8 | 95.3 | 95.8 | Perfect Galaxy250PVS-250 [208V]
Perfect Galaxy | PVS-250 [240V] | Y | N | N | 250 kW, 240 Vac, 3-phase Utility Interactive Inverter | 250 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 100 | 250 | 100 | 322 | 365 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 92.5 | 95.8 | 96.4 | 96.6 | 96.5 | 96.2 | 96.3 | 92.3 | 95.6 | 96.2 | 96.4 | 96.3 | 96 | 96.1 | 91.9 | 95.1 | 95.9 | 96 | 95.9 | 95.6 | 95.7 | Perfect Galaxy250PVS-250 [240V]
Perfect Galaxy | PVS-250 [480V] | Y | N | N | 250 kW, 480 Vac, 3-phase Utility Interactive Inverter | 250 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 119.7 | 250 | 119.7 | 320 | 365 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 93.4 | 96 | 96.4 | 96.6 | 96.5 | 96 | 96.3 | 93.1 | 95.7 | 96.2 | 96.3 | 96.2 | 95.7 | 96 | 92.3 | 94.9 | 95.8 | 95.9 | 95.7 | 95.2 | 95.5 | Perfect Galaxy250PVS-250 [480V]
Perfect Galaxy | PVS-375 [480V] | Y | N | N | 375 kW, 480 Vac, 3-phase Utility Interactive Inverter | 375 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 123.5 |  |  | 320 | 365 | 480 | 37.5 | 75 | 112.5 | 187.5 | 281.3 | 375 | 92.6 | 95.4 | 96 | 96.3 | 96.2 | 95.8 | 96 | 92.1 | 95.1 | 95.7 | 96 | 95.8 | 95.6 | 95.7 | 90.9 | 94.6 | 95 | 95.5 | 95.3 | 95.1 | 95.1 | Perfect Galaxy375PVS-375 [480V]
Perfect Galaxy | AE-500-60-PV-A [480V] | Y | N | N | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 208 |  |  | 330 | 405 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.2 | 94.9 | 95.7 | 95.8 | 95.6 | 95.2 | 95.5 | 91.8 | 94.5 | 95.4 | 95.5 | 95.4 | 94.9 | 95.2 | 91.3 | 93.7 | 94.6 | 95.1 | 95 | 94.8 | 94.8 | Perfect Galaxy500AE-500-60-PV-A [480V]
Perfect Galaxy | EQX0500US200X-N | Y | N | N | 500 kW, 3-phase Inverter, N for ground type | 500 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 171.5 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.9 | 96.1 | 96.5 | 96.6 | 96.1 | 95.6 | 96.2 | 93.6 | 96 | 96.5 | 96.5 | 96.1 | 95.6 | 96.1 | 92.7 | 95.5 | 96.1 | 96.2 | 95.9 | 95.5 | 95.8 | Perfect Galaxy500EQX0500US200X-N
Perfect Galaxy | EQX0500US200X-P | Y | N | N | 500 kW, 3-phase Inverter, P for ground type | 500 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 171.5 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.9 | 96.1 | 96.5 | 96.6 | 96.1 | 95.6 | 96.2 | 93.6 | 96 | 96.5 | 96.5 | 96.1 | 95.6 | 96.1 | 92.7 | 95.5 | 96.1 | 96.2 | 95.9 | 95.5 | 95.8 | Perfect Galaxy500EQX0500US200X-P
Perfect Galaxy | EQX0500US480T-N | Y | N | N | 500 kW, 3-phase Inverter, N for ground type | 500 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 116.5 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 92 | 95.4 | 96.2 | 96.7 | 96.6 | 96.4 | 96.3 | 91.7 | 95.3 | 96.1 | 96.6 | 96.6 | 96.5 | 96.3 | 90.8 | 94.8 | 95.8 | 96.4 | 96.4 | 96.3 | 96 | Perfect Galaxy500EQX0500US480T-N
Perfect Galaxy | EQX0500US480T-P | Y | N | N | 500 kW, 3-phase Inverter, P for ground type | 500 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 116.5 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 92 | 95.4 | 96.2 | 96.7 | 96.6 | 96.4 | 96.3 | 91.7 | 95.3 | 96.1 | 96.6 | 96.6 | 96.5 | 96.3 | 90.8 | 94.8 | 95.8 | 96.4 | 96.4 | 96.3 | 96 | Perfect Galaxy500EQX0500US480T-P
Perfect Galaxy | EQX0500UV320XP(N) | Y | N | N | 500 kW Utility Interactive Inverter | 500 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 96 |  |  | 515 | 590 | 800 | 50 | 100 | 150 | 250 | 375 | 500 | 94.8 | 96.8 | 97.2 | 97.4 | 97.1 | 96.5 | 97 | 94.3 | 96.4 | 97 | 97.3 | 97 | 96.5 | 96.9 | 93.1 | 95.6 | 96.5 | 96.9 | 96.7 | 96.2 | 96.5 | Perfect Galaxy500EQX0500UV320XP(N)
Perfect Galaxy | PVS-500 | Y | N | N | 500 kW, 3-phase Inverter for Medium Voltage Transformer | 500 |  | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2630 |  |  | 320 | 365 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.9 | 95.7 | 96.1 | 96 | 95.4 | 94.6 | 95.5 | 93.3 | 95.4 | 95.8 | 95.8 | 95.2 | 94.5 | 95.3 | 92.9 | 94.9 | 95.4 | 95.5 | 94.9 | 94.2 | 95 | Perfect Galaxy500PVS-500
Perfect Galaxy | PVS-500 [480V] | Y | N | N | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 131.1 |  |  | 315 | 365 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 92.9 | 95.7 | 96.2 | 96.5 | 96.4 | 96 | 96.2 | 92.4 | 95.4 | 96.1 | 96.3 | 96.2 | 95.8 | 96 | 91.8 | 95 | 95.7 | 96 | 95.8 | 95.3 | 95.6 | Perfect Galaxy500PVS-500 [480V]
Perfect Galaxy | SDMS0500UL320XN | Y | N | N | 500 kW, 320 V, 3-phase Inverter with combiner, N for ground type | 500 |  | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 98 |  |  | 300 | 430 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 90.51 | 94.95 | 95.18 | 95.47 | 95.31 | 94.7 | 95.09 | 91.29 | 93.9 | 95.72 | 95.96 | 95.59 | 95.09 | 95.4 | 90.71 | 93.8 | 95.8 | 95.9 | 95.76 | 95.19 | 95.46 | Perfect Galaxy500SDMS0500UL320XN
Perfect Galaxy | SDMS0500UL320XP | Y | N | N | 500 kW, 320 V, 3-phase Inverter with combiner, P for ground type | 500 |  | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 98 |  |  | 300 | 430 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 90.51 | 94.95 | 95.18 | 95.47 | 95.31 | 94.7 | 95.09 | 91.29 | 93.9 | 95.72 | 95.96 | 95.59 | 95.09 | 95.4 | 90.71 | 93.8 | 95.8 | 95.9 | 95.76 | 95.19 | 95.46 | Perfect Galaxy500SDMS0500UL320XP
Perfect Galaxy | SDMS0500UL480TN | Y | N | N | 500 kW, 480 V, 3-phase Inverter with combiner, N for ground type | 500 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 101 |  |  | 300 | 430 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 90.2 | 95.09 | 95.37 | 95.88 | 95.89 | 95.51 | 95.54 | 90.99 | 94.04 | 95.92 | 96.36 | 96.17 | 95.9 | 95.85 | 90.4 | 93.94 | 95.99 | 96.31 | 96.34 | 96 | 95.92 | Perfect Galaxy500SDMS0500UL480TN
Perfect Galaxy | SDMS0500UL480TP | Y | N | N | 500 kW, 480 V, 3-phase Inverter with combiner, P for ground type | 500 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 101 |  |  | 300 | 430 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 90.2 | 95.09 | 95.37 | 95.88 | 95.89 | 95.51 | 95.54 | 90.99 | 94.04 | 95.92 | 96.36 | 96.17 | 95.9 | 95.85 | 90.4 | 93.94 | 95.99 | 96.31 | 96.34 | 96 | 95.92 | Perfect Galaxy500SDMS0500UL480TP
Perfect Galaxy | PV-625-XRLS-VV-RVG | Y | N | N | 625 kW Utility Interactive Inverter | 625 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 259 |  |  | 500 | 600 | 800 | 62.5 | 125 | 187.5 | 312.5 | 468.75 | 625 | 94.45 | 96.6 | 97.05 | 97.11 | 96.78 | 96.24 | 96.75 | 93.64 | 96.19 | 96.72 | 96.86 | 96.55 | 96.02 | 96.47 | 92.24 | 95.31 | 96.07 | 96.36 | 96.13 | 95.62 | 95.95 | Perfect Galaxy625PV-625-XRLS-VV-RVG
Perfect Galaxy | PV-625-XRLS-VV-STG | Y | N | N | 625 kW Utility Interactive Inverter | 625 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 259 |  |  | 500 | 600 | 800 | 62.5 | 125 | 187.5 | 312.5 | 468.75 | 625 | 94.45 | 96.6 | 97.05 | 97.11 | 96.78 | 96.24 | 96.75 | 93.64 | 96.19 | 96.72 | 96.86 | 96.55 | 96.02 | 96.47 | 92.24 | 95.31 | 96.07 | 96.36 | 96.13 | 95.62 | 95.95 | Perfect Galaxy625PV-625-XRLS-VV-STG
Perfect Galaxy | EQX0630UV360XP(N) | Y | N | N | 630 KW Utility Interactive Inverter | 630 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 102 |  |  | 585 | 640 | 800 | 63 | 126 | 189 | 315 | 472.5 | 630 | 94.9 | 96.9 | 97.4 | 97.5 | 97.1 | 96.5 | 97.1 | 94.8 | 96.8 | 97.3 | 97.4 | 97 | 96.4 | 97 | 93.7 | 96.3 | 96.9 | 97.1 | 96.8 | 96.2 | 96.7 | Perfect Galaxy630EQX0630UV360XP(N)
Perfect Galaxy | PV-680-XRLS-VV-RVG | Y | N | N | 680 kW Utility Interactive Inverter | 680 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 265 |  |  | 560 | 650 | 800 | 68 | 136 | 204 | 340 | 510 | 680 | 94.55 | 96.58 | 97.1 | 97.19 | 96.93 | 96.44 | 96.87 | 93.9 | 96.22 | 96.8 | 96.98 | 96.74 | 96.25 | 96.63 | 92.87 | 95.59 | 96.32 | 96.61 | 96.43 | 95.94 | 96.24 | Perfect Galaxy680PV-680-XRLS-VV-RVG
Perfect Galaxy | PV-680-XRLS-VV-STG | Y | N | N | 680 kW Utility Interactive Inverter | 680 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 265 |  |  | 560 | 650 | 800 | 68 | 136 | 204 | 340 | 510 | 680 | 94.55 | 96.58 | 97.1 | 97.19 | 96.93 | 96.44 | 96.87 | 93.9 | 96.22 | 96.8 | 96.98 | 96.74 | 96.25 | 96.63 | 92.87 | 95.59 | 96.32 | 96.61 | 96.43 | 95.94 | 96.24 | Perfect Galaxy680PV-680-XRLS-VV-STG
Perfect Galaxy | EQX0750UV320XP(N) | Y | N | N | 750 kW Utility Interactive Inverter | 750 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 121 |  |  | 500 | 600 | 800 | 75 | 150 | 225 | 375 | 562.5 | 750 | 95.4 | 97.1 | 97.7 | 97.7 | 97.3 | 96.7 | 97.3 | 94.8 | 96.9 | 97.4 | 97.5 | 97.1 | 96.6 | 97.1 | 93.7 | 96.3 | 96.9 | 97.1 | 96.8 | 96.2 | 96.7 | Perfect Galaxy750EQX0750UV320XP(N)
Perfect Galaxy | EPP-1000-0600-32060-200X-U-N | Y | N | N | 1000 kW 3-phase Inverter, N for ground type | 1000 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 325.5 |  |  | 320 | 360 | 480 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.53 | 96.46 | 96.79 | 96.78 | 96.35 | 95.71 | 96.4 | 94.29 | 96.32 | 96.66 | 96.68 | 96.31 | 95.7 | 96.32 | 93.53 | 95.84 | 96.32 | 96.43 | 96.12 | 95.58 | 96.07 | Perfect Galaxy1000EPP-1000-0600-32060-200X-U-N
Perfect Galaxy | EPP-1000-0600-32060-200X-U-P | Y | N | N | 1000 kW 3-phase Inverter, P for ground type | 1000 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 325.5 |  |  | 320 | 360 | 480 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.53 | 96.46 | 96.79 | 96.78 | 96.35 | 95.71 | 96.4 | 94.29 | 96.32 | 96.66 | 96.68 | 96.31 | 95.7 | 96.32 | 93.53 | 95.84 | 96.32 | 96.43 | 96.12 | 95.58 | 96.07 | Perfect Galaxy1000EPP-1000-0600-32060-200X-U-P
Perfect Galaxy | EQX1000UV400XP(N) | Y | N | N | 1 MW Utility Interactive Inverter | 1000 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 124 |  |  | 615 | 700 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 95.4 | 97.2 | 97.7 | 97.8 | 97.5 | 97 | 97.5 | 94.9 | 97.1 | 97.5 | 97.7 | 97.4 | 96.8 | 97.3 | 94.4 | 96.8 | 97.3 | 97.6 | 97.3 | 96.8 | 97.2 | Perfect Galaxy1000EQX1000UV400XP(N)
Perfect Galaxy | PVS-1000 | Y | N | N | 1000 kW, 3-phase Inverter for Medium Voltage Transformer | 1000 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 396.4 |  |  | 420 | 486 | 670 | 100 | 200 | 300 | 500 | 750 | 1000 | 93.7 | 96.1 | 96.7 | 96.9 | 96.6 | 96.1 | 96.5 | 93.2 | 95.8 | 96.4 | 96.7 | 96.5 | 96 | 96.3 | 91.7 | 94.9 | 95.7 | 96.1 | 95.9 | 95.5 | 95.7 | Perfect Galaxy1000PVS-1000
Perfect Galaxy | EPP-1250-1000-52085-320X-U-N | Y | N | N | 1250 kW, 3-phase Inverter, N for ground type | 1250 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 320.4 |  |  | 525 | 595 | 800 | 125 | 250 | 375 | 625 | 937.5 | 1250 | 94.6 | 96.7 | 97.3 | 97.4 | 97.1 | 96.7 | 97 | 94.1 | 96.5 | 97.1 | 97.2 | 97 | 96.5 | 96.9 | 93 | 95.9 | 96.6 | 96.8 | 96.7 | 96.2 | 96.5 | Perfect Galaxy1250EPP-1250-1000-52085-320X-U-N
Perfect Galaxy | EPP-1250-1000-52085-320X-U-P | Y | N | N | 1250 kW, 3-phase Inverter, P for ground type | 1250 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 320.4 |  |  | 525 | 595 | 800 | 125 | 250 | 375 | 625 | 937.5 | 1250 | 94.6 | 96.7 | 97.3 | 97.4 | 97.1 | 96.7 | 97 | 94.1 | 96.5 | 97.1 | 97.2 | 97 | 96.5 | 96.9 | 93 | 95.9 | 96.6 | 96.8 | 96.7 | 96.2 | 96.5 | Perfect Galaxy1250EPP-1250-1000-52085-320X-U-P
Perfect Galaxy International Ltd | EQMX0500UV320XN [320V] | Y | N | N | 500kW, 320Vac Utility Interactive Inverter, Support negative grounded at PV side | 500 | 320 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Efficiency data inclusive of transformer effect based on 500 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE2016. | 106.8 |  |  | 500 | 600 | 800 | 50 | 100 | 150 | 250 | 375 | 500 | 95.9 | 97.4 | 97.6 | 97.8 | 97.6 | 97.1 | 97.5 | 95.3 | 97.1 | 97.4 | 97.7 | 97.4 | 97 | 97.4 | 93.8 | 96.6 | 97.2 | 97.4 | 97.2 | 96.8 | 97 | Perfect Galaxy International Ltd500EQMX0500UV320XN | 2017-11-15 | 2018-04-16
Perfect Galaxy International Ltd | EQMX0500UV320XP [320V] | Y | N | N | 500kW, 320Vac Utility Interactive Inverter, Support positive grounded at PV side | 500 | 320 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Efficiency data inclusive of transformer effect based on 500 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE2016. | 106.8 |  |  | 500 | 600 | 800 | 50 | 100 | 150 | 250 | 375 | 500 | 95.9 | 97.4 | 97.6 | 97.8 | 97.6 | 97.1 | 97.5 | 95.3 | 97.1 | 97.4 | 97.7 | 97.4 | 97 | 97.4 | 93.8 | 96.6 | 97.2 | 97.4 | 97.2 | 96.8 | 97 | Perfect Galaxy International Ltd500EQMX0500UV320XP | 2017-11-15 | 2018-04-16
Perfect Galaxy International Ltd | EQMX0630UV400XN [400V] | Y | N | N | 630kW, 400Vac Utility Interactive Inverter, Support negative grounded at PV side | 630 | 400 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Efficiency data inclusive of transformer effect based on 630 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE2016. | 138 |  |  | 615 | 700 | 800 | 63 | 126 | 189 | 315 | 472.5 | 630 | 95.7 | 97.3 | 97.7 | 97.9 | 97.5 | 97.2 | 97.5 | 95.3 | 97.1 | 97.6 | 97.7 | 97.4 | 97.2 | 97.4 | 94.6 | 96.7 | 97.3 | 97.6 | 97.3 | 97 | 97.2 | Perfect Galaxy International Ltd630EQMX0630UV400XN | 2017-11-15 | 2018-04-16
Perfect Galaxy International Ltd | EQMX0630UV400XP [400V] | Y | N | N | 630kW, 400Vac Utility Interactive Inverter, Support positive grounded at PV side | 630 | 400 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Efficiency data inclusive of transformer effect based on 630 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE2016. | 138 |  |  | 615 | 700 | 800 | 63 | 126 | 189 | 315 | 472.5 | 630 | 95.7 | 97.3 | 97.7 | 97.9 | 97.5 | 97.2 | 97.5 | 95.3 | 97.1 | 97.6 | 97.7 | 97.4 | 97.2 | 97.4 | 94.6 | 96.7 | 97.3 | 97.6 | 97.3 | 97 | 97.2 | Perfect Galaxy International Ltd630EQMX0630UV400XP | 2017-11-15 | 2018-04-16
Perfect Galaxy International Ltd. | EQX0500UV320XP(N) | Y | N | N | 500 kW Utility Interactive Inverter | 500 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 96 |  |  | 500 | 590 | 800 | 50 | 100 | 150 | 250 | 375 | 500 | 95.0415 | 97.2448 | 97.2893 | 97.1457 | 97.1723 | 96.4538 | 97.0632 | 94.3159 | 96.376 | 97.0243 | 97.3081 | 96.9975 | 96.4884 | 96.9022 | 93.126 | 95.6022 | 96.4659 | 96.9144 | 96.6959 | 96.2151 | 96.4926 | Perfect Galaxy International Ltd.500EQX0500UV320XP(N)
Petra Solar | 103.10866.500x [120V] | Y | N | N | 212 W, 120 Vac Inverter, where x = 1, 2, 3, or 4 | 0.2 | 120 | 93 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 1.59 |  |  | 29 | 35 | 40 | 0.02 | 0.04 | 0.06 | 0.1 | 0.15 | 0.2 | 85.3 | 91.2 | 92.3 | 93.3 | 93.6 | 93.4 | 92.9 | 85.6 | 91.1 | 92.4 | 93.2 | 93.7 | 93.6 | 93 | 84.7 | 90.8 | 92.2 | 93.1 | 93.6 | 93.7 | 92.8 | Petra Solar0.2103.10866.500x [120V]
Petra Systems | 103.10400.0002 [240V] | Y | N | N | 240 W, 240 Vac Utility Interactive Microinverter | 0.24 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.14 |  |  | 30 | 35 | 40 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 91.9 | 95.3 | 96 | 96.2 | 96.4 | 96.2 | 96 | 90.9 | 95 | 95.8 | 96.2 | 96.3 | 96.3 | 96 | 89.7 | 94.7 | 95.6 | 96.2 | 96.3 | 96.3 | 95.8 | Petra Systems0.24103.10400.0002 [240V]
Petra Systems | 103.10400.0001 [120V] | Y | N | N | 241 W, Utility Interactive, 120 Vac Microinverter | 0.241 | 120 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.05 |  |  | 30 | 35 | 40 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 93.4 | 95.7 | 96.1 | 95.9 | 96.1 | 95.7 | 95.9 | 92.7 | 95.5 | 96 | 96 | 96 | 95.8 | 95.9 | 91.6 | 95.2 | 95.9 | 96.1 | 96 | 95.8 | 95.8 | Petra Systems0.241103.10400.0001 [120V]
Phoenixtec Power | PS240US3R [208V] | Y | N | N | 4000 W, 208 Vac Utility Interactive Inverter | 4 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 60.3 |  |  | 100 | 310 | 360 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 90.2 | 93.8 | 95.1 | 95.6 | 95.3 | 94.8 | 95 | 90.7 | 94.3 | 95.4 | 95.8 | 95.6 | 95.2 | 95.3 | 91.5 | 94.6 | 95.8 | 96 | 95.8 | 95.3 | 95.6 | Phoenixtec Power4PS240US3R [208V]
Phoenixtec Power | PS240US3R [240V] | Y | N | N | 4000 W, 240 Vac Utility Interactive Inverter | 4 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 39 |  |  | 100 | 310 | 360 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 89.6 | 93.5 | 94.9 | 95.8 | 95.7 | 95.3 | 95.2 | 90.3 | 93.9 | 95.1 | 96.1 | 96 | 95.9 | 95.6 | 90 | 93.9 | 95.5 | 95.9 | 96 | 95.9 | 95.6 | Phoenixtec Power4PS240US3R [240V]
Phono Solar Technology | PS240M-20/U-AC | Y | N | N | 212 W Inverter | 0.212 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16 | Phono Solar Technology0.212PS240M-20/U-AC
Phono Solar Technology | PS240P-20/U-AC | Y | N | N | 212 W Inverter | 0.212 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16 | Phono Solar Technology0.212PS240P-20/U-AC
Phono Solar Technology | PS245M-20/U-AC | Y | N | N | 212 W Inverter | 0.212 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16 | Phono Solar Technology0.212PS245M-20/U-AC
Phono Solar Technology | PS245P-20/U-AC | Y | N | N | 212 W Inverter | 0.212 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16 | Phono Solar Technology0.212PS245P-20/U-AC
Phono Solar Technology | PS250M-20/U-AC | Y | N | N | 212 W Inverter | 0.212 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16 | Phono Solar Technology0.212PS250M-20/U-AC
Phono Solar Technology | PS250P-20/U-AC | Y | N | N | 212 W Inverter | 0.212 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16 | Phono Solar Technology0.212PS250P-20/U-AC
Phono Solar Technology | PS255M-20/U-AC | Y | N | N | 212 W Inverter | 0.212 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16 | Phono Solar Technology0.212PS255M-20/U-AC
Phono Solar Technology | PS255P-20/U-AC | Y | N | N | 212 W Inverter | 0.212 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16 | Phono Solar Technology0.212PS255P-20/U-AC
Phono Solar Technology | PS260M-20/U-AC | Y | N | N | 212 W Inverter | 0.212 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16 | Phono Solar Technology0.212PS260M-20/U-AC
Phono Solar Technology | PS260P-20/U-AC | Y | N | N | 212 W Inverter | 0.212 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.0212 | 0.0424 | 0.0636 | 0.106 | 0.159 | 0.212 | 87.88 | 94.35 | 95.79 | 95.73 | 94.8 | 93.45 | 94.75 | 85.23 | 92.51 | 94.56 | 95.3 | 95.12 | 94.17 | 94.52 | 83.57 | 92.02 | 94.33 | 94.87 | 94.87 | 93.91 | 94.16 | Phono Solar Technology0.212PS260P-20/U-AC
Pika Energy | X3001-NA | Y | N | N | Grid-tie Inverter for interconnection with a Rebus DC microgrid | 3 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.64 |  |  | 100 | 398 | 400 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 94 | 96 | 96.3 | 96.3 | 96 | 95.6 | 96 | 93.9 | 96 | 96.3 | 96.3 | 96 | 95.5 | 96 | 93.9 | 95.9 | 96.3 | 96.3 | 96 | 95.5 | 96 | Pika Energy3X3001-NA
Pika Energy | X7603 [240V] | Y | Y | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.585 | 240 | 96.5 | [11/22/2017] | [11430] | 2018-10-15 | N | N |  | 1.29 |  |  | 390 | 400 | 420 | 0.76 | 1.52 | 2.28 | 3.79 | 5.69 | 7.59 | 91.7 | 95.9 | 96.6 | 97.3 | 97.2 | 97 | 96.9 | 91 | 95.4 | 96.5 | 97.3 | 97.1 | 97 | 96.8 | 90.5 | 95.2 | 96.3 | 96.9 | 97 | 96.9 | 96.5 | Pika Energy7.585X7603 [240V] [SI1] | 2018-04-02 | 2018-10-15
Pika Energy | X7601 [240V] | Y | Y | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.587 | 240 | 96.5 | [11/22/2017] | [11430] | 2018-10-15 | Y | N |  | 1.29 |  |  | 390 | 400 | 420 | 0.76 | 1.52 | 2.28 | 3.79 | 5.69 | 7.59 | 91.7 | 95.9 | 96.6 | 97.3 | 97.2 | 97 | 96.9 | 91 | 95.4 | 96.5 | 97.3 | 97.1 | 97 | 96.8 | 90.5 | 95.2 | 96.3 | 96.9 | 97 | 96.9 | 96.5 | Pika Energy7.587X7601 [SI1] | 2017-12-15 | 2018-10-15
Pika Energy | X7602 [240V] | Y | Y | Y | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.587 | 240 | 96.5 | [11/22/2017] | [11430] | 2018-10-15 | Y | N |  | 1.29 |  |  | 390 | 400 | 420 | 0.76 | 1.52 | 2.28 | 3.79 | 5.69 | 7.59 | 91.7 | 95.9 | 96.6 | 97.3 | 97.2 | 97 | 96.9 | 91 | 95.4 | 96.5 | 97.3 | 97.1 | 97 | 96.8 | 90.5 | 95.2 | 96.3 | 96.9 | 97 | 96.9 | 96.5 | Pika Energy7.587X7602 [SI1] | 2017-12-15 | 2018-10-15
Pika Energy | X11403 [208V] | Y | Y | Y | 11.4 kW, 208 Vac Grid Support Utility Interactive Inverter | 11.18 | 208 | 97.5 | [11/22/2017] | [11430] | 2018-10-15 | N | N |  | 0.13 |  |  | 390 | 400 | 420 | 1.12 | 2.24 | 3.35 | 5.59 | 8.39 | 11.18 | 97.2 | 97.4 | 97.6 | 97.6 | 97.4 | 97.1 | 97.5 | 97 | 97.3 | 97.7 | 97.5 | 97.3 | 96.9 | 97.3 | 95.8 | 97.2 | 97.3 | 97.4 | 97.1 | 96.9 | 97.1 | Pika Energy11.18X11403 [208V] [SI1] | 2018-04-02 | 2018-10-15
Pika Energy | X11402 [208V] | Y | Y | Y | 11.4 kW, 208 Vac Grid Support Utility Interactive Inverter | 11.187 | 208 | 97.5 | [11/22/2017] | [11430] | 2018-10-15 | Y | N |  | 0.13 |  |  | 390 | 400 | 420 | 1.12 | 2.24 | 3.36 | 5.59 | 8.39 | 11.19 | 97.2 | 97.4 | 97.6 | 97.6 | 97.4 | 97.1 | 97.5 | 97 | 97.3 | 97.7 | 97.5 | 97.3 | 96.9 | 97.3 | 95.8 | 97.2 | 97.3 | 97.4 | 97.1 | 96.9 | 97.1 | Pika Energy11.187X11402 [SI1] | 2017-12-15 | 2018-10-15
Power Electronics | FS0300CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 300 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 232 |  |  | 585 | 650 | 800 | 30 | 60 | 90 | 150 | 225 | 300 | 95.2 | 96.6 | 96.6 | 97.2 | 97.1 | 96.4 | 96.9 | 95.1 | 96.4 | 96.4 | 97 | 96.9 | 96.4 | 96.7 | 94.3 | 95.7 | 95.6 | 96.4 | 96.4 | 95.8 | 96.2 | Power Electronics300FS0300CU
Power Electronics | FS0300PU | Y | N | N | Utility Interactive Photovoltaic Inverter | 300 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 232 |  |  | 585 | 650 | 800 | 30 | 60 | 90 | 150 | 225 | 300 | 95.2 | 96.6 | 96.6 | 97.2 | 97.1 | 96.4 | 96.9 | 95.1 | 96.4 | 96.4 | 97 | 96.9 | 96.4 | 96.7 | 94.3 | 95.7 | 95.6 | 96.4 | 96.4 | 95.8 | 96.2 | Power Electronics300FS0300PU
Power Electronics | FS0450CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 450 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 256 |  |  | 545 | 650 | 800 | 45 | 90 | 135 | 225 | 337.5 | 450 | 95 | 96.9 | 97.1 | 97.3 | 97.1 | 96.6 | 97.1 | 94.9 | 96.7 | 96.9 | 97.2 | 97 | 96.6 | 96.9 | 94.2 | 96.4 | 96.4 | 96.8 | 96.6 | 96.1 | 96.5 | Power Electronics450FS0450CU
Power Electronics | FS0450PU | Y | N | N | Utility Interactive Photovoltaic Inverter | 450 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 256 |  |  | 545 | 650 | 800 | 45 | 90 | 135 | 225 | 337.5 | 450 | 95 | 96.9 | 97.1 | 97.3 | 97.1 | 96.6 | 97.1 | 94.9 | 96.7 | 96.9 | 97.2 | 97 | 96.6 | 96.9 | 94.2 | 96.4 | 96.4 | 96.8 | 96.6 | 96.1 | 96.5 | Power Electronics450FS0450PU
Power Electronics | FS0501CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 499.9 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 477.9 |  |  | 500 | 575 | 800 | 49.98 | 99.97 | 150 | 249.9 | 374.9 | 499.9 | 94.3 | 96.3 | 96.8 | 97 | 96.8 | 96.4 | 96.7 | 94 | 96.2 | 96.6 | 96.8 | 96.6 | 96.2 | 96.5 | 93.1 | 95.5 | 96 | 96.1 | 96 | 95.7 | 95.9 | Power Electronics499.9FS0501CU
Power Electronics | FS0560CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 560 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 602 |  |  | 330 | 400 | 480 | 56 | 112 | 168 | 280 | 420 | 560 | 94.3 | 95.8 | 96.2 | 96.4 | 96.1 | 95.4 | 96.1 | 94 | 95.6 | 96 | 96.1 | 95.9 | 95.3 | 95.8 | 93.8 | 95.3 | 95.6 | 95.8 | 95.6 | 95 | 95.5 | Power Electronics560FS0560CU
Power Electronics | FS0560PU | Y | N | N | Utility Interactive Photovoltaic Inverter | 560 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 602 |  |  | 330 | 400 | 480 | 56 | 112 | 168 | 280 | 420 | 560 | 94.3 | 95.8 | 96.2 | 96.4 | 96.1 | 95.4 | 96.1 | 94 | 95.6 | 96 | 96.1 | 95.9 | 95.3 | 95.8 | 93.8 | 95.3 | 95.6 | 95.8 | 95.6 | 95 | 95.5 | Power Electronics560FS0560PU
Power Electronics | FS0600PU | Y | N | N | Utility Interactive Photovoltaic Inverter | 600 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 281 |  |  | 585 | 650 | 800 | 60 | 120 | 180 | 300 | 450 | 600 | 95.6 | 97 | 97.4 | 97.5 | 97.3 | 96.7 | 97.3 | 95.3 | 96.7 | 97.3 | 97.4 | 97.1 | 96.7 | 97.1 | 94.9 | 96.1 | 96.9 | 97 | 96.7 | 96.4 | 96.7 | Power Electronics600FS0600PU
Power Electronics | FS0640CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 640 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 629 |  |  | 330 | 400 | 480 | 64 | 128 | 192 | 320 | 480 | 640 | 94.3 | 95.8 | 96.3 | 96.4 | 96.1 | 95.3 | 96.1 | 94 | 95.6 | 96 | 96.1 | 95.9 | 95.3 | 95.8 | 93.8 | 95.3 | 95.7 | 95.8 | 95.6 | 95 | 95.5 | Power Electronics640FS0640CU
Power Electronics | FS0640PU | Y | N | N | Utility Interactive Photovoltaic Inverter | 640 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 629 |  |  | 330 | 400 | 480 | 64 | 128 | 192 | 320 | 480 | 640 | 94.3 | 95.8 | 96.3 | 96.4 | 96.1 | 95.3 | 96.1 | 94 | 95.6 | 96 | 96.1 | 95.9 | 95.3 | 95.8 | 93.8 | 95.3 | 95.7 | 95.8 | 95.6 | 95 | 95.5 | Power Electronics640FS0640PU
Power Electronics | FS0600CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 680 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 249 |  |  | 552 | 620 | 800 | 68 | 136 | 204 | 340 | 510 | 680 | 95.1 | 97 | 97.5 | 97.7 | 97.5 | 97 | 97.4 | 94.9 | 96.7 | 97.2 | 97.4 | 97.2 | 96.7 | 97.1 | 94.3 | 96.3 | 96.8 | 97 | 96.8 | 96.4 | 96.7 | Power Electronics680FS0600CU
Power Electronics | FS0750CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 750 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 506.3 |  |  | 500 | 575 | 800 | 75 | 150 | 225 | 375 | 562.5 | 750 | 95 | 96.7 | 97 | 97.1 | 97.1 | 96.6 | 96.9 | 94.8 | 96.5 | 96.8 | 96.9 | 96.8 | 96.4 | 96.7 | 94.2 | 95.8 | 96.2 | 96.3 | 96.3 | 95.9 | 96.1 | Power Electronics750FS0750CU
Power Electronics | FS0751PU | Y | N | N | Utility Interactive Photovoltaic Inverter | 751 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 306 |  |  | 585 | 650 | 800 | 75.1 | 150.2 | 225.3 | 375.5 | 563.3 | 751 | 95.4 | 97 | 97.4 | 97.4 | 97.3 | 96.7 | 97.2 | 95.3 | 96.8 | 97.2 | 97.2 | 97.2 | 96.7 | 97.1 | 94.9 | 96.3 | 96.7 | 96.8 | 96.8 | 96.4 | 96.7 | Power Electronics751FS0751PU
Power Electronics | FS0701CU [360V] | Y | N | N | Utility Interactive modular Inverter: 360Vac, 780 kW, with MV NEMA TP1 transformer | 780 | 360 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 254 |  |  | 510 | 590 | 800 | 78 | 156 | 234 | 390 | 585 | 780 | 95.3 | 97.1 | 97.5 | 97.6 | 97.4 | 96.8 | 97.3 | 95 | 96.7 | 97.1 | 97.3 | 97 | 96.4 | 96.9 | 94.5 | 96.1 | 96.6 | 96.8 | 96.5 | 96.1 | 96.4 | Power Electronics780FS0701CU [360V]
Power Electronics | FS0830PU | Y | N | N | Utility Interactive Photovoltaic Inverter | 830 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 466 |  |  | 540 | 606 | 800 | 83 | 166 | 249 | 415 | 622.5 | 830 | 95.6 | 97.2 | 97.5 | 97.7 | 97.4 | 96.8 | 97.4 | 95.5 | 97 | 97.4 | 97.5 | 97.3 | 96.8 | 97.2 | 95 | 96.5 | 96.8 | 96.9 | 96.8 | 96.4 | 96.7 | Power Electronics830FS0830PU
Power Electronics | FS0751CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 850 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 260 |  |  | 552 | 620 | 800 | 85 | 170 | 255 | 425 | 637.5 | 850 | 95.9 | 97.4 | 97.8 | 97.9 | 97.6 | 97.1 | 97.6 | 95.6 | 97.1 | 97.5 | 97.6 | 97.3 | 96.8 | 97.3 | 95.2 | 96.7 | 97 | 97.2 | 96.9 | 96.4 | 96.9 | Power Electronics850FS0751CU
Power Electronics | FS0900PU | Y | N | N | Utility Interactive Photovoltaic Inverter | 900 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 332 |  |  | 545 | 615 | 332 | 90 | 180 | 270 | 450 | 675 | 900 | 95.8 | 97.2 | 97.5 | 97.6 | 97.5 | 96.9 | 97.4 | 95.6 | 97.1 | 97.3 | 97.4 | 97.3 | 96.9 | 97.2 | 95.3 | 96.6 | 96.7 | 97 | 96.9 | 96.6 | 96.8 | Power Electronics900FS0900PU
Power Electronics | FS0830CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 930 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 295 |  |  | 510 | 590 | 800 | 93 | 186 | 279 | 465 | 697.5 | 930 | 95.6 | 97.2 | 97.6 | 97.7 | 97.5 | 96.9 | 97.4 | 95.1 | 96.9 | 97.3 | 97.4 | 97.1 | 96.6 | 97.1 | 94.8 | 96.4 | 96.8 | 96.8 | 96.6 | 96.1 | 96.6 | Power Electronics930FS0830CU
Power Electronics | FS0970CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 970 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 491 |  |  | 545 | 615 | 800 | 97 | 194 | 291 | 485 | 727.5 | 970 | 95.8 | 97.2 | 97.5 | 97.6 | 97.4 | 96.8 | 97.4 | 95.5 | 97 | 97.3 | 97.5 | 97.3 | 96.8 | 97.2 | 95.1 | 96.6 | 96.7 | 96.9 | 96.8 | 96.4 | 96.7 | Power Electronics970FS0970CU
Power Electronics | FS0970PU | Y | N | N | Utility Interactive Photovoltaic Inverter | 970 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 491 |  |  | 545 | 615 | 800 | 97 | 194 | 291 | 485 | 727.5 | 970 | 95.8 | 97.2 | 97.5 | 97.6 | 97.4 | 96.8 | 97.4 | 95.5 | 97 | 97.3 | 97.5 | 97.3 | 96.8 | 97.2 | 95.1 | 96.6 | 96.7 | 96.9 | 96.8 | 96.4 | 96.7 | Power Electronics970FS0970PU
Power Electronics | FS0901CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 1000 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 266 |  |  | 584 | 650 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 95.4 | 97 | 97.4 | 97.5 | 97.2 | 96.6 | 97.2 | 95.3 | 96.9 | 97.3 | 97.4 | 97 | 96.5 | 97 | 95 | 96.6 | 97 | 97.1 | 96.8 | 96.3 | 96.8 | Power Electronics1000FS0901CU
Power Electronics | FS1001CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 1000 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 615.6 |  |  | 500 | 575 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 95.4 | 97 | 97.4 | 97.5 | 97.3 | 96.9 | 97.3 | 95.2 | 96.8 | 97.2 | 97.3 | 97.1 | 96.7 | 97.1 | 94.7 | 96.2 | 96.6 | 96.7 | 96.6 | 96.2 | 96.5 | Power Electronics1000FS1001CU
Power Electronics | FS1004CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 1000 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 265.579 |  |  | 584 | 650 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 95.4 | 97 | 97.4 | 97.5 | 97.2 | 96.6 | 97.2 | 95.3 | 96.9 | 97.3 | 97.4 | 97 | 96.5 | 97 | 95 | 96.5886 | 97 | 97.1 | 96.8 | 96.3 | 96.8 | Power Electronics1000FS1004CU
Power Electronics | FS0900CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 1020 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 276 |  |  | 552 | 620 | 800 | 102 | 204 | 306 | 510 | 765 | 1020 | 95.8 | 97.5 | 97.9 | 97.9 | 97.7 | 97.2 | 97.7 | 95.5 | 97.1 | 97.5 | 97.6 | 97.3 | 96.8 | 97.3 | 94.8 | 96.6 | 97.1 | 97.2 | 96.9 | 96.4 | 96.8 | Power Electronics1020FS0900CU
Power Electronics | FS0940CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 1050 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 274 |  |  | 616 | 670 | 800 | 105 | 210 | 315 | 525 | 787.5 | 1050 | 95.3 | 97 | 97.4 | 97.5 | 97.2 | 96.7 | 97.2 | 95.2 | 96.9 | 97.3 | 97.4 | 97.1 | 96.6 | 97.1 | 94.9 | 96.6 | 97.1 | 97.2 | 96.9 | 96.4 | 96.9 | Power Electronics1050FS0940CU
Power Electronics | FS1050PU | Y | N | N | Utility Interactive Photovoltaic Inverter | 1050 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 356 |  |  | 545 | 615 | 800 | 120 | 240 | 360 | 600 | 900 | 1200 | 95.8 | 96.8 | 97.4 | 97.6 | 97.5 | 96.9 | 97.4 | 95.3 | 96.6 | 97.1 | 97.3 | 97.3 | 96.9 | 97.2 | 95.7 | 95.7 | 96.6 | 97 | 96.9 | 96.6 | 96.7 | Power Electronics1050FS1050PU
Power Electronics | FS1051CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 1050 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 274 |  |  | 616 | 670 | 800 | 105 | 210 | 315 | 525 | 787.5 | 1050 | 95.3 | 97 | 97.4 | 97.5 | 97.2 | 96.7 | 97.2 | 95.2 | 96.9 | 97.3 | 97.4 | 97.1 | 96.6 | 97.1 | 94.9 | 96.6 | 97.1 | 97.2 | 96.9 | 96.4 | 96.9 | Power Electronics1050FS1051CU
Power Electronics | FS1003CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 1100 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 317 |  |  | 510 | 590 | 800 | 110 | 220 | 330 | 550 | 825 | 1100 | 95.8 | 97.3 | 97.8 | 97.8 | 97.6 | 97 | 97.6 | 95.5 | 97 | 97.4 | 97.5 | 97.2 | 96.6 | 97.2 | 94.9 | 96.6 | 96.9 | 97 | 96.7 | 96.2 | 96.7 | Power Electronics1100FS1003CU
Power Electronics | FS01110PU | Y | N | N | Utility Interactive Photovoltaic Inverter | 1110 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 558 |  |  | 545 | 615 | 800 | 111 | 222 | 333 | 555 | 832.5 | 1110 | 95.7 | 97.1 | 97.1 | 97.7 | 97.6 | 96.9 | 97.4 | 95.6 | 96.9 | 96.9 | 97.4 | 97.4 | 96.9 | 97.2 | 94.8 | 96.1 | 96.1 | 96.9 | 96.9 | 96.3 | 96.6 | Power Electronics1110FS01110PU
Power Electronics | FS1000CU [440V] | Y | N | N | 1110 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1110 | 440 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 281 |  |  | 642 | 690 | 800 | 111 | 222 | 333 | 555 | 832.5 | 1110 | 95.4 | 97 | 97.4 | 97.5 | 97.2 | 96.7 | 97.2 | 95.3 | 96.9 | 97.4 | 97.4 | 97.2 | 96.7 | 97.1 | 95.1 | 96.7 | 97.1 | 97.2 | 97 | 96.6 | 97 | Power Electronics1110FS1000CU [440V]
Power Electronics | FS1112CU [440V] | Y | N | N | 1110 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1110 | 440 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 281.407 |  |  | 642 | 690 | 800 | 111 | 222 | 333 | 555 | 832.5 | 1110 | 95.4 | 97 | 97.4 | 97.5 | 97.2 | 96.7 | 97.2 | 95.3 | 96.9 | 97.4 | 97.4 | 97.2 | 96.7 | 97.1 | 95.1 | 96.7 | 97.1 | 97.2 | 97 | 96.6 | 97 | Power Electronics1110FS1112CU [440V]
Power Electronics | FS1050CU15 [565V] | Y | Y | y | 1050 kW, 565 Vac Grid Support Utility Interactive Inverter with combiner box | 1163.5 | 565 | 97 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 1050 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 338.51 |  |  | 800 | 900 | 1200 | 116 | 233 | 349 | 582 | 873 | 1164 | 93 | 96.2 | 96.7 | 97.5 | 97.6 | 97.5 | 97.2 | 93 | 96.1 | 96.7 | 97.4 | 97.5 | 97.3 | 97.1 | 93.2 | 96.2 | 96.6 | 97.4 | 97.6 | 97.3 | 97.2 | Power Electronics1163.5FS1050CU15 [565V] | 2018-05-15 | 2018-10-15
Power Electronics | FS1100CU15O3 [600V] | Y | Y | y | 1100 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant | 1176.44 | 600 | 98 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 1100 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 358.91 |  |  | 849 | 940 | 1200 | 118 | 235 | 353 | 588 | 882 | 1176 | 95.9 | 97.5 | 97.7 | 98 | 98 | 98 | 97.9 | 95.8 | 97.4 | 97.7 | 98 | 97.9 | 97.9 | 97.8 | 95.8 | 97.4 | 97.7 | 98 | 97.9 | 97.9 | 97.8 | Power Electronics1176.44FS1100CU15O3 [600V] | 2018-05-15 | 2018-10-15
Power Electronics | FS1050CU | Y | N | N | 1050 kW Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1190 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 314 |  |  | 552 | 620 | 800 | 119 | 238 | 357 | 595 | 892.5 | 1190 | 95.9 | 97.5 | 97.8 | 97.9 | 97.7 | 97.1 | 97.6 | 95.6 | 97.1 | 97.5 | 97.5 | 97.3 | 96.8 | 97.3 | 94.9 | 96.5 | 97 | 97.1 | 96.9 | 96.4 | 96.8 | Power Electronics1190FS1050CU
Power Electronics | FS1080CU [400V] | Y | N | N | 1200 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1200 | 400 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 289 |  |  | 584 | 650 | 800 | 120 | 240 | 360 | 600 | 900 | 1200 | 95.5 | 97 | 97.4 | 97.5 | 97.2 | 96.7 | 97.2 | 95.4 | 96.9 | 97.3 | 97.4 | 97.1 | 96.5 | 97 | 95.1 | 96.6 | 97 | 97.1 | 96.8 | 96.3 | 96.8 | Power Electronics1200FS1080CU [400V]
Power Electronics | FS1200CU | Y | N | N | 1200 kW Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1200 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 630 |  |  | 545 | 615 | 800 | 120 | 240 | 360 | 600 | 900 | 1200 | 95.8 | 96.6 | 97.1 | 97.7 | 97.6 | 96.9 | 97.4 | 95 | 96.2 | 96.9 | 97.5 | 97.4 | 97 | 97.2 | 95.6 | 95.4 | 96.2 | 97.1 | 96.9 | 96.5 | 96.7 | Power Electronics1200FS1200CU
Power Electronics | FS1200PU | Y | N | N | 1200 kW Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1200 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 630 |  |  | 545 | 615 | 800 | 120 | 240 | 360 | 600 | 900 | 1200 | 95.8 | 96.6 | 97.1 | 97.7 | 97.6 | 96.9 | 97.4 | 95 | 96.2 | 96.9 | 97.5 | 97.4 | 97 | 97.2 | 95.6 | 95.4 | 96.2 | 97.1 | 96.9 | 96.5 | 96.7 | Power Electronics1200FS1200PU
Power Electronics | FS1201CU [400V] | Y | N | N | 1200 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1200 | 400 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 289 |  |  | 584 | 650 | 800 | 120 | 240 | 360 | 600 | 900 | 1200 | 98.1 | 98.3 | 98.4 | 98.4 | 98.2 | 98.1 | 98.3 | 98 | 98.2 | 98.2 | 98.3 | 98.1 | 97.9 | 98.2 | 97.7 | 97.9 | 97.9 | 98 | 97.9 | 97.7 | 97.9 | Power Electronics1200FS1201CU [400V]
Power Electronics | FS1100CU15 [600V] | Y | Y | y | 1100 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box | 1209.25 | 600 | 97 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 1100 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 347.22 |  |  | 849 | 940 | 1200 | 121 | 242 | 363 | 605 | 907 | 1209 | 93.1 | 96.2 | 96.8 | 97.5 | 97.8 | 97.7 | 97.3 | 93.1 | 96.1 | 96.8 | 97.5 | 97.6 | 97.6 | 97.2 | 93.2 | 96.2 | 96.7 | 97.5 | 97.7 | 97.5 | 97.2 | Power Electronics1209.25FS1100CU15 [600V] | 2018-05-15 | 2018-10-15
Power Electronics | FS01110CU | Y | N | N | Utility Interactive Photovoltaic Inverter | 1250 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 340 |  |  | 510 | 590 | 800 | 125 | 250 | 375 | 625 | 937.5 | 1250 | 95.7 | 97.4 | 97.8 | 97.8 | 97.5 | 96.9 | 97.5 | 95.3 | 97 | 97.4 | 97.4 | 97.1 | 96.6 | 97.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.6 | 96.1 | 96.6 | Power Electronics1250FS01110CU
Power Electronics | FS1250PU | Y | N | N | 1250 kW Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1250 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 630 |  |  | 585 | 650 | 800 | 125 | 250 | 375 | 625 | 937.5 | 1250 | 95 | 96.7 | 97.2 | 97.4 | 97.2 | 96.6 | 97.1 | 94.7 | 96.6 | 97 | 97.1 | 97 | 96.6 | 96.9 | 94.3 | 96.1 | 96.6 | 96.7 | 96.6 | 96.2 | 96.5 | Power Electronics1250FS1250PU
Power Electronics | FS1140CU [420V] | Y | N | N | 1270 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1270 | 420 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted Efficiency includes MV TP1 Transformer efficiency. | 296 |  |  | 616 | 670 | 800 | 127 | 254 | 381 | 653 | 952.2 | 1270 | 95.6 | 97 | 97.4 | 97.6 | 97.2 | 96.7 | 97.2 | 95.5 | 96.9 | 97.3 | 97.5 | 97.1 | 96.6 | 97.1 | 95.2 | 96.7 | 97.1 | 97.2 | 96.9 | 96.4 | 96.9 | Power Electronics1270FS1140CU [420V] |  | 2018-02-15
Power Electronics | FS1271CU [420V] | Y | N | N | 1270 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1270 | 420 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 296 |  |  | 616 | 670 | 800 | 127 | 254 | 381 | 635 | 952.5 | 1270 | 98.2 | 98.3 | 98.4 | 98.5 | 98.3 | 98.1 | 98.3 | 98.1 | 98.2 | 98.3 | 98.4 | 98.2 | 98 | 98.2 | 97.8 | 98 | 98.1 | 98.1 | 98 | 97.8 | 98 | Power Electronics1270FS1271CU [420V]
Power Electronics | FS1290CU [330V] | Y | N | N | 1290.0 kW, 330 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1290 | 330 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 603 |  |  | 500 | 575 | 800 | 129 | 258 | 387 | 645 | 967.5 | 1290 | 95.3 | 97 | 97.4 | 97.5 | 97.2 | 96.6 | 97.2 | 95.1 | 96.7 | 97.2 | 97.2 | 97 | 96.5 | 97 | 94.4 | 96.2 | 96.5 | 96.6 | 96.4 | 96 | 96.3 | Power Electronics1290FS1290CU [330V]
Power Electronics | FS1200CU15 [645V] | Y | Y | y | 1200 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box | 1300.9 | 645 | 97.5 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 1200 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 348.45 |  |  | 913 | 980 | 1200 | 130 | 260 | 390 | 650 | 976 | 1301 | 93.5 | 96.5 | 97 | 97.7 | 97.8 | 97.7 | 97.5 | 93.5 | 96.5 | 96.9 | 97.6 | 97.7 | 97.6 | 97.4 | 93.5 | 96.5 | 96.9 | 97.6 | 97.8 | 97.6 | 97.4 | Power Electronics1300.9FS1200CU15 [645V] | 2018-05-15 | 2018-10-15
Power Electronics | FS1190CU [440V] | Y | N | N | 1330 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1330 | 440 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 302 |  |  | 642 | 690 | 800 | 133 | 266 | 399 | 665 | 997.5 | 1330 | 95.6 | 97.1 | 97.5 | 97.7 | 97.4 | 96.8 | 97.3 | 95.5 | 97 | 97.5 | 97.6 | 97.3 | 96.7 | 97.3 | 95.3 | 96.9 | 97.3 | 97.4 | 97.1 | 96.6 | 97.1 | Power Electronics1330FS1190CU [440V]
Power Electronics | FS1331CU [440V] | Y | N | N | 1330 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1330 | 440 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted Efficiency includes MV TP1 Transformer efficiency. | 302 |  |  | 642 | 690 | 800 | 133 | 266 | 399 | 665 | 997.5 | 1330 | 95.6 | 97.1 | 97.5 | 97.7 | 97.4 | 96.8 | 97.3 | 95.5 | 97 | 97.5 | 97.6 | 97.3 | 96.7 | 97.3 | 95.3 | 96.9 | 97.3 | 97.4 | 97.1 | 96.6 | 97.1 | Power Electronics1330FS1331CU [440V] |  | 2018-02-15
Power Electronics | FS1250CU | Y | N | N | 1250 kW Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1362 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 548.9 |  |  | 552 | 615 | 800 | 136.2 | 272.3 | 408.5 | 680.8 | 1021 | 1362 | 96 | 97.5 | 97.9 | 98.1 | 97.9 | 97.4 | 97.8 | 95.6 | 97.2 | 97.6 | 97.8 | 97.5 | 97.1 | 97.5 | 95.2 | 96.8 | 97.2 | 97.3 | 97.1 | 96.7 | 97 | Power Electronics1362FS1250CU
Power Electronics | FS1275CU15 [690V] | Y | Y | y | 1275 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box | 1389.08 | 690 | 97 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 1275 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 353.05 |  |  | 976 | 1030 | 1200 | 139 | 278 | 417 | 695 | 1042 | 1389 | 91.8 | 95.5 | 96.2 | 97.7 | 97.9 | 97.8 | 97.3 | 91.7 | 95.5 | 96.3 | 97.6 | 97.8 | 97.6 | 97.2 | 91.9 | 95.6 | 96.3 | 97.6 | 97.8 | 97.6 | 97.2 | Power Electronics1389.08FS1275CU15 [690V] | 2018-05-15 | 2018-10-15
Power Electronics | FS1260CU [400V] | Y | N | N | 1400 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1400 | 400 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 308 |  |  | 584 | 650 | 800 | 140 | 580 | 420 | 700 | 1050 | 1400 | 95.5 | 97.1 | 97.6 | 97.6 | 97.3 | 96.8 | 97.3 | 95.4 | 97 | 97.4 | 97.5 | 97.2 | 96.6 | 97.2 | 95 | 96.7 | 97.2 | 97.2 | 96.9 | 96.4 | 96.9 | Power Electronics1400FS1260CU [400V]
Power Electronics | FS1401CU [400V] | Y | N | N | 1400 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1400 | 400 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 307.65 |  |  | 584 | 650 | 800 | 140 | 280 | 420 | 700 | 1050 | 1400 | 95.5326 | 97.1484 | 97.5516 | 97.6456 | 97.297 | 96.7531 | 97.2956 | 95.3842 | 97.0123 | 97.4152 | 97.5174 | 97.1653 | 96.6103 | 97.1626 | 95.0314 | 96.721 | 97.1543 | 97.2453 | 96.9218 | 96.4089 | 96.9063 | Power Electronics1400FS1401CU [400V]
Power Electronics | FS1430CU [330V] | Y | N | N | 1430.0 kW, 330 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1430 | 330 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 604 |  |  | 500 | 575 | 800 | 143 | 286 | 429 | 715 | 1073 | 1430 | 95.4 | 96.9 | 97.4 | 97.5 | 97.3 | 96.7 | 97.2 | 95.2 | 96.7 | 97.2 | 97.3 | 97.1 | 96.5 | 97 | 94.6 | 96.2 | 96.6 | 96.6 | 96.5 | 96 | 96.4 | Power Electronics1430FS1430CU [330V]
Power Electronics | FS1330CU [420V] | Y | N | N | 1480 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1480 | 420 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 318 |  |  | 616 | 670 | 800 | 148 | 296 | 444 | 740 | 1110 | 1480 | 95.5 | 97.2 | 97.6 | 97.7 | 97.4 | 96.8 | 97.3 | 95.4 | 97.1 | 97.5 | 97.6 | 97.3 | 96.7 | 97.2 | 95.1 | 96.8 | 97.2 | 97.3 | 97 | 96.5 | 97 | Power Electronics1480FS1330CU [420V]
Power Electronics | FS1480CU [420V] | Y | N | N | 1480 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1480 | 420 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted Efficiency includes MV TP1 Transformer efficiency. | 318 |  |  | 616 | 670 | 800 | 148 | 296 | 444 | 740 | 1110 | 1480 | 95.5 | 97.2 | 97.6 | 97.7 | 97.4 | 96.8 | 97.3 | 95.4 | 97.1 | 97.5 | 97.6 | 97.3 | 96.7 | 97.2 | 95.1 | 96.8 | 97.2 | 97.3 | 97 | 96.5 | 97 | Power Electronics1480FS1480CU [420V] |  | 2018-02-15
Power Electronics | FS1400CU15 [565V] | Y | Y | y | 1400 kW, 565 Vac Grid Support Utility Interactive Inverter with combiner box | 1517.09 | 565 | 97.5 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 1400 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 359.56 |  |  | 800 | 900 | 1200 | 152 | 303 | 455 | 759 | 1138 | 1517 | 94.3 | 96.5 | 97.3 | 97.7 | 97.8 | 97.6 | 97.5 | 94.3 | 96.4 | 97.2 | 97.7 | 97.7 | 97.5 | 97.4 | 94.4 | 96.5 | 97.2 | 97.6 | 97.7 | 97.5 | 97.5 | Power Electronics1517.09FS1400CU15 [565V] | 2018-05-15 | 2018-10-15
Power Electronics | FS1530CU [390V] | Y | N | N | 1530.0 kW, 390 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1530 | 390 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 345 |  |  | 585 | 640 | 800 | 153 | 306 | 459 | 765 | 1148 | 1530 | 95.6 | 97.2 | 97.6 | 97.7 | 97.4 | 96.9 | 97.4 | 95.4 | 97 | 97.4 | 97.5 | 97.3 | 96.8 | 97.2 | 95 | 96.7 | 97 | 97.1 | 96.9 | 96.5 | 96.8 | Power Electronics1530FS1530CU [390V]
Power Electronics | FS1390CU [440V] | Y | N | N | 1550 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1550 | 440 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 328 |  |  | 642 | 690 | 800 | 155 | 310 | 465 | 775 | 1162.5 | 1550 | 95.7 | 97.2 | 97.5 | 97.6 | 97.4 | 96.8 | 97.2 | 95.5 | 97.1 | 97.5 | 97.6 | 97.3 | 96.8 | 97.2 | 95.2 | 96.9 | 97.3 | 97.4 | 97.1 | 96.6 | 97.1 | Power Electronics1550FS1390CU [440V]
Power Electronics | FS1550CU [440V] | Y | N | N | 1550 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1550 | 440 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 327.743 |  |  | 642 | 690 | 800 | 155 | 310 | 465 | 775 | 1162.5 | 1550 | 95.6552 | 97.1814 | 97.5474 | 97.644 | 97.3543 | 96.8248 | 97.3352 | 95.4619 | 97.0913 | 97.4707 | 97.5601 | 97.2682 | 96.7572 | 97.2472 | 95.1767 | 96.8769 | 97.2822 | 97.3862 | 97.0885 | 96.5985 | 97.0627 | Power Electronics1550FS1550CU [440V]
Power Electronics | FS1500CU15O3 [600V] | Y | Y | Y | 1500 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant | 1594.72 | 600 | 98 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 1500 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 379.71 |  |  | 849 | 940 | 1200 | 159 | 319 | 478 | 797 | 1196 | 1595 | 96.9 | 97.6 | 97.9 | 98.1 | 98 | 97.9 | 97.9 | 96.6 | 97.5 | 97.8 | 98 | 98 | 97.8 | 97.9 | 96.7 | 97.5 | 97.8 | 98 | 98 | 97.8 | 97.9 | Power Electronics1594.72FS1500CU15O3 [600V] | 2018-05-15 | 2018-10-15
Power Electronics | FS1440CU [400V] | Y | N | N | 1600 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1600 | 400 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 340 |  |  | 584 | 650 | 800 | 160 | 320 | 480 | 800 | 1200 | 1600 | 95.6 | 97.2 | 97.6 | 97.6 | 97.3 | 96.7 | 97.3 | 95.5 | 97.1 | 97.4 | 97.5 | 97.2 | 96.6 | 97.2 | 95.2 | 96.8 | 97.2 | 97.2 | 96.9 | 96.4 | 96.9 | Power Electronics1600FS1440CU [400V]
Power Electronics | FS1600CU [400V] | Y | N | N | 1600 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1600 | 400 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 339.859 |  |  | 584 | 650 | 800 | 160 | 320 | 480 | 800 | 1200 | 1600 | 95.6333 | 97.1795 | 97.5646 | 97.6168 | 97.274 | 96.6975 | 97.2817 | 95.4879 | 97.0566 | 97.4397 | 97.4707 | 97.1501 | 96.5652 | 97.1518 | 95.1515 | 96.7995 | 97.1599 | 97.1889 | 96.9098 | 96.3818 | 96.8962 | Power Electronics1600FS1600CU [400V]
Power Electronics | FS1475CU15 [600V] | Y | Y | Y | 1475 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box | 1610.37 | 600 | 97.5 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 1475 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 368.71 |  |  | 849 | 940 | 1200 | 161 | 322 | 483 | 805 | 1208 | 1610 | 94.5 | 96.7 | 97.5 | 97.8 | 97.9 | 97.6 | 97.6 | 94.5 | 96.6 | 97.4 | 97.8 | 97.8 | 97.6 | 97.5 | 94.6 | 96.6 | 97.4 | 97.7 | 97.8 | 97.5 | 97.5 | Power Electronics1610.37FS1475CU15 [600V] | 2018-05-15 | 2018-10-15
Power Electronics | FS1590CU [440V] | Y | N | N | 1617 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1617.5 | 440 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 351 |  |  | 642 | 690 | 800 | 161.75 | 323.49 | 485.24 | 808.74 | 1213.1 | 1617.47 | 95.7 | 97.2 | 97.5 | 97.6 | 97.3 | 96.8 | 97.3 | 95.7 | 97.1 | 97.5 | 97.6 | 97.3 | 96.7 | 97.2 | 95.3 | 96.9 | 97.3 | 97.3 | 97.1 | 96.6 | 97.1 | Power Electronics1617.5FS1590CU [440V]
Power Electronics | FS1520CU [420V] | Y | N | N | 1690 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1690 | 420 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 343 |  |  | 616 | 670 | 800 | 169 | 338 | 507 | 845 | 1267.5 | 1690 | 95.7 | 97.2 | 97.6 | 97.6 | 97.3 | 96.7 | 97.3 | 95.6 | 97.1 | 97.5 | 97.5 | 97.3 | 96.7 | 97.2 | 95.3 | 96.9 | 97.2 | 97.3 | 97 | 96.5 | 97 | Power Electronics1690FS1520CU [420V]
Power Electronics | FS1690CU [420V] | Y | N | N | 1690 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1690 | 420 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 342.523 |  |  | 616 | 670 | 800 | 169 | 338 | 507 | 845 | 1267.5 | 1690 | 95.6594 | 97.2312 | 97.5788 | 97.6328 | 97.345 | 96.7419 | 97.3302 | 95.5735 | 97.1191 | 97.4823 | 97.5387 | 97.2611 | 96.669 | 97.2417 | 95.2881 | 96.8732 | 97.2431 | 97.3128 | 97.0207 | 96.484 | 97.0052 | Power Electronics1690FS1690CU [420V]
Power Electronics | FS1700CU [390V] | Y | N | N | 1700.0 kW, 390 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1700 | 390 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 346 |  |  | 585 | 640 | 800 | 170 | 340 | 510 | 850 | 1275 | 1700 | 95.7 | 97.2 | 97.5 | 97.6 | 97.4 | 96.9 | 97.4 | 95.4 | 97 | 97.4 | 97.5 | 97.3 | 96.8 | 97.2 | 94.9 | 96.5 | 97 | 97 | 96.9 | 96.5 | 96.8 | Power Electronics1700FS1700CU [390V]
Power Electronics | FS1600CU15 [645V] | Y | Y | Y | 1600 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box | 1734.81 | 645 | 97.5 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 1600 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 373.96 |  |  | 913 | 980 | 1200 | 173 | 347 | 520 | 867 | 1301 | 1735 | 94.7 | 96.8 | 97.5 | 98 | 98 | 97.8 | 97.7 | 94.7 | 96.8 | 97.5 | 97.9 | 97.9 | 97.7 | 97.6 | 94.7 | 96.8 | 97.5 | 97.8 | 97.9 | 97.7 | 97.6 | Power Electronics1734.81FS1600CU15 [645V] | 2018-05-15 | 2018-10-15
Power Electronics | FS1770CU [440V] | Y | N | N | 1770 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1770 | 440 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 351.244 |  |  | 642 | 690 | 800 | 177 | 354 | 531 | 885 | 1327.5 | 1770 | 95.7353 | 97.1908 | 97.5406 | 97.636 | 97.3334 | 96.7563 | 97.3 | 95.664 | 97.1112 | 97.462 | 97.5505 | 97.2678 | 96.6876 | 97.2495 | 95.3184 | 96.9036 | 97.2617 | 97.3465 | 97.1073 | 96.558 | 97.0668 | Power Electronics1770FS1770CU [440V]
Power Electronics | FS1620CU [400V] | Y | N | N | 1800 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1800 | 400 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 356 |  |  | 584 | 650 | 800 | 180 | 360 | 540 | 900 | 1350 | 1800 | 95.7 | 97.2 | 97.6 | 97.6 | 97.3 | 93.7 | 97.3 | 95.6 | 97.1 | 97.4 | 97.5 | 97.3 | 96.6 | 97.2 | 95.3 | 96.8 | 97.2 | 97.2 | 96.9 | 96.4 | 96.9 | Power Electronics1800FS1620CU [400V]
Power Electronics | FS1801CU [400V] | Y | N | N | 1801 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1800 | 400 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 355.84 |  |  | 584 | 650 | 800 | 180 | 360 | 540 | 900 | 1350 | 1800 | 95.7155 | 97.1881 | 97.5572 | 97.6193 | 97.2912 | 96.709 | 97.2947 | 95.5786 | 97.0669 | 97.4345 | 97.4902 | 97.1718 | 96.5729 | 97.1713 | 95.2764 | 96.8074 | 97.1822 | 97.2104 | 96.9306 | 96.3813 | 96.9198 | Power Electronics1800FS1801CU [400V]
Power Electronics | FS1700CU15 [690V] | Y | Y | Y | 1700 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box | 1850.63 | 690 | 98 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 1700 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 368.51 |  |  | 976 | 1030 | 1200 | 185 | 370 | 555 | 925 | 1388 | 1851 | 95 | 97 | 97.7 | 98.1 | 98.2 | 97.9 | 97.9 | 94.9 | 97 | 97.6 | 98.1 | 98 | 97.9 | 97.8 | 94.9 | 96.9 | 97.6 | 98 | 98.1 | 97.8 | 97.8 | Power Electronics1850.63FS1700CU15 [690V] | 2018-05-15 | 2018-10-15
Power Electronics | FS1750CU15 [565V] | Y | Y | Y | 1750 kW, 565 Vac Grid Support Utility Interactive Inverter with combiner box | 1896.53 | 565 | 97.5 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 1750 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 378.47 |  |  | 800 | 900 | 1200 | 190 | 379 | 569 | 948 | 1422 | 1897 | 94.8 | 96.6 | 97.4 | 98 | 97.9 | 97.7 | 97.6 | 94.8 | 96.5 | 97.3 | 97.8 | 97.8 | 97.6 | 97.5 | 94.7 | 96.4 | 97.3 | 97.8 | 97.8 | 97.5 | 97.5 | Power Electronics1896.53FS1750CU15 [565V] | 2018-05-15 | 2018-10-15
Power Electronics | FS1710CU [420V] | Y | N | N | 1900 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1900 | 420 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 363 |  |  | 616 | 670 | 800 | 190 | 380 | 570 | 950 | 1425 | 1900 | 95.7 | 97.2 | 97.6 | 97.6 | 97.3 | 96.7 | 97.3 | 95.6 | 97.1 | 97.5 | 97.5 | 97.2 | 96.7 | 97.2 | 95.4 | 96.8 | 97.2 | 97.3 | 97 | 96.5 | 97 | Power Electronics1900FS1710CU [420V]
Power Electronics | FS1901CU [420V] | Y | N | N | 1901 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1900 | 420 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 362.802 |  |  | 616 | 670 | 800 | 190 | 380 | 570 | 950 | 1425 | 1900 | 95.7244 | 97.1882 | 97.5627 | 97.6299 | 97.3026 | 96.7121 | 97.3042 | 95.6152 | 97.089 | 97.4872 | 97.5311 | 97.2134 | 96.6755 | 97.2159 | 95.3576 | 96.8401 | 97.2392 | 97.2703 | 97.0404 | 96.4615 | 97.0063 | Power Electronics1900FS1901CU [420V]
Power Electronics | FS1850CU15O3 [600V] | Y | Y | Y | 1850 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant | 1974.29 | 600 | 98 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 1850 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 397.3 |  |  | 849 | 940 | 1200 | 197 | 395 | 592 | 987 | 1481 | 1974 | 96.9 | 97.7 | 97.9 | 98.1 | 98.1 | 97.9 | 98 | 96.7 | 97.5 | 97.8 | 98 | 98 | 97.8 | 97.9 | 96.8 | 97.6 | 97.9 | 98 | 98 | 97.8 | 97.9 | Power Electronics1974.29FS1850CU15O3 [600V] | 2018-05-15 | 2018-10-15
Power Electronics | FS1790CU [440V] | Y | N | N | 1990 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1990 | 440 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 371 |  |  | 642 | 690 | 800 | 199 | 398 | 597 | 995 | 1492.5 | 1990 | 95.7 | 97.2 | 97.6 | 97.6 | 97.3 | 96.6 | 97.3 | 95.6 | 97.1 | 97.5 | 97.5 | 97.2 | 96.5 | 97.2 | 95.4 | 96.9 | 97.3 | 97.3 | 97 | 96.4 | 97 | Power Electronics1990FS1790CU [440V]
Power Electronics | FS1991CU [440V] | Y | N | N | 1990 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 1990 | 440 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 370.81 |  |  | 642 | 690 | 800 | 199 | 398 | 597 | 995 | 1492.5 | 1990 | 95.713 | 97.176 | 97.5652 | 97.6151 | 97.3002 | 96.5736 | 97.2921 | 95.6172 | 97.1016 | 97.4866 | 97.5364 | 97.2267 | 96.5224 | 97.217 | 95.4006 | 96.9315 | 97.3019 | 97.3425 | 97.0467 | 96.3857 | 97.0348 | Power Electronics1990FS1991CU [440V]
Power Electronics | FS1800CU [400V] | Y | N | N | 2000 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 2000 | 400 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 381 |  |  | 584 | 650 | 800 | 200 | 400 | 600 | 1000 | 1500 | 2000 | 95.8 | 97.2 | 97.6 | 97.6 | 97.2 | 96.6 | 97.3 | 95.6 | 97.1 | 97.4 | 97.5 | 97.1 | 96.4 | 97.1 | 95.4 | 96.8 | 97.2 | 97.2 | 96.9 | 96.2 | 96.9 | Power Electronics2000FS1800CU [400V]
Power Electronics | FS2000CU [400V] | Y | N | N | 2000 kW, 400 Vac Utility Interactive Inverter with Medium Voltage Transformer | 2000 | 400 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted Efficiency includes MV TP1 Transformer efficiency. | 381 |  |  | 548 | 650 | 800 | 200 | 400 | 600 | 1000 | 1500 | 2000 | 95.8 | 97.2 | 97.6 | 97.6 | 97.2 | 96.6 | 97.3 | 95.6 | 97.1 | 97.4 | 97.5 | 97.1 | 96.4 | 97.1 | 95.4 | 96.8 | 97.2 | 97.2 | 96.9 | 96.2 | 96.9 | Power Electronics2000FS2000CU [400V] |  | 2018-02-15
Power Electronics | FS1850CU15 [600V] | Y | Y | Y | 1850 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box | 2020.96 | 600 | 97.5 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 1850 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 388.77 |  |  | 849 | 940 | 1200 | 202 | 404 | 606 | 1010 | 1516 | 2021 | 95.1 | 96.7 | 97.5 | 98 | 98 | 97.8 | 97.8 | 95 | 96.6 | 97.5 | 97.9 | 97.9 | 97.7 | 97.7 | 95 | 96.6 | 97.4 | 97.9 | 97.9 | 97.6 | 97.7 | Power Electronics2020.96FS1850CU15 [600V] | 2018-05-15 | 2018-10-15
Power Electronics | FS1900CU [420V] | Y | N | N | 2110 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 2110 | 420 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 388 |  |  | 616 | 670 | 800 | 211 | 422 | 633 | 1055 | 1582.5 | 2110 | 95.7 | 97.2 | 97.6 | 97.6 | 97.2 | 96.6 | 97.3 | 95.7 | 97.1 | 97.5 | 97.5 | 97.1 | 96.6 | 97.2 | 95.4 | 96.9 | 97.3 | 97.3 | 96.9 | 96.4 | 97 | Power Electronics2110FS1900CU [420V]
Power Electronics | FS2110CU [420V] | Y | N | N | 2110 kW, 420 Vac Utility Interactive Inverter with Medium Voltage Transformer | 2110 | 420 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted Efficiency includes MV TP1 Transformer efficiency. | 388 |  |  | 616 | 670 | 800 | 211 | 422 | 633 | 1055 | 1582.5 | 2110 | 95.7 | 97.2 | 97.6 | 97.6 | 97.2 | 96.6 | 97.3 | 95.7 | 97.3 | 97.5 | 97.5 | 97.1 | 96.6 | 97.2 | 95.4 | 96.9 | 97.3 | 97.3 | 96.9 | 96.4 | 97 | Power Electronics2110FS2110CU [420V] |  | 2018-02-15
Power Electronics | FS2000CU15 [645V] | Y | Y | Y | 2000 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box | 2162.42 | 645 | 98 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 2000 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 388.97 |  |  | 913 | 980 | 1200 | 216 | 432 | 649 | 1081 | 1622 | 2162 | 95.2 | 96.9 | 97.6 | 98.1 | 98.1 | 97.9 | 97.9 | 95.2 | 96.8 | 97.5 | 98 | 98 | 97.8 | 97.8 | 95.2 | 96.8 | 97.5 | 98 | 98 | 97.8 | 97.7 | Power Electronics2162.42FS2000CU15 [645V] | 2018-05-15 | 2018-10-15
Power Electronics | FS1980CU [440V] | Y | N | N | 2200 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 2200 | 440 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 396 |  |  | 642 | 690 | 800 | 220 | 440 | 660 | 1100 | 1650 | 2200 | 95.7 | 97.2 | 97.6 | 97.6 | 97.3 | 96.7 | 97.3 | 95.7 | 97.1 | 97.5 | 97.5 | 97.2 | 96.7 | 97.2 | 95.5 | 97 | 97.3 | 97.4 | 97.1 | 96.5 | 97.1 | Power Electronics2200FS1980CU [440V]
Power Electronics | FS2200CU [440V] | Y | N | N | 2200 kW, 440 Vac Utility Interactive Inverter with Medium Voltage Transformer | 2200 | 440 | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted Efficiency includes MV TP1 Transformer efficiency. | 396 |  |  | 642 | 690 | 800 | 220 | 440 | 660 | 1100 | 1650 | 2200 | 95.8 | 97.2 | 97.6 | 97.6 | 97.3 | 96.7 | 97.3 | 95.7 | 97.1 | 97.5 | 97.5 | 97.2 | 96.7 | 97.2 | 95.5 | 97 | 97.3 | 97.4 | 97.1 | 96.5 | 97.1 | Power Electronics2200FS2200CU [440V] |  | 2018-02-15
Power Electronics | FS2100CU15 [565V] | Y | Y | Y | 2100 kW, 565 Vac Grid Support Utility Interactive Inverter with combiner box | 2275.89 | 565 | 97.5 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 2100 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 398.85 |  |  | 800 | 900 | 1200 | 228 | 455 | 683 | 1138 | 1707 | 2276 | 95.4 | 97.2 | 97.6 | 98 | 98 | 97.7 | 97.8 | 95.2 | 97.1 | 97.6 | 97.9 | 97.8 | 97.6 | 97.7 | 95.3 | 97 | 97.5 | 97.9 | 97.8 | 97.6 | 97.7 | Power Electronics2275.89FS2100CU15 [565V] | 2018-05-15 | 2018-10-15
Power Electronics | FS2125CU15 [690V] | Y | Y | Y | 2125 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box | 2306.41 | 690 | 98 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 2125 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 390.63 |  |  | 976 | 1030 | 1200 | 231 | 461 | 692 | 1153 | 1730 | 2306 | 95.6 | 97.1 | 97.8 | 98.2 | 98.2 | 98 | 98 | 95.6 | 97.1 | 97.7 | 98.1 | 98.1 | 97.9 | 97.9 | 95.5 | 97 | 97.6 | 98.1 | 98.1 | 97.8 | 97.9 | Power Electronics2306.41FS2125CU15 [690V] | 2018-05-15 | 2018-10-15
Power Electronics | FS2225CU15 [600V] | Y | Y | Y | 2225 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box | 2417.08 | 600 | 97.5 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 2225 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 403.32 |  |  | 849 | 940 | 1200 | 242 | 483 | 725 | 1209 | 1813 | 2417 | 95.5 | 97.2 | 97.7 | 98.1 | 98.1 | 97.8 | 97.9 | 95.5 | 97.2 | 97.7 | 98 | 98 | 97.7 | 97.8 | 95.4 | 97.1 | 97.6 | 98 | 98 | 97.7 | 97.8 | Power Electronics2417.08FS2225CU15 [600V] | 2018-05-15 | 2018-10-15
Power Electronics | FS2250CU15O3 [600V] | Y | Y | Y | 2250 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant | 2420.37 | 600 | 98 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 2250 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 416.47 |  |  | 849 | 940 | 1200 | 242 | 484 | 726 | 1210 | 1815 | 2420 | 97.2 | 97.8 | 98 | 98.2 | 98.1 | 97.9 | 98 | 96.9 | 97.8 | 98 | 98 | 98 | 97.7 | 97.9 | 96.9 | 97.7 | 97.9 | 98.1 | 98 | 97.8 | 97.9 | Power Electronics2420.37FS2250CU15O3 [600V] | 2018-05-15 | 2018-10-15
Power Electronics | FS2150CU15 [645V] | Y | Y | Y | 2150 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box | 2558.48 | 645 | 98 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 2150 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 409.99 |  |  | 913 | 980 | 1200 | 256 | 512 | 768 | 1279 | 1919 | 2558 | 95.7 | 97.4 | 97.8 | 98.1 | 98.1 | 97.9 | 97.9 | 95.6 | 97.3 | 97.8 | 98.1 | 98.1 | 97.8 | 97.9 | 95.6 | 97.3 | 97.7 | 98.1 | 98.1 | 97.8 | 97.9 | Power Electronics2558.48FS2150CU15 [645V] | 2018-05-15 | 2018-10-15
Power Electronics | FS2400CU15 [645V] | Y | Y | Y | 2400 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box | 2583.76 | 645 | 98 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 2400 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 407.44 |  |  | 913 | 980 | 1200 | 258 | 517 | 775 | 1292 | 1938 | 2584 | 95.8 | 97.4 | 97.9 | 98.1 | 98.1 | 97.9 | 98 | 95.8 | 97.4 | 97.7 | 98.1 | 98.1 | 97.8 | 97.9 | 95.7 | 97.3 | 97.7 | 98.1 | 98 | 97.8 | 97.9 | Power Electronics2583.76FS2400CU15 [645V] | 2018-05-15 | 2018-10-15
Power Electronics | FS2450CU15 [565V] | Y | Y | Y | 2450 kW, 565 Vac Grid Support Utility Interactive Inverter with combiner box | 2664.07 | 565 | 97.5 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 2450 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 417.35 |  |  | 800 | 900 | 1200 | 266 | 533 | 799 | 1332 | 1998 | 2664 | 95.7 | 97.3 | 97.6 | 98 | 98 | 97.7 | 97.8 | 95.6 | 97.2 | 97.6 | 97.9 | 97.9 | 97.6 | 97.7 | 95.6 | 97.2 | 97.5 | 97.9 | 97.9 | 97.6 | 97.7 | Power Electronics2664.07FS2450CU15 [565V] | 2018-05-15 | 2018-10-15
Power Electronics | FS2550CU15 [690V] | Y | Y | Y | 2250 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box | 2759.39 | 690 | 98 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 2550 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 408.29 |  |  | 976 | 1030 | 1200 | 276 | 552 | 828 | 1380 | 2070 | 2759 | 96 | 97.5 | 97.9 | 98.2 | 98.2 | 97.9 | 98 | 95.9 | 97.4 | 97.8 | 98.2 | 98.1 | 97.8 | 97.9 | 95.9 | 97.4 | 97.8 | 98.1 | 98.1 | 97.9 | 98 | Power Electronics2759.39FS2550CU15 [690V] | 2018-05-15 | 2018-10-15
Power Electronics | FS2300CU15 [690V] | Y | Y | Y | 2300 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box | 2759.49 | 690 | 98 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 2300 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 408.67 |  |  | 976 | 1030 | 1200 | 276 | 552 | 828 | 1380 | 2070 | 2759 | 95.9 | 97.5 | 97.9 | 98.2 | 98.2 | 98 | 98 | 95.8 | 97.4 | 97.8 | 98.1 | 98.2 | 97.9 | 98 | 95.8 | 97.4 | 97.8 | 98.2 | 98.1 | 97.9 | 98 | Power Electronics2759.49FS2300CU15 [690V] | 2018-05-15 | 2018-10-15
Power Electronics | FS2600CU15O3 [600V] | Y | Y | Y | 2600 kW, 600 Vac Grid Support Utility Interactive Inverter with combiner box and a back feed power supply of 10kW to feed solar trackers on the PV power plant | 2770.2 | 600 | 98 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 2600 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 433.54 |  |  | 849 | 940 | 1200 | 277 | 554 | 831 | 1385 | 2078 | 2770 | 97.2 | 97.9 | 98.1 | 98.2 | 98.1 | 97.9 | 98 | 97.1 | 97.8 | 98 | 98 | 98 | 97.8 | 98 | 97.1 | 97.8 | 98 | 98.1 | 98 | 97.8 | 98 | Power Electronics2770.2FS2600CU15O3 [600V] | 2018-05-15 | 2018-10-15
Power Electronics | FS2600CU15 [600V] | Y | Y | Y | 2600 kW, 600 Vac Grid SupportUtility Interactive Inverter with combiner box | 2821.84 | 600 | 98 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 2600 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 423.67 |  |  | 849 | 940 | 1200 | 282 | 564 | 847 | 1411 | 2116 | 2822 | 95.7 | 97.4 | 97.9 | 98.1 | 98 | 97.8 | 97.9 | 95.7 | 97.3 | 97.8 | 98.1 | 98 | 97.7 | 97.8 | 95.7 | 97.2 | 97.7 | 98 | 98 | 97.7 | 97.8 | Power Electronics2821.84FS2600CU15 [600V] | 2018-05-15 | 2018-10-15
Power Electronics | FS2800CU15 [645V] | Y | Y | Y | 2800 kW, 645 Vac Grid Support Utility Interactive Inverter with combiner box | 3024.91 | 645 | 98 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 2800 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 427.54 |  |  | 913 | 940 | 1200 | 302 | 605 | 907 | 1512 | 2269 | 3025 | 96 | 97.4 | 97.9 | 98.1 | 98.1 | 97.9 | 98 | 95.9 | 97.4 | 97.8 | 98.1 | 98.1 | 97.8 | 97.9 | 95.9 | 97.3 | 97.7 | 98.1 | 98 | 97.8 | 97.9 | Power Electronics3024.91FS2800CU15 [645V] | 2018-05-15 | 2018-10-15
Power Electronics | FS3000CU15 [690V] | Y | Y | Y | 3000 kW, 690 Vac Grid Support Utility Interactive Inverter with combiner box | 3201.17 | 690 | 98 | [02/15/2018] | [HEP2G_2.0.0] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 3000 kVA Liquid-Immeresed Distribution Transformers Table in DOE2016. | 426.4 |  |  | 976 | 1030 | 1200 | 320 | 640 | 960 | 1601 | 2401 | 3201 | 96.1 | 97.5 | 97.9 | 98.2 | 98.3 | 98.1 | 98.1 | 96 | 97.5 | 97.9 | 98.1 | 98.2 | 98 | 98 | 95.9 | 97.5 | 97.9 | 98.2 | 98.2 | 97.9 | 98 | Power Electronics3201.17FS3000CU15 [690V] | 2018-05-15 | 2018-10-15
Powercom | SLK-1500 [208V] | Y | N | N | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.46 | 90.49 | 92.52 | 94.25 | 94.92 | 95.02 | 93.86 | 85.04 | 91.04 | 93.19 | 94.79 | 95.41 | 95.53 | 94.38 | 85.31 | 91.19 | 93.54 | 95.02 | 95.55 | 95.76 | 94.58 | Powercom1.55SLK-1500 [208V]
Powercom | SLK-1500 [240V] | Y | N | N | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.62 | 90.46 | 92.57 | 94.42 | 95.07 | 95.25 | 93.99 | 84.89 | 90.97 | 93.04 | 94.81 | 95.51 | 95.73 | 94.42 | 85.22 | 91.38 | 93.44 | 95.12 | 95.65 | 95.93 | 94.66 | Powercom1.55SLK-1500 [240V]
Powercom | SLK-2000 [208V] | Y | N | N | 2 kW, 208 Vac Utility Interactive Inverter | 2.06 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.29 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 88.28 | 93.12 | 94.41 | 95.27 | 95.43 | 95.37 | 94.87 | 89.63 | 93.68 | 94.91 | 95.73 | 95.84 | 95.8 | 95.34 | 89.74 | 94.01 | 95.11 | 96.13 | 96.38 | 96.07 | 95.77 | Powercom2.06SLK-2000 [208V]
Powercom | SLK-2000 [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter | 2.06 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 86.91 | 92.14 | 93.78 | 94.94 | 95.3 | 95.37 | 94.55 | 87.84 | 92.87 | 94.26 | 95.56 | 95.79 | 95.73 | 95.09 | 88.1 | 93.05 | 94.37 | 95.71 | 96 | 95.94 | 95.28 | Powercom2.06SLK-2000 [240V]
Powercom | SLK-3000 [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.57 | 94.41 | 95.16 | 95.47 | 95.31 | 94.62 | 95.1 | 92.05 | 94.92 | 95.58 | 95.89 | 95.76 | 95.37 | 95.56 | 92.22 | 95.17 | 95.79 | 96.25 | 95.93 | 95.8 | 95.78 | Powercom3SLK-3000 [208V]
Powercom | SLK-3000 [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.301 | 0.602 | 0.903 | 1.505 | 2.258 | 3.01 | 90 | 93.9 | 94.85 | 95.4 | 95.31 | 94.83 | 94.97 | 90.64 | 94.34 | 95.34 | 95.79 | 95.87 | 95.6 | 95.49 | 91 | 94.59 | 95.44 | 95.97 | 96.01 | 95.77 | 95.65 | Powercom3.01SLK-3000 [240V]
Powercom | SLK-4000 [208V] | Y | N | N | 4 kW, 208 Vac Utility Interactive Inverter | 3.98 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.398 | 0.796 | 1.194 | 1.99 | 2.985 | 3.98 | 90.53 | 94.32 | 95.17 | 95.44 | 95.41 | 95.16 | 95.13 | 91.58 | 94.87 | 95.63 | 96.05 | 96 | 95.45 | 95.7 | 91.82 | 95.03 | 95.8 | 96.45 | 96.31 | 95.76 | 96.01 | Powercom3.98SLK-4000 [208V]
Powercom | SLK-4000 [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.399 | 0.798 | 1.197 | 1.995 | 2.993 | 3.99 | 90.55 | 94.3 | 95.24 | 95.69 | 95.74 | 95.56 | 95.38 | 91.53 | 94.95 | 95.81 | 96.33 | 96.33 | 96.05 | 95.99 | 91.95 | 95.23 | 95.96 | 96.4 | 96.48 | 96.25 | 96.15 | Powercom3.99SLK-4000 [240V]
Powercom | SLK-4000 [277V] | Y | N | N | 4 kW, 277 Vac Utility Interactive Inverter | 4.02 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.29 |  |  | 100 | 332 | 360 | 0.4 | 0.8 | 1.21 | 2.01 | 3.02 | 4.02 | 89.9 | 93.4 | 94.5 | 95.2 | 95.3 | 95.2 | 94.9 | 90.8 | 94.1 | 95 | 95.7 | 95.8 | 95.8 | 95.4 | 91 | 94.3 | 95.3 | 95.9 | 96 | 96 | 95.6 | Powercom4.02SLK-4000 [277V]
Power-One | MICRO-0.25-I-OUTD-US-208 [208V] | Y | N | N | 250 W Utility Interactive Inverter | 0.25 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | Multiple Listing of ABB | 0.02 |  |  | 30 | 40 | 50 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 91.2 | 94.5 | 95.4 | 96 | 96.2 | 96.2 | 95.8 | 91.5 | 94.4 | 95.5 | 96.2 | 96.3 | 96.4 | 95.9 | 91.2 | 94.3 | 95.3 | 96.2 | 96.2 | 96.4 | 95.8 | Power-One0.25MICRO-0.25-I-OUTD-US-208 [208V]
Power-One | MICRO-0.25-I-OUTD-US-240 [240V] | Y | N | N | 250 W Utility Interactive Inverter | 0.25 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | Multiple Listing of ABB | 0.05 |  |  | 30 | 40 | 50 | 0.03 | 0.05 | 0.08 | 0.13 | 0.19 | 0.25 | 90.8 | 94.2 | 95.4 | 96 | 96.1 | 96.2 | 95.7 | 91.2 | 94.2 | 95.3 | 96.3 | 96.2 | 96.5 | 95.8 | 90.5 | 94 | 95.3 | 96.3 | 96.1 | 96.5 | 95.8 | Power-One0.25MICRO-0.25-I-OUTD-US-240 [240V]
Power-One | MICRO-0.3HV-I-OUTD-US-208 [208V] | Y | N | N | 300 W Utility Interactive Inverter | 0.3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | Multiple Listing of ABB | 0.06 |  |  | 30 | 45 | 60 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.3 | 92.8 | 95.2 | 95.8 | 96.1 | 96 | 95.6 | 95.8 | 92.3 | 95 | 95.8 | 96.2 | 96.3 | 96.3 | 96 | 91.9 | 94.9 | 95.7 | 96.2 | 96.2 | 96.2 | 95.9 | Power-One0.3MICRO-0.3HV-I-OUTD-US-208 [208V]
Power-One | MICRO-0.3HV-I-OUTD-US-240 [240V] | Y | N | N | 300 W Utility Interactive Inverter | 0.3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | Multiple Listing of ABB | 0.06 |  |  | 30 | 45 | 60 | 0.03 | 0.06 | 0.09 | 0.15 | 0.225 | 0.3 | 92.4 | 95 | 95.7 | 96 | 96 | 95.7 | 95.8 | 91.8 | 94.7 | 95.8 | 96.2 | 96.4 | 96.4 | 96 | 91.7 | 94.6 | 95.6 | 96.1 | 96.2 | 96.4 | 95.8 | Power-One0.3MICRO-0.3HV-I-OUTD-US-240 [240V]
Power-One | MICRO-0.3-I-OUTD-US-208 [208V] | Y | N | N | 300 W Utility Interactive Inverter | 0.3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | Multiple Listing of ABB | 0.02 |  |  | 30 | 40 | 50 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 92 | 95 | 95.8 | 96 | 96.2 | 96 | 95.9 | 92.2 | 94.9 | 95.8 | 96.3 | 96.4 | 96.4 | 96 | 91.7 | 94.8 | 95.6 | 96.2 | 96.3 | 96.4 | 96 | Power-One0.3MICRO-0.3-I-OUTD-US-208 [208V]
Power-One | MICRO-0.3-I-OUTD-US-240 [240V] | Y | N | N | 300 W Utility Interactive Inverter | 0.3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | Multiple Listing of ABB | 0.05 |  |  | 30 | 40 | 50 | 0.03 | 0.06 | 0.09 | 0.15 | 0.23 | 0.3 | 91.7 | 94.8 | 95.8 | 96 | 96.1 | 96 | 95.8 | 92 | 94.8 | 95.7 | 96.3 | 96.4 | 96.4 | 96 | 91.6 | 94.7 | 95.6 | 96.3 | 96.4 | 96.5 | 96 | Power-One0.3MICRO-0.3-I-OUTD-US-240 [240V]
Power-One | UNO-2.0-I-OUTD-S-US [208V] | Y | N | N | 2 kW, 208 Vac Utility Interactive Inverter. Model Number may include -W | 2 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.4 | 2 | 0.4 | 100 | 330 | 416 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 90.4 | 94.2 | 95.5 | 95.9 | 95.6 | 95 | 95.4 | 88.3 | 94.1 | 95.3 | 96.1 | 96.1 | 96 | 95.6 | 85.6 | 92.5 | 94.3 | 95.6 | 95.8 | 95.8 | 95 | Power-One2UNO-2.0-I-OUTD-S-US [208V]
Power-One | UNO-2.0-I-OUTD-S-US [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter. Model Number may include -W | 2 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.4 | 2 | 0.4 | 100 | 340 | 416 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89.2 | 94.5 | 95.4 | 96 | 96 | 95.5 | 95.5 | 88.3 | 94.1 | 95.5 | 96.4 | 96.5 | 96.5 | 95.9 | 85.5 | 92.8 | 94.6 | 95.9 | 96.2 | 96.3 | 95.4 | Power-One2UNO-2.0-I-OUTD-S-US [240V]
Power-One | UNO-2.0-I-OUTD-S-US [277V] | Y | N | N | 2 kW, 277 Vac Utility Interactive Inverter. Model Number may include -W | 2 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.5 | 2 | 0.5 | 100 | 360 | 416 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.6 | 94.2 | 95.1 | 95.9 | 96 | 95.7 | 95.4 | 87.8 | 93.7 | 95.1 | 96.2 | 96.6 | 96.6 | 95.8 | 85.8 | 93 | 94.7 | 96.1 | 96.4 | 96.6 | 95.6 | Power-One2UNO-2.0-I-OUTD-S-US [277V]
Power-One | UNO-2.5-I-OUTD-S-US [208V] | Y | N | N | 2.5 kW, 208 Vac Utility Interactive Inverter. Model Number may include -W | 2.5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.4 | 2.5 | 0.4 | 100 | 330 | 416 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 91.9 | 95.2 | 95.8 | 95.8 | 95.2 | 94.2 | 95.2 | 89.6 | 94.9 | 95.8 | 96.1 | 96 | 95.7 | 95.7 | 87.5 | 93.6 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | Power-One2.5UNO-2.5-I-OUTD-S-US [208V]
Power-One | UNO-2.5-I-OUTD-S-US [240V] | Y | N | N | 2.5 kW, 240 Vac Utility Interactive Inverter. Model Number may include -W | 2.5 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.4 | 2.5 | 0.4 | 100 | 340 | 416 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 91 | 95.1 | 95.8 | 96.1 | 95.7 | 95 | 95.5 | 89.8 | 95 | 96 | 96.5 | 96.5 | 96.3 | 96.1 | 87.8 | 94 | 95.3 | 96.3 | 96.3 | 96.3 | 95.7 | Power-One2.5UNO-2.5-I-OUTD-S-US [240V]
Power-One | UNO-2.5-I-OUTD-S-US [277V] | Y | N | N | 2.5 kW, 277 Vac Utility Interactive Inverter. Model Number may include -W | 2.5 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.5 | 2.5 | 0.5 | 100 | 360 | 416 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 89.7 | 94.7 | 95.6 | 96 | 95.9 | 95.3 | 95.5 | 89 | 94.6 | 95.7 | 96.4 | 96.6 | 96.6 | 96.1 | 87.9 | 94.1 | 95.4 | 96.4 | 96.6 | 96.6 | 95.9 | Power-One2.5UNO-2.5-I-OUTD-S-US [277V]
Power-One | PVI-3000-I-OUTD-US [208V] | Y | N | N | 3 kW, 150-600 Vdc Utility Interactive Inverter | 2.7 | 208 | 90.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.4 | 2.5 | 0.4 | 100 | 330 | 480 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 86.2 | 90.4 | 91.1 | 90.9 | 90.1 | 88.9 | 90.2 | 87 | 91.9 | 92.5 | 92.1 | 91.2 | 90.1 | 91.4 | 81.7 | 89.2 | 90.6 | 90.6 | 89.9 | 88.9 | 89.7 | Power-One2.7PVI-3000-I-OUTD-US [208V]
Power-One | PVI-3000-I-OUTD-US-F [208V] | Y | N | N | 3 kW, 150-600 Vdc Utility Interactive Inverter | 2.7 | 208 | 90.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.4 | 2.7 | 0.4 | 100 | 330 | 480 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 86.2 | 90.4 | 91.2 | 91 | 90.1 | 88.9 | 90.2 | 87 | 91.9 | 92.5 | 92.3 | 91.1 | 90 | 91.4 | 81.7 | 89.2 | 90.6 | 90.8 | 89.9 | 88.8 | 89.7 | Power-One2.7PVI-3000-I-OUTD-US-F [208V]
Power-One | PVI-3.0-OUTD-S-US [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | Power-One3PVI-3.0-OUTD-S-US [208V]
Power-One | PVI-3.0-OUTD-S-US [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | Power-One3PVI-3.0-OUTD-S-US [240V]
Power-One | PVI-3.0-OUTD-S-US [277V] | Y | N | N | 3 kW, 277 Vac Utility Interactive Inverter | 3 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | Power-One3PVI-3.0-OUTD-S-US [277V]
Power-One | PVI-3.0-OUTD-S-US-A [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter with arc detector | 3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | Power-One3PVI-3.0-OUTD-S-US-A [208V]
Power-One | PVI-3.0-OUTD-S-US-A [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter with arc detector | 3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | Power-One3PVI-3.0-OUTD-S-US-A [240V]
Power-One | PVI-3.0-OUTD-S-US-A [277V] | Y | N | N | 3 kW, 277 Vac Utility Interactive Inverter with arc detector | 3 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | Power-One3PVI-3.0-OUTD-S-US-A [277V]
Power-One | PVI-3.0-OUTD-S-US-Z [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter with Zigbee | 3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | Power-One3PVI-3.0-OUTD-S-US-Z [208V]
Power-One | PVI-3.0-OUTD-S-US-Z [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter with Zigbee | 3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | Power-One3PVI-3.0-OUTD-S-US-Z [240V]
Power-One | PVI-3.0-OUTD-S-US-Z [277V] | Y | N | N | 3 kW, 277 Vac Utility Interactive Inverter with Zigbee | 3 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | Power-One3PVI-3.0-OUTD-S-US-Z [277V]
Power-One | PVI-3.0-OUTD-S-US-Z-A [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter with Zigbee and arc detector | 3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | Power-One3PVI-3.0-OUTD-S-US-Z-A [208V]
Power-One | PVI-3.0-OUTD-S-US-Z-A [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter with Zigbee and arc detector | 3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | Power-One3PVI-3.0-OUTD-S-US-Z-A [240V]
Power-One | PVI-3.0-OUTD-S-US-Z-A [277V] | Y | N | N | 3 kW, 277 Vac Utility Interactive Inverter with Zigbee and arc detector | 3 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | Power-One3PVI-3.0-OUTD-S-US-Z-A [277V]
Power-One | PVI-3.0-OUTD-US [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 3 | 0.1 | 100 | 310 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.1 | 95.5 | 96 | 95.9 | 95.7 | 95.1 | 95.6 | 93.3 | 95.9 | 96.4 | 96.4 | 96.2 | 95.8 | 96.1 | 91 | 94.9 | 95.7 | 96 | 95.8 | 95.5 | 95.6 | Power-One3PVI-3.0-OUTD-US [208V]
Power-One | PVI-3.0-OUTD-US [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter. Model Number may include -S- or -W | 3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 3 | 0.1 | 100 | 340 | 480 | 0.25 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 92.5 | 95.2 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 93.1 | 95.9 | 96.5 | 96.7 | 96.7 | 96.4 | 96.5 | 91.1 | 95.1 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | Power-One3PVI-3.0-OUTD-US [240V]
Power-One | PVI-3.0-OUTD-US [277V] | Y | N | N | 3 kW, 277 Vac Utility Interactive Inverter. Model Number may include -S- or -W | 3 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 3 | 0.2 | 100 | 390 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.4 | 94.7 | 95.5 | 96.1 | 95.9 | 95.6 | 95.7 | 92.5 | 95.8 | 96.5 | 96.9 | 96.9 | 96.8 | 96.6 | 91.1 | 95.2 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | Power-One3PVI-3.0-OUTD-US [277V]
Power-One | PVI-3000-I-OUTD-US [240V] | Y | N | N | 3 kW, 150-600 Vdc Utility Interactive Inverter | 3 | 240 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.4 | 2.516 | 0.4 | 100 | 360 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 85.6 | 89.8 | 91.3 | 91.7 | 91 | 89.7 | 90.8 | 86.9 | 91.3 | 92.6 | 92.9 | 92.1 | 91.1 | 92 | 83.3 | 89.6 | 91.4 | 92.2 | 91.7 | 90.6 | 91.3 | Power-One3PVI-3000-I-OUTD-US [240V]
Power-One | PVI-3000-I-OUTD-US-F [240V] | Y | N | N | 3 kW, 150-600 Vdc Utility Interactive Inverter | 3 | 240 | 91 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.4 | 3 | 0.4 | 100 | 380 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 85.6 | 90 | 91.1 | 91.1 | 90.7 | 89.6 | 90.5 | 87.1 | 92 | 92.7 | 92.7 | 91.9 | 90.9 | 91.9 | 83.9 | 90.3 | 91.3 | 91.7 | 91.1 | 90.2 | 90.9 | Power-One3PVI-3000-I-OUTD-US-F [240V]
Power-One | PVI-3.8-1-OUTD-x-US-y [208V] | Y | N | N | 3.8 kW, 208 Vac Inverter, where x = (blank) or -S and y = -PG or -NG | 3.3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 3.3 | 0.1 | 100 | 310 | 416 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 93.58 | 95.7 | 96.16 | 96.41 | 96.34 | 95.99 | 96.17 | 92.51 | 95.59 | 96.33 | 96.63 | 96.66 | 96.54 | 96.39 | 89.49 | 94.02 | 95.28 | 96.08 | 96.29 | 96.05 | 95.73 | Power-One3.3PVI-3.8-1-OUTD-x-US-y [208V]
Power-One | PVI-3600-OUTD-US-F [208V] | Y | N | N | 3.3 kW, 150-600 Vdc Utility Interactive Inverter | 3.3 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.24 | 3.3 | 0.24 | 100 | 330 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 89.4 | 93.1 | 94.4 | 94.9 | 94.8 | 94.5 | 94.5 | 90.5 | 94.1 | 95.2 | 95.6 | 95.6 | 95.2 | 95.2 | 85.9 | 91.8 | 93.4 | 94.4 | 94.6 | 94.3 | 93.9 | Power-One3.3PVI-3600-OUTD-US-F [208V]
Power-One | PVI-3600-US [208V] | Y | N | N | 3.3 kW, 150-600 Vdc Utility Interactive Inverter | 3.3 | 208 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.24 | 3.3 | 0.24 | 100 | 380 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 88.7 | 92.7 | 93.9 | 94.6 | 94.5 | 94.1 | 94.1 | 89.9 | 94 | 95 | 95.5 | 95.3 | 95 | 95 | 84.3 | 91.1 | 92.8 | 94 | 94 | 93.9 | 93.3 | Power-One3.3PVI-3600-US [208V]
Power-One | PVI-3.6-OUTD-S-US [208V] | Y | N | N | 3.6 kW, 208 Vac Utility Interactive Inverter | 3.6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | Power-One3.6PVI-3.6-OUTD-S-US [208V]
Power-One | PVI-3.6-OUTD-S-US [240V] | Y | N | N | 3.6 kW, 240 Vac Utility Interactive Inverter | 3.6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | Power-One3.6PVI-3.6-OUTD-S-US [240V]
Power-One | PVI-3.6-OUTD-S-US [277V] | Y | N | N | 3.6 kW, 277 Vac Utility Interactive Inverter | 3.6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | Power-One3.6PVI-3.6-OUTD-S-US [277V]
Power-One | PVI-3.6-OUTD-S-US-A [208V] | Y | N | N | 3.6 kW, 208 Vac Utility Interactive Inverter with arc detector | 3.6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | Power-One3.6PVI-3.6-OUTD-S-US-A [208V]
Power-One | PVI-3.6-OUTD-S-US-A [240V] | Y | N | N | 3.6 kW, 240 Vac Utility Interactive Inverter with arc detector | 3.6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | Power-One3.6PVI-3.6-OUTD-S-US-A [240V]
Power-One | PVI-3.6-OUTD-S-US-A [277V] | Y | N | N | 3.6 kW, 277 Vac Utility Interactive Inverter with arc detector | 3.6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | Power-One3.6PVI-3.6-OUTD-S-US-A [277V]
Power-One | PVI-3.6-OUTD-S-US-Z [208V] | Y | N | N | 3.6 kW, 208 Vac Utility Interactive Inverter with Zigbee | 3.6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | Power-One3.6PVI-3.6-OUTD-S-US-Z [208V]
Power-One | PVI-3.6-OUTD-S-US-Z [240V] | Y | N | N | 3.6 kW, 240 Vac Utility Interactive Inverter with Zigbee | 3.6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | Power-One3.6PVI-3.6-OUTD-S-US-Z [240V]
Power-One | PVI-3.6-OUTD-S-US-Z [277V] | Y | N | N | 3.6 kW, 277 Vac Utility Interactive Inverter with Zigbee | 3.6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | Power-One3.6PVI-3.6-OUTD-S-US-Z [277V]
Power-One | PVI-3.6-OUTD-S-US-Z-A [208V] | Y | N | N | 3.6 kW, 208 Vac Utility Interactive Inverter with arc detector | 3.6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | Power-One3.6PVI-3.6-OUTD-S-US-Z-A [208V]
Power-One | PVI-3.6-OUTD-S-US-Z-A [240V] | Y | N | N | 3.6 kW, 240 Vac Utility Interactive Inverter with arc detector | 3.6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | Power-One3.6PVI-3.6-OUTD-S-US-Z-A [240V]
Power-One | PVI-3.6-OUTD-S-US-Z-A [277V] | Y | N | N | 3.6 kW, 277 Vac Utility Interactive Inverter with arc detector | 3.6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | Power-One3.6PVI-3.6-OUTD-S-US-Z-A [277V]
Power-One | PVI-3.6-OUTD-US [208V] | Y | N | N | 3.6 kW, 208 Vac Utility Interactive Inverter. Model number may include -S- or -W | 3.6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 3.6 | 0.1 | 100 | 310 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.2 | 94.7 | 95.4 | 95.9 | 95.9 | 95.6 | 95.6 | 92.7 | 95.5 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 90.3 | 94.5 | 95.3 | 95.9 | 96 | 95.7 | 95.6 | Power-One3.6PVI-3.6-OUTD-US [208V]
Power-One | PVI-3.6-OUTD-US [240V] | Y | N | N | 3.6 kW, 240 Vac Utility Interactive Inverter. Model number may include -S- or -W | 3.6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 3.6 | 0.2 | 100 | 340 | 480 | 0.3 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.1 | 94.1 | 94.9 | 95.6 | 95.8 | 95.7 | 95.4 | 92.4 | 95.5 | 96.3 | 96.7 | 96.7 | 96.6 | 96.5 | 90.2 | 94.6 | 95.6 | 96.2 | 96.4 | 96.3 | 95.9 | Power-One3.6PVI-3.6-OUTD-US [240V]
Power-One | PVI-3.6-OUTD-US [277V] | Y | N | N | 3.6 kW, 277 Vac Utility Interactive Inverter. Model number may include -S- or -W | 3.6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 3.6 | 0.2 | 100 | 395 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 90 | 93.4 | 94.4 | 95.4 | 95.7 | 95.6 | 95.1 | 91.9 | 95.4 | 96.3 | 96.9 | 97 | 96.9 | 96.6 | 90.4 | 94.9 | 95.9 | 96.6 | 96.8 | 96.8 | 96.3 | Power-One3.6PVI-3.6-OUTD-US [277V]
Power-One | PVI-3600-OUTD-US-F [240V] | Y | N | N | 3.6 kW, 150-600 Vdc Utility Interactive Inverter | 3.6 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.34 | 3.6 | 0.34 | 100 | 380 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 88.8 | 92.9 | 94.1 | 94.8 | 94.8 | 94.6 | 94.4 | 90.1 | 94.3 | 95.2 | 95.8 | 95.9 | 95.6 | 95.4 | 87.3 | 92.8 | 94.2 | 95.1 | 95.4 | 95.1 | 94.7 | Power-One3.6PVI-3600-OUTD-US-F [240V]
Power-One | PVI-3600-US [240V] | Y | N | N | 3.6 kW, 150-600 Vdc Utility Interactive Inverter | 3.6 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.34 | 3.6 | 0.34 | 100 | 380 | 480 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 88.1 | 92 | 93.5 | 94.4 | 94.4 | 94.1 | 93.9 | 89.4 | 93.9 | 95 | 95.6 | 95.6 | 95.3 | 95.2 | 85.9 | 91.9 | 93.6 | 94.7 | 94.9 | 94.7 | 94.2 | Power-One3.6PVI-3600-US [240V]
Power-One | PVI-3.8-1-OUTD-x-US-y [240V] | Y | N | N | 3.8 kW, 240 Vac Inverter, where x = (blank) or S and y = PG or NG | 3.8 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 3.8 | 0.1 | 100 | 340 | 416 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93.72 | 95.75 | 96.23 | 96.47 | 96.44 | 96.09 | 96.26 | 92.77 | 95.88 | 96.59 | 96.88 | 96.84 | 96.81 | 96.6 | 90.71 | 94.81 | 95.88 | 96.53 | 96.5 | 96.49 | 96.12 | Power-One3.8PVI-3.8-1-OUTD-x-US-y [240V]
Power-One | PVI-3.8-1-OUTD-x-US-y [277V] | Y | N | N | 3.8 kW, 277 Vac Inverter, where x = (blank) or S and y = PG or NG | 3.8 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 3.8 | 0.1 | 100 | 362 | 416 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.86 | 95.37 | 95.99 | 96.34 | 96.38 | 96.14 | 96.12 | 92.27 | 95.6 | 96.41 | 96.92 | 96.88 | 96.93 | 96.59 | 91.34 | 95.21 | 96.22 | 96.83 | 96.8 | 96.85 | 96.44 | Power-One3.8PVI-3.8-1-OUTD-x-US-y [277V]
Power-One | PVI-3.8-OUTD-S-US [208V] | Y | N | N | 3.3 kW, 208 Vac Utility Interactive Inverter | 3.8 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | Power-One3.8PVI-3.8-OUTD-S-US [208V]
Power-One | PVI-3.8-OUTD-S-US [240V] | Y | N | N | 3.8 kW, 240 Vac Utility Interactive Inverter | 3.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | Power-One3.8PVI-3.8-OUTD-S-US [240V]
Power-One | PVI-3.8-OUTD-S-US [277V] | Y | N | N | 3.8 kW, 277 Vac Utility Interactive Inverter | 3.8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | Power-One3.8PVI-3.8-OUTD-S-US [277V]
Power-One | PVI-3.8-OUTD-S-US-A [208V] | Y | N | N | 3.3 kW, 208 Vac Utility Interactive Inverter with arc detector | 3.8 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | Power-One3.8PVI-3.8-OUTD-S-US-A [208V]
Power-One | PVI-3.8-OUTD-S-US-A [240V] | Y | N | N | 3.8 kW, 240 Vac Utility Interactive Inverter with arc detector | 3.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | Power-One3.8PVI-3.8-OUTD-S-US-A [240V]
Power-One | PVI-3.8-OUTD-S-US-A [277V] | Y | N | N | 3.8 kW, 277 Vac Utility Interactive Inverter with arc detector | 3.8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | Power-One3.8PVI-3.8-OUTD-S-US-A [277V]
Power-One | PVI-3.8-OUTD-S-US-Z [208V] | Y | N | N | 3.3 kW, 208 Vac Utility Interactive Inverter | 3.8 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | Power-One3.8PVI-3.8-OUTD-S-US-Z [208V]
Power-One | PVI-3.8-OUTD-S-US-Z [240V] | Y | N | N | 3.3 kW, 240 Vac Utility Interactive Inverter | 3.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | Power-One3.8PVI-3.8-OUTD-S-US-Z [240V] |  | 2018-03-05
Power-One | PVI-3.8-OUTD-S-US-Z [277V] | Y | N | N | 3.3 kW, 277 Vac Utility Interactive Inverter | 3.8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | Power-One3.8PVI-3.8-OUTD-S-US-Z [277V] |  | 2018-03-05
Power-One | PVI-3.8-OUTD-S-US-Z-A [208V] | Y | N | N | 3.3 kW, 208 Vac Utility Interactive Inverter with arc detector | 3.8 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | Power-One3.8PVI-3.8-OUTD-S-US-Z-A [208V]
Power-One | PVI-3.8-OUTD-S-US-Z-A [240V] | Y | N | N | 3.8 kW, 240 Vac Utility Interactive Inverter with arc detector | 3.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | Power-One3.8PVI-3.8-OUTD-S-US-Z-A [240V]
Power-One | PVI-3.8-OUTD-S-US-Z-A [277V] | Y | N | N | 3.8 kW, 277 Vac Utility Interactive Inverter with arc detector | 3.8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | Power-One3.8PVI-3.8-OUTD-S-US-Z-A [277V]
Power-One | PVI-3.8-OUTD-US [208V] | Y | N | N | 3.3 kW, 208 Vac Utility Interactive Inverter | 3.8 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.12 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91.5 | 94.3 | 95.1 | 95.6 | 95.6 | 95.4 | 95.3 | 92.1 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96.1 | 89.1 | 93.9 | 95 | 95.7 | 95.9 | 95.8 | 95.4 | Power-One3.8PVI-3.8-OUTD-US [208V]
Power-One | PVI-3.8-OUTD-US [240V] | Y | N | N | 3.8 kW, 240 Vac Utility Interactive Inverter | 3.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.16 |  |  | 100 | 340 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.4 | 94.2 | 94.9 | 95.5 | 95.6 | 95.5 | 95.3 | 92.6 | 95.5 | 96.2 | 96.6 | 96.7 | 96.6 | 96.4 | 90.3 | 94.5 | 95.5 | 96.2 | 96.3 | 96.3 | 95.9 | Power-One3.8PVI-3.8-OUTD-US [240V]
Power-One | PVI-3.8-OUTD-US [277V] | Y | N | N | 3.8 kW, 277 Vac Utility Interactive Inverter | 3.8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.22 |  |  | 100 | 395 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 90.3 | 93.6 | 94.5 | 95.3 | 95.6 | 95.5 | 95.1 | 92 | 95.3 | 96.2 | 96.8 | 96.9 | 96.9 | 96.5 | 90.4 | 94.7 | 95.8 | 96.5 | 96.7 | 96.8 | 96.2 | Power-One3.8PVI-3.8-OUTD-US [277V]
Power-One | PVI-4.2-OUTD-S-US [208V] | Y | N | N | 4.2 kW, 208 Vac Utility Interactive Inverter | 4.2 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.94 | 95.03 | 95.58 | 95.92 | 95.78 | 95.39 | 95.62 | 93.47 | 95.8 | 96.25 | 96.39 | 96.26 | 95.9 | 96.14 | 91.39 | 94.89 | 95.55 | 95.94 | 95.83 | 95.47 | 95.58 | Power-One4.2PVI-4.2-OUTD-S-US [208V]
Power-One | PVI-4.2-OUTD-S-US [240V] | Y | N | N | 4.2 kW, 240 Vac Utility Interactive Inverter | 4.2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.83 | 94.43 | 95.2 | 95.75 | 95.79 | 95.42 | 95.47 | 93.26 | 95.9 | 96.5 | 96.69 | 96.7 | 96.45 | 96.48 | 91.29 | 95.06 | 95.86 | 96.32 | 96.37 | 96.19 | 96.02 | Power-One4.2PVI-4.2-OUTD-S-US [240V]
Power-One | PVI-4.2-OUTD-S-US [277V] | Y | N | N | 4.2 kW, 277 Vac Utility Interactive Inverter | 4.2 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.84 | 93.88 | 94.81 | 95.56 | 95.7 | 95.55 | 95.27 | 92.78 | 95.81 | 96.56 | 96.99 | 96.97 | 96.88 | 96.7 | 91.63 | 95.36 | 96.18 | 96.72 | 96.8 | 96.74 | 96.43 | Power-One4.2PVI-4.2-OUTD-S-US [277V]
Power-One | PVI-4.2-OUTD-S-US-A [208V] | Y | N | N | 4.2 kW, 208 Vac Utility Interactive Inverter with arc detector | 4.2 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.94 | 95.03 | 95.58 | 95.92 | 95.78 | 95.39 | 95.62 | 93.47 | 95.8 | 96.25 | 96.39 | 96.26 | 95.9 | 96.14 | 91.39 | 94.89 | 95.55 | 95.94 | 95.83 | 95.47 | 95.58 | Power-One4.2PVI-4.2-OUTD-S-US-A [208V]
Power-One | PVI-4.2-OUTD-S-US-A [240V] | Y | N | N | 4.2 kW, 240 Vac Utility Interactive Inverter with arc detector | 4.2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.83 | 94.43 | 95.2 | 95.75 | 95.79 | 95.42 | 95.47 | 93.26 | 95.9 | 96.5 | 96.69 | 96.7 | 96.45 | 96.48 | 91.29 | 95.06 | 95.86 | 96.32 | 96.37 | 96.19 | 96.02 | Power-One4.2PVI-4.2-OUTD-S-US-A [240V]
Power-One | PVI-4.2-OUTD-S-US-A [277V] | Y | N | N | 4.2 kW, 277 Vac Utility Interactive Inverter with arc detector | 4.2 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.84 | 93.88 | 94.81 | 95.56 | 95.7 | 95.55 | 95.27 | 92.78 | 95.81 | 96.56 | 96.99 | 96.97 | 96.88 | 96.7 | 91.63 | 95.36 | 96.18 | 96.72 | 96.8 | 96.74 | 96.43 | Power-One4.2PVI-4.2-OUTD-S-US-A [277V]
Power-One | PVI-4.2-OUTD-S-US-Z [208V] | Y | N | N | 4.2 kW, 208 Vac Utility Interactive Inverter with Zigbee | 4.2 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6 | Power-One4.2PVI-4.2-OUTD-S-US-Z [208V]
Power-One | PVI-4.2-OUTD-S-US-Z [240V] | Y | N | N | 4.2 kW, 240 Vac Utility Interactive Inverter with Zigbee | 4.2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96 | Power-One4.2PVI-4.2-OUTD-S-US-Z [240V]
Power-One | PVI-4.2-OUTD-S-US-Z [277V] | Y | N | N | 4.2 kW, 277 Vac Utility Interactive Inverter with Zigbee | 4.2 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | Power-One4.2PVI-4.2-OUTD-S-US-Z [277V]
Power-One | PVI-4.2-OUTD-S-US-Z-A [208V] | Y | N | N | 4.2 kW, 208 Vac Utility Interactive Inverter with Zigbee and arc detector | 4.2 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.9 | 95 | 95.6 | 95.9 | 95.8 | 95.4 | 95.6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.3 | 95.9 | 96.1 | 91.4 | 94.9 | 95.6 | 95.9 | 95.8 | 95.5 | 95.6 | Power-One4.2PVI-4.2-OUTD-S-US-Z-A [208V]
Power-One | PVI-4.2-OUTD-S-US-Z-A [240V] | Y | N | N | 4.2 kW, 240 Vac Utility Interactive Inverter with Zigbee and arc detector | 4.2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.8 | 94.4 | 95.2 | 95.8 | 95.8 | 95.4 | 95.5 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | 91.3 | 95.1 | 95.9 | 96.3 | 96.4 | 96.2 | 96 | Power-One4.2PVI-4.2-OUTD-S-US-Z-A [240V]
Power-One | PVI-4.2-OUTD-S-US-Z-A [277V] | Y | N | N | 4.2 kW, 277 Vac Utility Interactive Inverter with Zigbee and arc detector | 4.2 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.8 | 93.9 | 94.8 | 95.6 | 95.7 | 95.6 | 95.3 | 92.8 | 95.8 | 96.6 | 97 | 97 | 96.9 | 96.7 | 91.6 | 95.4 | 96.2 | 96.7 | 96.8 | 96.7 | 96.4 | Power-One4.2PVI-4.2-OUTD-S-US-Z-A [277V]
Power-One | PVI-4.2-OUTD-US [208V] | Y | N | N | 4.2 kW, 208 Vac Utility Interactive Inverter. Model Number may include -S- or -W | 4.2 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 4.2 | 0.1 | 100 | 310 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.94 | 95.03 | 95.58 | 95.92 | 95.78 | 95.39 | 95.62 | 93.47 | 95.8 | 96.25 | 96.39 | 96.26 | 95.9 | 96.14 | 91.39 | 94.89 | 95.55 | 95.94 | 95.83 | 95.47 | 95.58 | Power-One4.2PVI-4.2-OUTD-US [208V]
Power-One | PVI-4.2-OUTD-US [240V] | Y | N | N | 4.2 kW, 240 Vac Utility Interactive Inverter. Model Number may include -S- or -W | 4.2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 4.2 | 0.2 | 100 | 340 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.83 | 94.43 | 95.2 | 95.75 | 95.79 | 95.42 | 95.47 | 93.26 | 95.9 | 96.5 | 96.69 | 96.7 | 96.45 | 96.48 | 91.29 | 95.06 | 95.86 | 96.32 | 96.37 | 96.19 | 96.02 | Power-One4.2PVI-4.2-OUTD-US [240V]
Power-One | PVI-4.2-OUTD-US [277V] | Y | N | N | 4.2 kW, 277 Vac Utility Interactive Inverter. Model Number may include -S- or -W | 4.2 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.2 | 4.2 | 0.2 | 100 | 395 | 480 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 90.84 | 93.88 | 94.81 | 95.56 | 95.7 | 95.55 | 95.27 | 92.78 | 95.81 | 96.56 | 96.99 | 96.97 | 96.88 | 96.7 | 91.63 | 95.36 | 96.18 | 96.72 | 96.8 | 96.74 | 96.43 | Power-One4.2PVI-4.2-OUTD-US [277V]
Power-One | PVI-4.6-1-OUTD-x-US-y [208V] | Y | N | N | 4.6 kW, 208 Vac Inverter, where x = (blank) or S and y = PG or NG | 4.6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 4.6 | 0.1 | 100 | 310 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.57 | 96.13 | 96.17 | 96.4 | 95.91 | 95.12 | 95.96 | 94.12 | 96.25 | 96.59 | 96.68 | 96.51 | 96.15 | 96.43 | 91.78 | 95.13 | 95.92 | 96.31 | 96 | 95.92 | 95.84 | Power-One4.6PVI-4.6-1-OUTD-x-US-y [208V]
Power-One | PVI-4.6-1-OUTD-x-US-y [240V] | Y | N | N | 4.6 kW, 240 Vac Inverter, where x = (blank) or S and y = PG or NG | 4.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 4.6 | 0.1 | 100 | 340 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.08 | 96.02 | 96.23 | 96.45 | 96.18 | 95.56 | 96.12 | 93.82 | 96.27 | 96.7 | 96.87 | 96.79 | 96.64 | 96.64 | 92 | 95.4 | 96.18 | 96.62 | 96.45 | 96.48 | 96.22 | Power-One4.6PVI-4.6-1-OUTD-x-US-y [240V]
Power-One | PVI-4.6-1-OUTD-x-US-y [277V] | Y | N | N | 4.6 kW, 277 Vac Inverter, where x = (blank) or S and y = PG or NG | 4.6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 4.6 | 0.1 | 100 | 360 | 416 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.41 | 95.73 | 96.14 | 96.42 | 96.31 | 95.85 | 96.14 | 93.31 | 96.05 | 96.63 | 96.96 | 96.93 | 96.89 | 96.71 | 92.56 | 95.76 | 96.55 | 96.95 | 96.8 | 96.84 | 96.58 | Power-One4.6PVI-4.6-1-OUTD-x-US-y [277V]
Power-One | PVI-5000-OUTD-S-US-Z [208V] | Y | N | N | 5 kW, 208 Vac Utility Interactive Inverter with Zigbee | 5 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | Power-One5PVI-5000-OUTD-S-US-Z [208V]
Power-One | PVI-5000-OUTD-S-US-Z [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter with Zigbee | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | Power-One5PVI-5000-OUTD-S-US-Z [240V]
Power-One | PVI-5000-OUTD-S-US-Z [277V] | Y | N | N | 5 kW, 277 Vac Utility Interactive Inverter with Zigbee | 5 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | Power-One5PVI-5000-OUTD-S-US-Z [277V]
Power-One | PVI-5000-OUTD-S-US-Z-A [208V] | Y | N | N | 5 kW, 208 Vac Utility Interactive Inverter with Zigbee and arc detector | 5 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | Power-One5PVI-5000-OUTD-S-US-Z-A [208V]
Power-One | PVI-5000-OUTD-S-US-Z-A [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter with Zigbee and arc detector | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | Power-One5PVI-5000-OUTD-S-US-Z-A [240V]
Power-One | PVI-5000-OUTD-S-US-Z-A [277V] | Y | N | N | 5 kW, 277 Vac Utility Interactive Inverter with Zigbee and arc detector | 5 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | Power-One5PVI-5000-OUTD-S-US-Z-A [277V]
Power-One | PVI-5000-OUTD-US [208V] | Y | N | N | 5 kW, 208 Vac Utility Interactive Inverter | 5 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | Power-One5PVI-5000-OUTD-US [208V]
Power-One | PVI-5000-OUTD-US [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | Power-One5PVI-5000-OUTD-US [240V]
Power-One | PVI-5000-OUTD-US [277V] | Y | N | N | 5 kW, 277 Vac Utility Interactive Inverter | 5 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | Power-One5PVI-5000-OUTD-US [277V]
Power-One | PVI-5000-OUTD-US-A [208V] | Y | N | N | 5 kW, 208 Vac Utility Interactive Inverter with arc detector | 5 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | Power-One5PVI-5000-OUTD-US-A [208V]
Power-One | PVI-5000-OUTD-US-A [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter with arc detector | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | Power-One5PVI-5000-OUTD-US-A [240V]
Power-One | PVI-5000-OUTD-US-A [277V] | Y | N | N | 5 kW, 277 Vac Utility Interactive Inverter with arc detector | 5 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | Power-One5PVI-5000-OUTD-US-A [277V]
Power-One | PVI-5000-OUTD-US-Z [208V] | Y | N | N | 5 kW, 208 Vac Utility Interactive Inverter | 5 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | Power-One5PVI-5000-OUTD-US-Z [208V]
Power-One | PVI-5000-OUTD-US-Z [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | Power-One5PVI-5000-OUTD-US-Z [240V]
Power-One | PVI-5000-OUTD-US-Z [277V] | Y | N | N | 5 kW, 277 Vac Utility Interactive Inverter | 5 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | Power-One5PVI-5000-OUTD-US-Z [277V]
Power-One | PVI-5000-OUTD-US-Z-A [208V] | Y | N | N | 5 kW, 208 Vac Utility Interactive Inverter | 5 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.4 | 95.7 | 96.2 | 96.4 | 96.2 | 95.8 | 96.1 | 93.6 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 96.4 | 90.9 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.8 | Power-One5PVI-5000-OUTD-US-Z-A [208V]
Power-One | PVI-5000-OUTD-US-Z-A [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.5 | 95.5 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | 93.8 | 96.2 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 91.5 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | Power-One5PVI-5000-OUTD-US-Z-A [240V]
Power-One | PVI-5000-OUTD-US-Z-A [277V] | Y | N | N | 5 kW, 277 Vac Utility Interactive Inverter | 5 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.6 | 95 | 95.9 | 96.4 | 96.5 | 96.3 | 96.1 | 92.5 | 95.7 | 96.5 | 97.1 | 97.1 | 97 | 96.8 | 90.9 | 95 | 95.9 | 96.7 | 96.9 | 96.9 | 96.4 | Power-One5PVI-5000-OUTD-US-Z-A [277V]
Power-One | PVI-6000-OUTD-S-US-A [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter with arc detector | 6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | Power-One6PVI-6000-OUTD-S-US-A [208V]
Power-One | PVI-6000-OUTD-S-US-A [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter with arc detector | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | Power-One6PVI-6000-OUTD-S-US-A [240V]
Power-One | PVI-6000-OUTD-S-US-A [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter with arc detector | 6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | Power-One6PVI-6000-OUTD-S-US-A [277V]
Power-One | PVI-6000-OUTD-S-US-Z [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter with Zigbee | 6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | Power-One6PVI-6000-OUTD-S-US-Z [208V]
Power-One | PVI-6000-OUTD-S-US-Z [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter with Zigbee | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | Power-One6PVI-6000-OUTD-S-US-Z [240V]
Power-One | PVI-6000-OUTD-S-US-Z [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter with Zigbee | 6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | Power-One6PVI-6000-OUTD-S-US-Z [277V]
Power-One | PVI-6000-OUTD-S-US-Z-A [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter with Zigbee and arc detector | 6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | Power-One6PVI-6000-OUTD-S-US-Z-A [208V]
Power-One | PVI-6000-OUTD-S-US-Z-A [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter with Zigbee and arc detector | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | Power-One6PVI-6000-OUTD-S-US-Z-A [240V]
Power-One | PVI-6000-OUTD-S-US-Z-A [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter with Zigbee and arc detector | 6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | Power-One6PVI-6000-OUTD-S-US-Z-A [277V]
Power-One | PVI-6000-OUTD-US [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter | 6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | Power-One6PVI-6000-OUTD-US [208V]
Power-One | PVI-6000-OUTD-US [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | Power-One6PVI-6000-OUTD-US [240V]
Power-One | PVI-6000-OUTD-US [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | Power-One6PVI-6000-OUTD-US [277V]
Power-One | PVI-6000-OUTD-US-A [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter with arc detector | 6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | Power-One6PVI-6000-OUTD-US-A [208V]
Power-One | PVI-6000-OUTD-US-A [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter with arc detector | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | Power-One6PVI-6000-OUTD-US-A [240V]
Power-One | PVI-6000-OUTD-US-A [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter with arc detector | 6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | Power-One6PVI-6000-OUTD-US-A [277V]
Power-One | PVI-6000-OUTD-US-Z [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter | 6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | Power-One6PVI-6000-OUTD-US-Z [208V]
Power-One | PVI-6000-OUTD-US-Z [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | Power-One6PVI-6000-OUTD-US-Z [240V]
Power-One | PVI-6000-OUTD-US-Z [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | Power-One6PVI-6000-OUTD-US-Z [277V]
Power-One | PVI-6000-OUTD-US-Z-A [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter | 6 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.18 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94 | 96 | 96.4 | 96.3 | 96 | 95.5 | 96 | 94.3 | 96.2 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 92.1 | 95.1 | 95.9 | 96.1 | 96 | 95.7 | 95.8 | Power-One6PVI-6000-OUTD-US-Z-A [208V]
Power-One | PVI-6000-OUTD-US-Z-A [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.24 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.5 | 95.8 | 96.3 | 96.4 | 96.2 | 95.8 | 96.1 | 94.6 | 96.5 | 96.9 | 96.9 | 96.8 | 96.5 | 96.7 | 92.6 | 95.5 | 96.1 | 96.5 | 96.4 | 96.2 | 96.2 | Power-One6PVI-6000-OUTD-US-Z-A [240V]
Power-One | PVI-6000-OUTD-US-Z-A [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.32 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 93.5 | 96.2 | 96.8 | 97.1 | 97.1 | 97 | 96.9 | 92.2 | 95.5 | 96.3 | 96.8 | 96.9 | 96.9 | 96.5 | Power-One6PVI-6000-OUTD-US-Z-A [277V]
Power-One | UNO-7.6-TL-OUTD-S-US-A [208V] | Y | N | N | transformerless Utility Interactive Inverter with arc detector | 7.6 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.33 |  |  | 100 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.3 | 95.3 | 95.8 | 95.9 | 95.8 | 95.6 | 95.7 | 95.2 | 96.8 | 97.1 | 97.2 | 97.1 | 96.9 | 97 | 93.2 | 96 | 96.4 | 96.8 | 96.8 | 96.6 | 96.5 | Power-One7.6UNO-7.6-TL-OUTD-S-US-A [208V]
Power-One | UNO-7.6-TL-OUTD-S-US-A [240V] | Y | N | N | transformerless Utility Interactive Inverter with arc detector | 7.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.4 |  |  | 100 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.5 | 95 | 95.7 | 96 | 96 | 95.8 | 95.7 | 95 | 96.9 | 97.3 | 97.5 | 97.5 | 97.3 | 97.3 | 93.3 | 96.2 | 96.8 | 97.2 | 97.2 | 97.1 | 96.9 | Power-One7.6UNO-7.6-TL-OUTD-S-US-A [240V]
Power-One | UNO-7.6-TL-OUTD-S-US-A [277V] | Y | N | N | transformerless Utility Interactive Inverter with arc detector | 7.6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.5 |  |  | 100 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 91.5 | 94.6 | 95.4 | 95.9 | 95.9 | 95.9 | 95.6 | 93.1 | 95.7 | 96.3 | 96.8 | 96.9 | 96.9 | 96.6 | 93.6 | 96.4 | 97 | 97.5 | 97.6 | 97.5 | 97.3 | Power-One7.6UNO-7.6-TL-OUTD-S-US-A [277V]
Power-One | UNO-7.6-TL-OUTD-S-US-Z-A [208V] | Y | N | N | transformerless Utility Interactive Inverter with arc detector | 7.6 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.33 |  |  | 100 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.3 | 95.3 | 95.8 | 95.9 | 95.8 | 95.6 | 95.7 | 95.2 | 96.8 | 97.1 | 97.2 | 97.1 | 96.9 | 97 | 93.2 | 96 | 96.4 | 96.8 | 96.8 | 96.6 | 96.5 | Power-One7.6UNO-7.6-TL-OUTD-S-US-Z-A [208V]
Power-One | UNO-7.6-TL-OUTD-S-US-Z-A [240V] | Y | N | N | transformerless Utility Interactive Inverter with arc detector | 7.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.4 |  |  | 100 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 92.5 | 95 | 95.7 | 96 | 96 | 95.8 | 95.7 | 95 | 96.9 | 97.3 | 97.5 | 97.5 | 97.3 | 97.3 | 93.3 | 96.2 | 96.8 | 97.2 | 97.2 | 97.1 | 96.9 | Power-One7.6UNO-7.6-TL-OUTD-S-US-Z-A [240V]
Power-One | UNO-7.6-TL-OUTD-S-US-Z-A [277V] | Y | N | N | transformerless Utility Interactive Inverter with arc detector | 7.6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.5 |  |  | 100 | 380 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 91.5 | 94.6 | 95.4 | 95.9 | 95.9 | 95.9 | 95.6 | 93.1 | 95.7 | 96.3 | 96.8 | 96.9 | 96.9 | 96.6 | 93.6 | 96.4 | 97 | 97.5 | 97.6 | 97.5 | 97.3 | Power-One7.6UNO-7.6-TL-OUTD-S-US-Z-A [277V]
Power-One | UNO-8.6-TL-OUTD-S-US-A [240V] | Y | N | N | transformerless Utility Interactive Inverter with arc detector | 8.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.5 |  |  | 100 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.1 | 94.9 | 95.6 | 95.9 | 95.9 | 95.8 | 95.7 | 93.6 | 95.9 | 96.5 | 96.8 | 96.9 | 96.8 | 96.6 | 94.2 | 96.7 | 97.2 | 97.5 | 97.6 | 97.5 | 97.3 | Power-One8.6UNO-8.6-TL-OUTD-S-US-A [240V]
Power-One | UNO-8.6-TL-OUTD-S-US-A [277V] | Y | N | N | transformerless Utility Interactive Inverter with arc detector | 8.6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.4 |  |  | 100 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93 | 95.2 | 95.8 | 96 | 95.9 | 95.7 | 95.8 | 95.4 | 97 | 97.4 | 97.5 | 97.5 | 97.3 | 97.3 | 94 | 96.4 | 96.9 | 97.2 | 97.2 | 97 | 97 | Power-One8.6UNO-8.6-TL-OUTD-S-US-A [277V]
Power-One | UNO-8.6-TL-OUTD-S-US-Z-A [240V] | Y | N | N | transformerless Utility Interactive Inverter with arc detector | 8.6 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.5 |  |  | 100 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 92.1 | 94.9 | 95.6 | 95.9 | 95.9 | 95.8 | 95.7 | 93.6 | 95.9 | 96.5 | 96.8 | 96.9 | 96.8 | 96.6 | 94.2 | 96.7 | 97.2 | 97.5 | 97.6 | 97.5 | 97.3 | Power-One8.6UNO-8.6-TL-OUTD-S-US-Z-A [240V]
Power-One | UNO-8.6-TL-OUTD-S-US-Z-A [277V] | Y | N | N | transformerless Utility Interactive Inverter with arc detector | 8.6 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.4 |  |  | 100 | 380 | 480 | 0.86 | 1.72 | 2.58 | 4.3 | 6.45 | 8.6 | 93 | 95.2 | 95.8 | 96 | 95.9 | 95.7 | 95.8 | 95.4 | 97 | 97.4 | 97.5 | 97.5 | 97.3 | 97.3 | 94 | 96.4 | 96.9 | 97.2 | 97.2 | 97 | 97 | Power-One8.6UNO-8.6-TL-OUTD-S-US-Z-A [277V]
Power-One | PVI-10.0-I-OUTD-x-US-208-y [208V] | Y | N | N | 10 kW, 208 Vac Inverter, x may be empty, S, S1 or S2; y either PG or NG | 10 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.1 | 10 | 0.1 | 220 | 320 | 416 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.5 | 96.1 | 96.2 | 96.3 | 95.7 | 94.8 | 95.8 | 94.4 | 96.3 | 96.5 | 96.5 | 96.3 | 95.7 | 96.2 | 93.1 | 95.7 | 96.2 | 96.2 | 95.9 | 95.5 | 95.8 | Power-One10PVI-10.0-I-OUTD-x-US-208-y [208V]
Power-One | PVI-10.0-I-OUTD-x-US-480-y-z [480V] | Y | N | N | 10 kW, 480 Vac Inverter, x may be empty, S, S1 or S2; y either PG or NG; z may be empty or 12A | 10 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.4 | 10 | 0.4 | 220 | 362 | 416 | 1 | 2 | 3 | 5 | 7.5 | 10 | 92.7 | 95.4 | 96.2 | 96.9 | 96.8 | 96.4 | 96.5 | 92.6 | 96 | 96.8 | 97.2 | 97.3 | 97.3 | 97 | 92.3 | 95.9 | 96.8 | 97.3 | 97.3 | 97.3 | 97 | Power-One10PVI-10.0-I-OUTD-x-US-480-y-z [480V]
Power-One | PVI-12.0-I-OUTD-x-US-480-y [480V] | Y | N | N | 12 kW, 480 Vac Inverter, x may be empty, S, S1 or S2; y either PG or NG | 12 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.4 | 12 | 0.4 | 250 | 370 | 416 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 93.7 | 96 | 96.5 | 97 | 96.9 | 96.4 | 96.7 | 93.6 | 96.3 | 97 | 97.2 | 97.3 | 97.2 | 97 | 93.4 | 96.4 | 97 | 97.2 | 97.3 | 97.3 | 97.1 | Power-One12PVI-12.0-I-OUTD-x-US-480-y [480V]
Power-One | TRIO-20.0-TL-OUTD-S1-480-A [480V] | Y | N | N | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9 | Power-One20TRIO-20.0-TL-OUTD-S1-480-A [480V]
Power-One | TRIO-20.0-TL-OUTD-S1A-480-A [480V] | Y | N | N | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9 | Power-One20TRIO-20.0-TL-OUTD-S1A-480-A [480V]
Power-One | TRIO-20.0-TL-OUTD-S1A-US-480 [480V] | Y | N | N | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9 | Power-One20TRIO-20.0-TL-OUTD-S1A-US-480 [480V]
Power-One | TRIO-20.0-TL-OUTD-S1B-480-A [480V] | Y | N | N | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9 | Power-One20TRIO-20.0-TL-OUTD-S1B-480-A [480V]
Power-One | TRIO-20.0-TL-OUTD-S1B-US-480 [480V] | Y | N | N | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9 | Power-One20TRIO-20.0-TL-OUTD-S1B-US-480 [480V]
Power-One | TRIO-20.0-TL-OUTD-S1-US-480 [480V] | Y | N | N | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9 | Power-One20TRIO-20.0-TL-OUTD-S1-US-480 [480V]
Power-One | TRIO-20.0-TL-OUTD-S-480-A [480V] | Y | N | N | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9 | Power-One20TRIO-20.0-TL-OUTD-S-480-A [480V]
Power-One | TRIO-20.0-TL-OUTD-S-US-480 [480V] | Y | N | N | 20 kW, 480 Vac Inverter with arc detector | 20 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.61 |  |  | 450 | 700 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 93.5 | 95.4 | 96.3 | 96.9 | 97 | 97 | 96.7 | 94.5 | 96.7 | 97.3 | 97.7 | 97.7 | 97.7 | 97.5 | 95.4 | 97.2 | 97.8 | 98.1 | 98.2 | 98.1 | 97.9 | Power-One20TRIO-20.0-TL-OUTD-S-US-480 [480V]
Power-One | TRIO-27.6-TL-OUTD-S1-480-A [480V] | Y | N | N | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1 | Power-One27.6TRIO-27.6-TL-OUTD-S1-480-A [480V]
Power-One | TRIO-27.6-TL-OUTD-S1A-480-A [480V] | Y | N | N | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1 | Power-One27.6TRIO-27.6-TL-OUTD-S1A-480-A [480V]
Power-One | TRIO-27.6-TL-OUTD-S1A-US-480 [480V] | Y | N | N | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1 | Power-One27.6TRIO-27.6-TL-OUTD-S1A-US-480 [480V]
Power-One | TRIO-27.6-TL-OUTD-S1B-480-A [480V] | Y | N | N | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1 | Power-One27.6TRIO-27.6-TL-OUTD-S1B-480-A [480V]
Power-One | TRIO-27.6-TL-OUTD-S1B-US-480 [480V] | Y | N | N | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1 | Power-One27.6TRIO-27.6-TL-OUTD-S1B-US-480 [480V]
Power-One | TRIO-27.6-TL-OUTD-S1-US-480 [480V] | Y | N | N | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1 | Power-One27.6TRIO-27.6-TL-OUTD-S1-US-480 [480V]
Power-One | TRIO-27.6-TL-OUTD-S-480-A [480V] | Y | N | N | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1 | Power-One27.6TRIO-27.6-TL-OUTD-S-480-A [480V]
Power-One | TRIO-27.6-TL-OUTD-S-US-480 [480V] | Y | N | N | 27.6 kW, 480 Vac Inverter with arc detector | 27.6 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 0.61 |  |  | 520 | 715 | 800 | 2.76 | 5.52 | 8.28 | 13.8 | 20.7 | 27.6 | 94.8 | 96.4 | 97 | 97.4 | 97.4 | 97.3 | 97.2 | 95.4 | 97.1 | 97.6 | 97.8 | 97.9 | 97.8 | 97.7 | 96.1 | 97.6 | 98 | 98.2 | 98.2 | 98.2 | 98.1 | Power-One27.6TRIO-27.6-TL-OUTD-S-US-480 [480V]
Power-One | PVI-CENTRAL-50-US [208V] | Y | N | N | 50 kW, 208 Vac Utility Interactive Inverter | 50 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 33 | 50 | 33 | 330 | 370 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.7 | 94.5 | 95.4 | 95.6 | 95.3 | 94.7 | 95.1 | 90.4 | 94.4 | 95.3 | 95.6 | 95.2 | 94.6 | 95 | 89.7 | 94 | 94.8 | 95.2 | 94.9 | 94.4 | 94.7 | Power-One50PVI-CENTRAL-50-US [208V]
Power-One | PVI-CENTRAL-50-US [480V] | Y | N | N | 50 kW, 480 Vac Utility Interactive Inverter | 50 | 480 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 41 | 50 | 41 | 330 | 370 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.5 | 94.4 | 95.3 | 95.7 | 95.6 | 95.1 | 95.3 | 90.2 | 94.2 | 95.2 | 95.6 | 95.5 | 95 | 95.2 | 89.5 | 93.8 | 94.9 | 95.3 | 95.3 | 94.8 | 94.9 | Power-One50PVI-CENTRAL-50-US [480V]
Power-One | PVI-CENTRAL-100-US [208V] | Y | N | N | 100 kW, 208 Vac Utility Interactive Inverter | 100 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 47 | 100 | 47 | 330 | 370 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.5 | 94.7 | 95.4 | 95.6 | 95.3 | 94.7 | 95.2 | 91.2 | 94.5 | 95.3 | 95.5 | 95.2 | 94.6 | 95.1 | 90.3 | 94.1 | 94.9 | 95.2 | 95 | 94.4 | 94.7 | Power-One100PVI-CENTRAL-100-US [208V]
Power-One | PVI-CENTRAL-100-US [480V] | Y | N | N | 100 kW, 480 Vac Utility Interactive Inverter | 100 | 480 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 50 | 100 | 50 | 330 | 370 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.5 | 94.8 | 95.5 | 95.7 | 95.5 | 94.7 | 95.3 | 91.2 | 94.6 | 95.3 | 95.6 | 95.4 | 94.6 | 95.2 | 90.3 | 94.2 | 95 | 95.3 | 95.1 | 94.4 | 94.8 | Power-One100PVI-CENTRAL-100-US [480V]
Power-One | PVI-CENTRAL-250-US [480V] | Y | N | N | 250 kW, 480 Vac Utility Interactive Inverter | 250 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 105.3 | 250 | 105.3 | 320 | 360 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 95.7 | 97.5 | 97.5 | 97.6 | 97 | 96.6 | 97.1 | 95.4 | 97.2 | 97.3 | 97.4 | 96.8 | 96.5 | 96.9 | 94.1 | 96 | 96.3 | 96.7 | 96.5 | 96 | 96.3 | Power-One250PVI-CENTRAL-250-US [480V]
Power-One | PVI-CENTRAL-300-US [480V] | Y | N | N | 300 kW, 480 Vac Utility Interactive Inverter | 300 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 119 | 300 | 119 | 320 | 360 | 480 | 30 | 60 | 90 | 150 | 225 | 300 | 96.2 | 97.5 | 97.6 | 97.6 | 97.1 | 96.5 | 97.2 | 95.8 | 97.3 | 97.4 | 97.4 | 96.9 | 96.4 | 97 | 94.8 | 96.2 | 96.3 | 96.6 | 96.3 | 95.8 | 96.3 | Power-One300PVI-CENTRAL-300-US [480V]
Power-One | ULTRA-750-TL-OUTD-2-US-690-x-y-z [690V] | Y | N | N | 750 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 750 | 690 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 301.7 |  |  | 585 | 746 | 800 | 75 | 150 | 225 | 375 | 562.5 | 750 | 94.5 | 95.8 | 96.2 | 96.2 | 95.9 | 95.1 | 95.9 | 95 | 96.5 | 96.7 | 96.9 | 96.5 | 95.9 | 96.5 | 95.1 | 96.6 | 96.9 | 97 | 96.7 | 96.1 | 96.7 | Power-One750ULTRA-750-TL-OUTD-2-US-690-x-y-z [690V]
Power-One | ULTRA-750-TL-OUTD-4-US-690-x-y-z [690V] | Y | N | N | 750 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 750 | 690 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 346.8 |  |  | 585 | 746 | 800 | 75 | 150 | 225 | 375 | 562.5 | 750 | 94.4 | 96 | 96.4 | 96.5 | 96.1 | 95.4 | 96.1 | 94.9 | 96.5 | 96.8 | 97.1 | 96.8 | 96.2 | 96.7 | 95 | 96.6 | 96.9 | 97.1 | 96.9 | 96.4 | 96.8 | Power-One750ULTRA-750-TL-OUTD-4-US-690-x-y-z [690V]
Power-One | ULTRA-750-TL-OUTD-1-US-690-x-y-z [690V] | Y | N | N | 750 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 780 | 690 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 302 |  |  | 585 | 746 | 800 | 78 | 156 | 234 | 390 | 585 | 780 | 94.4 | 95.8 | 96.1 | 96.2 | 95.8 | 95.1 | 95.8 | 94.9 | 96.4 | 96.7 | 96.9 | 96.5 | 96 | 96.5 | 95.1 | 96.6 | 96.9 | 97 | 96.7 | 96.2 | 96.7 | Power-One780ULTRA-750-TL-OUTD-1-US-690-x-y-z [690V]
Power-One | ULTRA-750-TL-OUTD-3-US-690-x-y-z [690V] | Y | N | N | 750 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 780 | 690 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 346.8 |  |  | 585 | 746 | 800 | 78 | 156 | 234 | 390 | 585 | 780 | 94.5 | 96 | 96.4 | 96.4 | 96 | 95.3 | 96.1 | 95 | 96.5 | 97 | 97.1 | 96.8 | 96.2 | 96.7 | 95.1 | 96.6 | 97.1 | 97.2 | 96.9 | 96.3 | 96.9 | Power-One780ULTRA-750-TL-OUTD-3-US-690-x-y-z [690V]
Power-One | ULTRA-1100-TL-OUTD-2-US-690-x-y-z [690V] | Y | N | N | 1100 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1000 | 690 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 328.8 |  |  | 585 | 746 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.5 | 96.1 | 96.5 | 96.5 | 96.2 | 95.4 | 96.2 | 94.9 | 96.7 | 97.1 | 97.1 | 96.8 | 96.2 | 96.8 | 95.1 | 96.9 | 97.2 | 97.3 | 96.9 | 96.4 | 96.9 | Power-One1000ULTRA-1100-TL-OUTD-2-US-690-x-y-z [690V]
Power-One | ULTRA-1100-TL-OUTD-4-US-690-x-y-z [690V] | Y | N | N | 1100 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1000 | 690 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 381.6 |  |  | 585 | 746 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.5 | 96.2 | 96.6 | 96.8 | 96.4 | 95.8 | 96.4 | 95 | 96.8 | 97.2 | 97.3 | 97 | 96.5 | 97 | 95.1 | 96.9 | 97.4 | 97.4 | 97.1 | 96.6 | 97.1 | Power-One1000ULTRA-1100-TL-OUTD-4-US-690-x-y-z [690V]
Power-One | ULTRA-1100-TL-OUTD-1-US-690-x-y-z [690V] | Y | N | N | 1100 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1154 | 690 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 329 |  |  | 585 | 746 | 800 | 117 | 234 | 351 | 585 | 877.5 | 1170 | 94.4 | 96 | 96.4 | 96.5 | 96.1 | 95.4 | 96.1 | 95 | 96.6 | 97 | 97.1 | 96.8 | 96.2 | 96.8 | 95.1 | 96.8 | 97.2 | 97.3 | 97 | 96.4 | 97 | Power-One1154ULTRA-1100-TL-OUTD-1-US-690-x-y-z [690V]
Power-One | ULTRA-1100-TL-OUTD-3-US-690-x-y-z [690V] | Y | N | N | 1100 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1170 | 690 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 381.6 |  |  | 585 | 746 | 800 | 117 | 234 | 351 | 585 | 877.5 | 1170 | 94.6 | 96.3 | 96.6 | 96.7 | 96.3 | 95.6 | 96.3 | 95.2 | 96.8 | 97.3 | 97.3 | 96.9 | 96.3 | 96.9 | 95.3 | 96.9 | 97.4 | 97.4 | 97 | 96.5 | 97 | Power-One1170ULTRA-1100-TL-OUTD-3-US-690-x-y-z [690V]
Power-One | ULTRA-1500-TL-OUTD-2-US-690-x-y-z [690V] | Y | N | N | 1500 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1500 | 690 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 373.9 |  |  | 585 | 746 | 800 | 150 | 300 | 450 | 750 | 1125 | 1500 | 94.9 | 96.3 | 96.5 | 96.7 | 96.3 | 95.6 | 96.3 | 95.3 | 96.8 | 97 | 97.2 | 96.9 | 96.3 | 96.9 | 95.4 | 96.9 | 97.2 | 97.4 | 97 | 96.5 | 97 | Power-One1500ULTRA-1500-TL-OUTD-2-US-690-x-y-z [690V]
Power-One | ULTRA-1500-TL-OUTD-4-US-690-x-y-z [690V] | Y | N | N | 1500 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1500 | 690 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 430.1 |  |  | 585 | 746 | 800 | 150 | 300 | 450 | 750 | 1125 | 1500 | 94.9 | 96.5 | 96.8 | 97 | 96.5 | 95.8 | 96.5 | 95.4 | 97 | 97.3 | 97.5 | 97.1 | 96.6 | 97.1 | 95.5 | 97.1 | 97.4 | 97.6 | 97.3 | 96.7 | 97.2 | Power-One1500ULTRA-1500-TL-OUTD-4-US-690-x-y-z [690V]
Power-One | ULTRA-1500-TL-OUTD-1-US-690-x-y-z [690V] | Y | N | N | 1500 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1550 | 690 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 374 |  |  | 585 | 746 | 800 | 156 | 312 | 468 | 780 | 1170 | 1560 | 94.9 | 96.3 | 96.5 | 96.8 | 96.2 | 95.4 | 96.2 | 95.3 | 96.8 | 97.1 | 97.2 | 96.9 | 96.3 | 96.9 | 95.5 | 97 | 97.2 | 97.4 | 97.1 | 96.5 | 97 | Power-One1550ULTRA-1500-TL-OUTD-1-US-690-x-y-z [690V]
Power-One | ULTRA-1500-TL-OUTD-3-US-690-x-y-z [690V] | Y | N | N | 1500 kW, 690 Vac Utility Interactive Inverter with Medium Voltage NEMA TP1 transformer | 1560 | 690 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Multiple Listing of ABB | 430.1 |  |  | 585 | 746 | 800 | 156 | 312 | 468 | 780 | 1170 | 1560 | 94.9 | 96.5 | 96.8 | 97 | 96.4 | 95.7 | 96.5 | 95.4 | 97 | 97.3 | 97.5 | 97.1 | 96.6 | 97.1 | 95.5 | 97.1 | 97.4 | 97.6 | 97.2 | 96.7 | 97.2 | Power-One1560ULTRA-1500-TL-OUTD-3-US-690-x-y-z [690V]
Princeton Power Systems | GTIB-208-30WYYYYYY [208V] | Y | N | N | 30 kW, 208 Vac, 780 Vdc max, 3-phase Utility Interactive Inverter with transformer, where Y= -ATS, -GA, -F, - GN-H, -H, -EMOS, or (blank) W, – Integrated transformer that provides AC/DC isolation. | 30 | 208 | 93 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 98.9 |  |  | 280 | 650 | 780 | 3 | 6 | 9 | 15 | 22.5 | 30 | 83.2 | 89.7 | 91.7 | 92.5 | 92.1 | 91.3 | 91.6 | 88.4 | 91.9 | 93.2 | 93.6 | 93.1 | 93.3 | 93 | 89 | 92.3 | 93.6 | 94.2 | 93.9 | 93.3 | 93.6 | Princeton Power Systems30GTIB-208-30WYYYYYY [208V] | 2017-06
Princeton Power Systems | GTIB30-480BGNSC [480V] | Y | N | N | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter | 30 | 480 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 64.2 |  |  | 280 | 443 | 580 | 3 | 6 | 9 | 15 | 22.5 | 30 | 80.1 | 88.6 | 91.3 | 92.5 | 92.4 | 91.7 | 91.6 | 80.1 | 88.7 | 91.6 | 93.4 | 93.6 | 93.3 | 92.5 | 83 | 90.7 | 93.6 | 94.1 | 94.2 | 94 | 93.5 | Princeton Power Systems30GTIB30-480BGNSC [480V]
Princeton Power Systems | GTIB-480-30-WZZZZZZ [480V] | Y | N | N | 30 kW, 480 Vac, 780 Vdc max, 3-phase Utility Interactive Inverter without transformer, where Z = -W, -ATS, -GA, -F, -GN-W-H, -H, -EMOS, or (blank) | 30 | 480 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 98.9 |  |  | 280 | 650 | 780 | 3 | 6 | 9 | 15 | 22.5 | 30 | 82.4 | 89.1 | 91.3 | 92.2 | 91.7 | 90.9 | 91.2 | 88.2 | 91.6 | 92.7 | 93.6 | 93.3 | 92.9 | 93 | 88.6 | 92.6 | 93.6 | 94 | 93.7 | 93 | 93.5 | Princeton Power Systems30GTIB-480-30-WZZZZZZ [480V] | 2017-06
Princeton Power Systems | GTIB-480-30-ZZZZZZZ [480V] | Y | N | N | 30 kW, 480 Vac, 780 V dc max, 3-phase Utility Interactive Inverter without transformer, where Z = -ATS, -GA, -F, -GN-H, -H, -EMOS, or (blank) | 30 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 98.9 |  |  | 280 | 650 | 780 | 3 | 6 | 9 | 15 | 22.5 | 30 | 86.1 | 90.9 | 93.6 | 94.7 | 95.3 | 95.3 | 94.4 | 91.3 | 94.2 | 95.3 | 96.2 | 96.6 | 96.6 | 96 | 91.4 | 94.6 | 95.6 | 96.6 | 97 | 97.1 | 96.4 | Princeton Power Systems30GTIB-480-30-ZZZZZZZ [480V] | 2017-06
Princeton Power Systems | GTIB-480-100-xxxx [480V] [480Vdc] | Y | N | N | 100 kW, 480 Vac, 480 Vdc max Utility Interactive Inverter | 100 | 480 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 170 |  |  | 330 | 400 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 87.42 | 92.23 | 93.54 | 94.53 | 94.49 | 93.87 | 93.96 | 87.74 | 92.55 | 93.79 | 94.76 | 94.76 | 94.43 | 94.24 | 88.37 | 93.27 | 94.56 | 95.46 | 95.59 | 95.07 | 95.01 | Princeton Power Systems100GTIB-480-100-xxxx [480V] [480Vdc]
Princeton Power Systems | GTIB-480-100-xxxx [480V] [600Vdc] | Y | N | N | 100 kW, 480 Vac, 600 Vdc Utility Interactive Inverter | 100 | 480 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 170 |  |  | 330 | 480 | 600 | 10 | 20 | 30 | 50 | 75 | 100 | 87.42 | 92.23 | 93.54 | 94.53 | 94.49 | 93.87 | 93.96 | 88.37 | 93.27 | 94.56 | 95.46 | 95.59 | 95.07 | 95.01 | 89.35 | 93.63 | 94.97 | 95.74 | 95.84 | 95.4 | 95.32 | Princeton Power Systems100GTIB-480-100-xxxx [480V] [600Vdc]
Princeton Power Systems | GTIB-480-100X-YYYYYYYY-Z-G1.2 [480V] | Y | N | N | 100 kW, 480 Vac, 800 Vdc, 3-phase, Utility Interactive Inverter with Princeton Power Systems transformer | 100 | 480 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 69.52 |  |  | 280 | 670 | 800 | 10 | 20 | 30 | 50 | 75 | 100 | 86.9 | 91.9 | 93.3 | 93.9 | 93.5 | 93 | 93.2 | 88.2 | 92.8 | 94.4 | 95.3 | 95.3 | 94.9 | 94.7 | 89.5 | 94 | 95.1 | 95.7 | 95.6 | 95.3 | 95.2 | Princeton Power Systems100GTIB-480-100X-YYYYYYYY-Z-G1.2 [480V]
Princeton Power Systems | GTIB-480-125-XXXXXX-W-G1.3 [480V] | Y | N | N | 125 kW, 480 Vac, 800 Vdc max, 3-phase Utility Interactive Inverter with transformer, where X = B, D, DH, GN, M, OV, V or blank B=Battery Temperature sensor D=Microgrid Option (dark start option)-254-780 Vdc (cannot be used with DH option) DH= Microgrid Option (dark start option)-450-800 Vdc (cannot be used with D option) GN= Ground Fault Detector/interrupter module installed, negatively grounded (cannot be used when position Y is blank) M= Integrated Revenue Meter with Modbus over TCP/IP OV=DC port overvoltage relay V=Low voltage option DC36-800V (Cannot be used with D or DH option) Position Y=X,W, or blank | 125 | 480 | 94 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 99.7 |  |  | 280 | 670 | 800 | 12.5 | 25 | 37.5 | 62.5 | 93.8 | 125 | 85.8 | 91.3 | 92.8 | 93.8 | 94 | 93.8 | 93.3 | 86.5 | 92.2 | 93.6 | 94.8 | 94.9 | 94.8 | 94.2 | 86.7 | 92.5 | 94 | 97 | 95.2 | 95.2 | 94.6 | Princeton Power Systems125GTIB-480-125-XXXXXX-W-G1.3 [480V] | 2017-06
Princeton Power Systems | GTIB-480-125-XXXXXX-Y-G1.3 [480V] | Y | N | N | 125 kW, 480 Vac, 800 Vdc max, 3-phase Utility Interactive Inverter without transformer, where X=B, D, DH, GN, M, OV, V or (blank) B=Battery Temperature sensor D=Microgrid Option (dark start option)-254-780 Vdc (cannot be used with DH option) DH= Microgrid Option (dark start option)-450-800 Vdc (cannot be used with D option) GN= Ground Fault Detector/interrupter module installed, negatively grounded (cannot be used when position Y is blank) M= Integrated Revenue Meter with Modbus over TCP/IP OV=DC port overvoltage relay V=Low voltage option DC36-800V (cannot be used with D or DH option) Y=X,W, or blank | 125 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 99.7 |  |  | 354 | 670 | 800 | 12.5 | 25 | 37.5 | 62.5 | 93.8 | 125 | 91 | 94.1 | 95.2 | 95.6 | 95.7 | 95.5 | 95.3 | 91.5 | 94.9 | 95.9 | 96.5 | 96.7 | 96.6 | 96.3 | 92.3 | 95.6 | 96.4 | 96.9 | 97 | 96.9 | 96.6 | Princeton Power Systems125GTIB-480-125-XXXXXX-Y-G1.3 [480V] | 2017-06
Princeton Power Systems | BIGI-250-X48GNMNR [480V] | Y | N | N | 250 kW, 2-input, 480V 3-phase Inverter | 250 | 480 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 138 |  |  | 417 | 490 | 580 | 25 | 50 | 75 | 125 | 187.5 | 250 | 87.2 | 92.4 | 94 | 94.8 | 94.7 | 94.3 | 94.2 | 87.6 | 92.7 | 94.2 | 95 | 94.9 | 94.6 | 94.4 | 88 | 92.9 | 94.4 | 95.3 | 95.2 | 94.7 | 94.7 | Princeton Power Systems250BIGI-250-X48GNMNR [480V]
Princeton Power Systems | BIGI-250-X48GNNR [480V] | Y | N | N | 250 kW, 2-input, 480V 3-phase Inverter | 250 | 480 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 138 |  |  | 417 | 490 | 580 | 25 | 50 | 75 | 125 | 187.5 | 250 | 87.2 | 92.4 | 94 | 94.8 | 94.7 | 94.3 | 94.2 | 87.6 | 92.7 | 94.2 | 95 | 94.9 | 94.6 | 94.4 | 88 | 92.9 | 94.4 | 95.3 | 95.2 | 94.7 | 94.7 | Princeton Power Systems250BIGI-250-X48GNNR [480V]
PV Powered | PVP1100 | Y | N | N | 1100 W Utility Interactive Inverter | 1.1 |  | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 207.5 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 80.8 | 89 | 91.1 | 92.7 | 93.3 | 93.3 | 92.2 | 78.9 | 87.9 | 90.4 | 92.3 | 92.9 | 93.1 | 91.7 | 73.5 | 84.8 | 88.1 | 90.7 | 91.7 | 92 | 90 | PV Powered1.1PVP1100
PV Powered | PVP1100EVR [120V] | Y | N | N | 1100 W, 120 Vac Utility Interactive Inverter with extended voltage range | 1.1 | 120 | 90.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 182 | 380 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 81.8 | 89 | 90.9 | 92.1 | 92.4 | 92.5 | 91.6 | 79.9 | 88 | 90.1 | 91.7 | 92.2 | 92.3 | 91.1 | 74.8 | 84.7 | 87.8 | 90 | 90.8 | 91.1 | 89.3 | PV Powered1.1PVP1100EVR [120V]
PV Powered | PVP2000 [120V] | Y | N | N | 2000 W, 120 Vac Utility Interactive Inverter | 2 | 120 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 207.5 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 85.7 | 91.4 | 92.8 | 93.7 | 93.9 | 93.7 | 93.3 | 84.5 | 90.8 | 92.4 | 93.5 | 93.6 | 93.5 | 92.9 | 81.1 | 88.8 | 90.9 | 92.3 | 92.7 | 92.6 | 91.7 | PV Powered2PVP2000 [120V]
PV Powered | PVP2000EVR [240V] | Y | N | N | 2000 W, 240 Vac Utility Interactive Inverter with extended voltage range | 2 | 240 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.6 |  |  | 100 | 199 | 380 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 87.3 | 91.7 | 92.6 | 93.5 | 93.2 | 93 | 92.9 | 85.7 | 90.8 | 92.1 | 92.9 | 92.9 | 92.6 | 92.4 | 82.4 | 88.8 | 90.5 | 91.6 | 91.8 | 91.6 | 91.1 | PV Powered2PVP2000EVR [240V]
PV Powered | PVP2500 [240V] | Y | N | N | 2500 W, 240 Vac Utility Interactive Inverter | 2.5 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2 | PV Powered2.5PVP2500 [240V]
PV Powered | PVP2800-208 [208V] | Y | N | N | 2800 W, 208 Vac Utility Interactive Inverter | 2.8 | 208 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.85 |  |  | 100 | 230 | 380 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 81.5 | 89.7 | 91.6 | 92.9 | 93.1 | 93 | 92.2 | 80.8 | 89.3 | 91.3 | 92.7 | 92.9 | 92.8 | 92 | 78.3 | 87.9 | 90.2 | 91.9 | 92.2 | 92.1 | 91.1 | PV Powered2.8PVP2800-208 [208V]
PV Powered | PVP3000 [240V] | Y | N | N | 3000 W, 240 Vac Utility Interactive Inverter | 3 | 240 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.63 |  |  | 100 | 222.5 | 380 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 88.9 | 92.9 | 93.8 | 94.3 | 94.2 | 93.9 | 93.9 | 87.9 | 92.5 | 93.5 | 94.1 | 94 | 93.8 | 93.7 | 84.9 | 90.9 | 92.4 | 93.3 | 93.2 | 93 | 92.7 | PV Powered3PVP3000 [240V]
PV Powered | PVP3500 [240V] | Y | N | N | 3500 W, 240 Vac Utility Interactive Inverter | 3.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.86 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5 | PV Powered3.5PVP3500 [240V]
PV Powered | PVP4600 [240V] | Y | N | N | 4600 W, 240 Vac Utility Interactive Inverter | 4.6 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 | 4.6 | 4 | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95 | PV Powered4.6PVP4600 [240V]
PV Powered | PVP4800 [240V] | Y | N | N | 4800 W, 240 Vac Utility Interactive Inverter | 4.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4.1 |  |  | 100 | 263 | 400 | 0.48 | 0.96 | 1.44 | 2.4 | 3.6 | 4.8 | 86.8 | 93.5 | 95.5 | 97 | 97.2 | 97.1 | 96.4 | 85.5 | 92.9 | 95 | 96.7 | 96.9 | 96.8 | 96 | 84.5 | 91.5 | 93.9 | 95.9 | 96.2 | 96.1 | 95.1 | PV Powered4.8PVP4800 [240V]
PV Powered | PVP5200 [240V] | Y | N | N | 5200 W, 240 Vac Utility Interactive Inverter | 5.2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 | 5.2 | 4 | 100 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5 | PV Powered5.2PVP5200 [240V]
PV Powered | PVP30KW-208 [208V] | Y | N | N | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter with 330-600 Vdc input | 30 | 208 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 17 | 30 | 17 | 330 | 368 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 89.8 | 93.6 | 94.5 | 94.7 | 94.6 | 94.1 | 94.4 | 89.4 | 93.2 | 94.3 | 94.5 | 94.4 | 94 | 94.2 | 87.6 | 92.4 | 93.5 | 94 | 93.9 | 93.5 | 93.5 | PV Powered30PVP30KW-208 [208V]
PV Powered | PVP30KW-480 [480V] | Y | N | N | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter with 330-600 Vdc input | 30 | 480 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 16 | 30 | 16 | 330 | 368 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 90.6 | 94 | 94.8 | 95.1 | 94.9 | 94.3 | 94.7 | 90 | 93.6 | 94.4 | 94.9 | 94.6 | 94.1 | 94.4 | 88.4 | 92.4 | 93.5 | 94.3 | 94 | 93.5 | 93.7 | PV Powered30PVP30KW-480 [480V]
PV Powered | PVP30KW-LV-208 [208V] | Y | N | N | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 30 | 208 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 22 |  |  | 295 | 341 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 89.4 | 93 | 94.1 | 94.4 | 94.1 | 93.8 | 93.9 | 88.2 | 92.5 | 93.5 | 94.1 | 93.8 | 93.5 | 93.5 | 83.6 | 89.7 | 91.2 | 92.4 | 92.4 | 92.2 | 91.8 | PV Powered30PVP30KW-LV-208 [208V]
PV Powered | PVP30KW-LV-480 [480V] | Y | N | N | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 30 | 480 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 22 |  |  | 295 | 341 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 89.9 | 93.7 | 94.5 | 94.9 | 94.7 | 94.1 | 94.5 | 88.7 | 93 | 93.9 | 94.5 | 94.3 | 93.8 | 94 | 84.1 | 90.1 | 91.8 | 92.9 | 92.8 | 92.6 | 92.2 | PV Powered30PVP30KW-LV-480 [480V]
PV Powered | PVP35 kW-208 [208V] | Y | N | N | 35 kW, 208 Vac, 3-phase Utility Interactive Inverter | 35 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 38.63 |  |  | 295 | 341 | 480 | 3.5 | 7 | 10.5 | 17.5 | 26.25 | 35 | 93.3 | 95.6 | 96.2 | 96.2 | 95.8 | 95.3 | 95.8 | 92.6 | 95.3 | 95.9 | 95.9 | 95.6 | 95.1 | 95.5 | 90.5 | 94.1 | 94.9 | 95.1 | 94.9 | 94.5 | 94.7 | PV Powered35PVP35 kW-208 [208V]
PV Powered | PVP35 kW-480 [480V] | Y | N | N | 35 kW, 480 Vac, 3-phase Utility Interactive Inverter | 35 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 37.79 |  |  | 295 | 341 | 480 | 3.5 | 7 | 10.5 | 17.5 | 26.25 | 35 | 94.1 | 96.4 | 96.9 | 97 | 96.8 | 96.3 | 96.7 | 93.3 | 95.9 | 96.5 | 96.7 | 96.5 | 96 | 96.4 | 91.1 | 94.7 | 95.4 | 95.7 | 95.6 | 95.2 | 95.3 | PV Powered35PVP35 kW-480 [480V]
PV Powered | PVP35 kW-600 [600V] | Y | N | N | 35 kW, 600 Vac, 3-phase Utility Interactive Inverter | 35 | 600 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 37.27 |  |  | 295 | 341 | 480 | 3.5 | 7 | 10.5 | 17.5 | 26.25 | 35 | 93.6 | 95.9 | 96.3 | 96.4 | 96.1 | 95.7 | 96.1 | 93 | 95.5 | 96 | 96.1 | 96 | 95.6 | 95.8 | 91 | 94.5 | 95.1 | 95.4 | 95.3 | 95 | 95.1 | PV Powered35PVP35 kW-600 [600V]
PV Powered | PVP50KW-208 [208V] | Y | N | N | 50 kW, 208 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 50 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 33 |  |  | 295 | 341 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95 | 96.7 | 96.6 | 96.6 | 96 | 95.3 | 96.2 | 94.4 | 96.3 | 96.3 | 96.3 | 95.8 | 95.2 | 95.9 | 92.7 | 95.5 | 95.4 | 95.6 | 95.2 | 94.7 | 95.2 | PV Powered50PVP50KW-208 [208V]
PV Powered | PVP50KW-480 [480V] | Y | N | N | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 50 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 33 |  |  | 295 | 341 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95.7 | 96.8 | 97.2 | 97 | 96.4 | 95.9 | 96.6 | 95.2 | 96.5 | 97 | 96.8 | 96.2 | 95.8 | 96.4 | 93.8 | 95.6 | 96.3 | 96 | 95.6 | 95.3 | 95.7 | PV Powered50PVP50KW-480 [480V]
PV Powered | PVP50KW-600 [600V] | Y | N | N | 50 kW, 600 Vac, 3-phase Utility Interactive Inverter | 50 | 600 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 43 |  |  | 295 | 341 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 94.2 | 96.2 | 96.6 | 96.6 | 96.2 | 95.7 | 96.2 | 93.6 | 95.9 | 96.3 | 96.3 | 96 | 95.6 | 95.9 | 91.6 | 94.8 | 95.4 | 95.5 | 95.3 | 95 | 95.1 | PV Powered50PVP50KW-600 [600V]
PV Powered | PVP75KW-208 [208V] | Y | N | N | 75 kW, 208 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 75 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 50 |  |  | 295 | 341 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.7 | 95.6 | 96.1 | 96 | 95.9 | 95.6 | 95.8 | 92 | 95.2 | 95.8 | 95.8 | 95.7 | 95.3 | 95.5 | 89.8 | 93.8 | 94.8 | 94.9 | 95 | 94.6 | 94.6 | PV Powered75PVP75KW-208 [208V]
PV Powered | PVP75KW-480 [480V] | Y | N | N | 75 kW, 480 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 75 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 50 |  |  | 295 | 341 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.7 | 95.6 | 96.2 | 96.6 | 96.4 | 96.1 | 96.2 | 91.9 | 95 | 95.6 | 96.3 | 96.1 | 95.8 | 95.9 | 89.2 | 93.3 | 94.1 | 95.2 | 95.1 | 95 | 94.6 | PV Powered75PVP75KW-480 [480V]
PV Powered | PVP75KW-600 [600V] | Y | N | N | 75 kW, 600 Vac, 3-phase Utility Interactive Inverter | 75 | 600 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 105.8 |  |  | 295 | 341 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.3 | 95.5 | 96.2 | 96.5 | 96.5 | 96.2 | 96.24 | 91.5 | 95.1 | 95.9 | 96.3 | 96.3 | 96.1 | 96 | 89.4 | 93.9 | 95 | 95.5 | 95.7 | 95.6 | 95.26 | PV Powered75PVP75KW-600 [600V]
PV Powered | PVP100 kW-208 [208V] | Y | N | N | 100 kW, 208 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 100 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 42 |  |  | 295 | 341 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 94.2 | 96.4 | 96.3 | 96.3 | 95.8 | 95.2 | 95.9 | 93.6 | 96 | 96.1 | 96.1 | 95.7 | 95.1 | 95.7 | 91.7 | 95 | 95.2 | 95.3 | 95.1 | 94.6 | 95 | PV Powered100PVP100 kW-208 [208V]
PV Powered | PVP100 kW-480 [480V] | Y | N | N | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 100 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 36 |  |  | 295 | 341 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 94.4 | 96.6 | 97.1 | 97 | 96.2 | 95.8 | 96.4 | 93.7 | 96.2 | 96.8 | 96.7 | 96 | 95.6 | 96.1 | 91.9 | 95 | 95.9 | 96 | 95.2 | 94.9 | 95.3 | PV Powered100PVP100 kW-480 [480V]
PV Powered | PVP100KW-600 [600V] | Y | N | N | 100 kW, 600 Vac, 3-phase Utility Interactive Inverter | 100 | 600 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 99.56 |  |  | 295 | 341 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 93.8 | 96.1 | 96.5 | 96.6 | 96.3 | 95.9 | 96.3 | 93.2 | 95.8 | 96.3 | 96.4 | 96.1 | 95.8 | 96.1 | 91.5 | 94.8 | 95.5 | 95.8 | 95.6 | 95.2 | 95.4 | PV Powered100PVP100KW-600 [600V]
PV Powered | PVP250KW-480 [480V] | Y | N | N | 250 kW, 480 Vac, 3-phase Utility Interactive Inverter | 249.5 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 54.14 |  |  | 295 | 341 | 480 | 24.95 | 49.9 | 74.85 | 124.8 | 187.1 | 249.5 | 96 | 97 | 96.9 | 96.9 | 96.6 | 96.1 | 96.7 | 95.6 | 96.6 | 96.7 | 96.8 | 96.4 | 96 | 96.5 | 94.7 | 95.8 | 96.2 | 96.2 | 95.9 | 95.4 | 95.9 | PV Powered249.5PVP250KW-480 [480V]
PV Powered | PVP250KW-600 [600V] | Y | N | N | 250 kW, 600 Vac, 3-phase Utility Interactive Inverter | 249.5 | 600 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 101 |  |  | 295 | 341 | 480 | 24.95 | 49.9 | 74.85 | 124.8 | 187.1 | 249.5 | 95.2 | 96.8 | 97.1 | 97.1 | 96.8 | 96.4 | 96.8 | 94.8 | 96.5 | 96.8 | 96.9 | 96.6 | 96.3 | 96.6 | 93.4 | 95.6 | 96.1 | 96.2 | 96 | 95.7 | 95.9 | PV Powered249.5PVP250KW-600 [600V]
PV Powered | PVP260KW [480V] | Y | N | N | 260 kW, 480 Vac, 3-phase Utility Interactive Inverter with 295-600 Vdc input | 260 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 67 |  |  | 295 | 341 | 480 | 26 | 52 | 78 | 130 | 195 | 260 | 96 | 97.5 | 97.7 | 97.6 | 97.1 | 96.4 | 97.2 | 95.6 | 97.3 | 97.5 | 97.4 | 97 | 96.4 | 97 | 94.4 | 96.5 | 96.9 | 97 | 96.6 | 96.1 | 96.6 | PV Powered260PVP260KW [480V]
PV Powered | PVP260KW-LV [480V] | Y | N | N | 260 kW, 480 Vac, 3-phase Utility Interactive Inverter with 265-600 Vdc input | 260 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 67 |  |  | 265 | 319 | 480 | 26 | 52 | 78 | 130 | 195 | 260 | 96.1 | 97.6 | 97.8 | 97.5 | 96.9 | 96 | 97.1 | 95.6 | 97.3 | 97.5 | 97.3 | 96.7 | 95.9 | 96.9 | 94 | 96.2 | 96.7 | 96.8 | 96.2 | 95.5 | 96.3 | PV Powered260PVP260KW-LV [480V]
REFU Elektronik | REFUsol 24K-UL [480V] | Y | N | N | 24 kW, 480 Vac, 1000 Vdc, 3-phase String Inverter | 24 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.3 |  |  | 570 | 730 | 890 | 2.34 | 4.67 | 7.01 | 11.69 | 17.53 | 23.37 | 97.4 | 97.9 | 98 | 97.9 | 97.7 | 97.6 | 97.8 | 97.5 | 98 | 98.1 | 98.2 | 98.2 | 98.1 | 98.1 | 96.9 | 97.6 | 97.8 | 98 | 97.9 | 97.9 | 97.8 | REFU Elektronik24REFUsol 24K-UL [480V] | 2017-04 | 2017-05-31
REFU Elektronik | REFUsol 24K-UL-AFCI [480V] | Y | N | N | 24 kW, 480 Vac, 1000 Vdc, 3-phase String Inverter | 24 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.3 |  |  | 570 | 730 | 890 | 2.34 | 4.67 | 7.01 | 11.69 | 17.53 | 23.37 | 97.3 | 97.8 | 97.9 | 97.9 | 97.7 | 97.6 | 97.8 | 97.4 | 98 | 98.1 | 98.2 | 98.2 | 98.1 | 98.1 | 96.8 | 97.5 | 97.7 | 98 | 97.8 | 97.8 | 97.8 | REFU Elektronik24REFUsol 24K-UL-AFCI [480V] | 2017-04 | 2017-05-31
REFU Elektronik | REFUsol 48K-UL [480V] | Y | N | N | 48 kW, 480 Vac, 1000 Vdc, 3-phase String Inverter | 47.888 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.9 |  |  | 580 | 720 | 850 | 4.79 | 9.58 | 14.37 | 23.94 | 35.92 | 47.89 | 97.1 | 98.1 | 98.2 | 98.2 | 98.2 | 98 | 98.1 | 97.1 | 98.2 | 98.3 | 98.3 | 98.2 | 98.1 | 98.2 | 96.7 | 97.8 | 98 | 98.1 | 98 | 97.9 | 97.9 | REFU Elektronik47.888REFUsol 48K-UL [480V] | 2017-04
REFU Elektronik | REFUsol 48K-UL-AFCI [480V] | Y | N | N | 48 kW, 480 Vac, 1000 Vdc, 3-phase String Inverter | 47.888 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.9 |  |  | 580 | 720 | 850 | 4.79 | 9.58 | 14.37 | 23.94 | 35.92 | 47.89 | 96.7 | 98 | 98.1 | 98.1 | 98.1 | 97.9 | 98 | 96.9 | 98 | 98.2 | 98.3 | 98.3 | 98.1 | 98.2 | 96.9 | 97.9 | 98 | 98.1 | 97.9 | 97.6 | 97.9 | REFU Elektronik47.888REFUsol 48K-UL-AFCI [480V] | 2017-04
Refusol | 804R012 [480V] | Y | N | N | 12 kW, 480 Vac, 3-phase Utility Interactive Inverter | 12.12 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.87 |  |  | 450 | 720 | 900 | 1.212 | 2.424 | 3.636 | 6.06 | 9.09 | 12.12 | 94.93 | 96.05 | 96.86 | 97.37 | 97.46 | 97.3 | 97.19 | 95.96 | 96.52 | 97.44 | 97.9 | 98.05 | 98.07 | 97.79 | 95.21 | 95.89 | 96.76 | 97.44 | 97.63 | 97.74 | 97.31 | Refusol12.12804R012 [480V]
Refusol | 804R016 [480V] | Y | N | N | 16 kW, 480 Vac, 3-phase Utility Interactive Inverter | 16.1 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.087 |  |  | 500 | 720 | 900 | 1.61 | 3.22 | 4.83 | 8.05 | 12.08 | 16.1 | 95.95 | 96.84 | 97.38 | 97.62 | 97.59 | 97.41 | 97.46 | 96.59 | 97.26 | 97.74 | 98.02 | 98.07 | 97.97 | 97.91 | 95.93 | 96.54 | 97.19 | 97.63 | 97.73 | 97.72 | 97.51 | Refusol16.1804R016 [480V]
Refusol | 804R020 [480V] | Y | N | N | 20 kW, 480 Vac, 3-phase Utility Interactive Inverter | 19.65 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.09 |  |  | 550 | 720 | 900 | 1.97 | 3.93 | 5.9 | 9.83 | 14.74 | 19.65 | 96.5 | 97.3 | 97.7 | 97.8 | 97.7 | 97.5 | 97.6 | 96.7 | 97.5 | 97.9 | 98.1 | 98.1 | 98 | 98 | 96 | 96.6 | 97.2 | 97.6 | 97.6 | 97.5 | 97.4 | Refusol19.65804R020 [480V]
Refusol | 804R024 [480V] | Y | N | N | 22.2 kW, 480 Vac, 3-phase Utility Interactive Inverter | 22.23 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.49 |  |  | 600 | 720 | 900 | 2.223 | 4.446 | 6.669 | 11.12 | 16.67 | 22.23 | 97.17 | 97.69 | 97.93 | 97.92 | 97.81 | 97.57 | 97.8 | 97.25 | 97.73 | 98.01 | 98.1 | 97.99 | 97.81 | 97.96 | 96.69 | 97.05 | 97.49 | 97.7 | 97.62 | 97.48 | 97.55 | Refusol22.23804R024 [480V]
Renergy | RS-1500 [208V] | Y | N | N | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.46 | 90.49 | 92.52 | 94.25 | 94.92 | 95.02 | 93.86 | 85.04 | 91.04 | 93.19 | 94.79 | 95.41 | 95.53 | 94.38 | 85.31 | 91.19 | 93.54 | 95.02 | 95.55 | 95.76 | 94.58 | Renergy1.55RS-1500 [208V]
Renergy | RS-1500 [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.62 | 90.46 | 92.57 | 94.42 | 95.07 | 95.25 | 93.99 | 84.89 | 90.97 | 93.04 | 94.81 | 95.51 | 95.73 | 94.42 | 85.22 | 91.38 | 93.44 | 95.12 | 95.65 | 95.93 | 94.66 | Renergy1.55RS-1500 [240V]
Renergy | RS-2000 [208V] | Y | N | N | 2 kW, 208 Vac Utility Interactive Inverter | 2.06 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.29 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 88.28 | 93.12 | 94.41 | 95.27 | 95.43 | 95.37 | 94.87 | 89.63 | 93.68 | 94.91 | 95.73 | 95.84 | 95.8 | 95.34 | 89.74 | 94.01 | 95.11 | 96.13 | 96.38 | 96.07 | 95.77 | Renergy2.06RS-2000 [208V]
Renergy | RS-2000 [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter | 2.06 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 86.91 | 92.14 | 93.78 | 94.94 | 95.3 | 95.37 | 94.55 | 87.84 | 92.87 | 94.26 | 95.56 | 95.79 | 95.73 | 95.09 | 88.1 | 93.05 | 94.37 | 95.71 | 96 | 95.94 | 95.28 | Renergy2.06RS-2000 [240V]
Renergy | RS-3000 [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.57 | 94.41 | 95.16 | 95.47 | 95.31 | 94.62 | 95.1 | 92.05 | 94.92 | 95.58 | 95.89 | 95.76 | 95.37 | 95.56 | 92.22 | 95.17 | 95.79 | 96.25 | 95.93 | 95.8 | 95.78 | Renergy3RS-3000 [208V]
Renergy | RS-3000 [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.301 | 0.602 | 0.903 | 1.505 | 2.258 | 3.01 | 90 | 93.9 | 94.85 | 95.4 | 95.31 | 94.83 | 94.97 | 90.64 | 94.34 | 95.34 | 95.79 | 95.87 | 95.6 | 95.49 | 91 | 94.59 | 95.44 | 95.97 | 96.01 | 95.77 | 95.65 | Renergy3.01RS-3000 [240V]
Renergy | RS-4000 [208V] | Y | N | N | 4 kW, 208 Vac Utility Interactive Inverter | 3.98 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.398 | 0.796 | 1.194 | 1.99 | 2.985 | 3.98 | 90.53 | 94.32 | 95.17 | 95.44 | 95.41 | 95.16 | 95.13 | 91.58 | 94.87 | 95.63 | 96.05 | 96 | 95.45 | 95.7 | 91.82 | 95.03 | 95.8 | 96.45 | 96.31 | 95.76 | 96.01 | Renergy3.98RS-4000 [208V]
Renergy | RS-4000 [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.399 | 0.798 | 1.197 | 1.995 | 2.993 | 3.99 | 90.55 | 94.3 | 95.24 | 95.69 | 95.74 | 95.56 | 95.38 | 91.53 | 94.95 | 95.81 | 96.33 | 96.33 | 96.05 | 95.99 | 91.95 | 95.23 | 95.96 | 96.4 | 96.48 | 96.25 | 96.15 | Renergy3.99RS-4000 [240V]
Renergy | RS-5000 [240V] | Y | N | N | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8 | Renergy5.24RS-5000 [240V]
Renesola Zhejiang | Replus-250A [240V] | Y | N | N | 225 W, 240 Vac Utility Interactive Inverter | 0.22 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.17 |  |  | 22 | 28.5 | 44 | 0.02 | 0.04 | 0.07 | 0.11 | 0.16 | 0.22 | 89.6 | 95.5 | 95.3 | 95.7 | 95 | 94.1 | 94.9 | 90.8 | 95.2 | 94.8 | 95.5 | 95.4 | 95 | 95.2 | 85.8 | 91.5 | 93.5 | 94.4 | 95.1 | 95.5 | 94.2 | Renesola Zhejiang0.22Replus-250A [240V]
Renesola Zhejiang | Replus-250B [208V] | Y | N | N | 217 W, 208 Vac Utility Interactive Inverter | 0.23 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.17 |  |  | 22 | 28.5 | 44 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 90.1 | 94.5 | 94.9 | 95.1 | 95.9 | 95.4 | 95.3 | 89.7 | 93.9 | 95.2 | 95.1 | 96.2 | 96.2 | 95.5 | 85.2 | 91.4 | 93.7 | 92.5 | 95.2 | 96.3 | 93.9 | Renesola Zhejiang0.23Replus-250B [208V]
Renesola Zhejiang | Replus-300-208A | Y | N | N | Utility Interactive Inverter | 0.251 |  | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.06 |  |  | 22 | 29 | 38 | 0.025 | 0.05 | 0.075 | 0.125 | 0.188 | 0.251 | 93.3 | 94.8 | 96.1 | 95.2 | 95.5 | 95.3 | 95.4 | 94.1 | 95.7 | 96.2 | 95.6 | 95.7 | 95.6 | 95.7 | 94.2 | 96.1 | 95.9 | 95.8 | 95.5 | 96 | 95.6 | Renesola Zhejiang0.251Replus-300-208A
Renesola Zhejiang | Replus-300-240A | Y | N | N | Utility Interactive Inverter | 0.251 |  | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.08 |  |  | 22 | 29 | 38 | 0.025 | 0.05 | 0.075 | 0.125 | 0.188 | 0.251 | 92.2 | 94.1 | 94.9 | 95.2 | 96.1 | 95.7 | 95.5 | 92.9 | 94.7 | 94.5 | 95.7 | 96.1 | 96.3 | 95.7 | 92.7 | 94.6 | 93.2 | 95.7 | 95.4 | 96.4 | 95.1 | Renesola Zhejiang0.251Replus-300-240A
Renesola Zhejiang | MU300SAP3 [240V] | Y | N | N | 289 W, 240 Vac Utility Interactive Inverter | 0.29 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.1 |  |  | 26 | 31 | 43 | 0.03 | 0.06 | 0.09 | 0.14 | 0.22 | 0.29 | 92.1 | 94.4 | 95 | 95.7 | 96.3 | 95.9 | 95.7 | 91.6 | 95.1 | 94.8 | 96.5 | 96.5 | 96.5 | 96.1 | 89.9 | 94.3 | 95.3 | 96.3 | 96.2 | 96.2 | 95.8 | Renesola Zhejiang0.29MU300SAP3 [240V]
Renesola Zhejiang | Replus 3600MTLB-US [208V] | Y | N | N | 3600W, 208 Vac Utility Interactive Inverter | 3.6 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.23 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.9 | 94.6 | 95.5 | 96.4 | 96.5 | 96.3 | 96.1 | 94.5 | 96.7 | 97.3 | 97.6 | 97.4 | 97.2 | 97.3 | 93 | 96 | 96.9 | 97.3 | 97.3 | 97.1 | 97 | Renesola Zhejiang3.6Replus 3600MTLB-US [208V]
Renesola Zhejiang | Replus 3600MTLB-US [240V] | Y | N | N | 3600W, 240 Vac Utility Interactive Inverter | 3.6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.31 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.4 | 94.6 | 95.5 | 96.5 | 96.7 | 96.7 | 96.2 | 95.3 | 97.1 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | 94.2 | 96.5 | 97.1 | 97.5 | 97.6 | 97.4 | 97.3 | Renesola Zhejiang3.6Replus 3600MTLB-US [240V]
Renesola Zhejiang | Replus 3600MTLB-US [277V] | Y | N | N | 3600W, 277 Vac Utility Interactive Inverter | 3.6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.2 | 93.9 | 94.7 | 96.1 | 96.6 | 96.6 | 95.9 | 93.4 | 96 | 96.6 | 97.4 | 97.5 | 97.5 | 97.2 | 94.5 | 96.8 | 97.4 | 97.9 | 98 | 97.9 | 97.7 | Renesola Zhejiang3.6Replus 3600MTLB-US [277V]
Renesola Zhejiang | Replus 4200MTLB-US [208V] | Y | N | N | 4200W, 208 Vac Utility Interactive Inverter | 4.2 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.6 | 94.4 | 95.5 | 96.6 | 96.8 | 96.7 | 96.3 | 94.1 | 96.5 | 97.1 | 97.3 | 97.1 | 96.7 | 97 | 93.6 | 96.2 | 96.8 | 97.2 | 97.5 | 97.1 | 97.1 | Renesola Zhejiang4.2Replus 4200MTLB-US [208V]
Renesola Zhejiang | Replus 4200MTLB-US [240V] | Y | N | N | 4200W, 240 Vac Utility Interactive Inverter | 4.2 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.33 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 92.4 | 94.6 | 95.5 | 96.5 | 96.7 | 96.7 | 96.2 | 95.3 | 97.1 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | 94.2 | 96.5 | 97.1 | 97.5 | 97.6 | 97.4 | 97.3 | Renesola Zhejiang4.2Replus 4200MTLB-US [240V]
Renesola Zhejiang | Replus 4200MTLB-US [277V] | Y | N | N | 4200 W, 277 Vac Utility Interactive Inverter | 4.2 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.4 | 94.4 | 96 | 96.6 | 96.8 | 96.6 | 96.3 | 92.1 | 95.2 | 96.3 | 97.3 | 97.6 | 97.1 | 97 | 93.6 | 96.3 | 97.2 | 97.6 | 97.6 | 97.6 | 97.4 | Renesola Zhejiang4.2Replus 4200MTLB-US [277V]
Renesola Zhejiang | Replus 5000MTLB-US [208V] | Y | N | N | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.7 | 96.5 | 96.8 | 96.9 | 96.5 | 96 | 96.5 | 95.4 | 97 | 97.3 | 97.4 | 97 | 96.5 | 97 | 94.3 | 96.4 | 96.9 | 97.1 | 97 | 96.5 | 96.8 | Renesola Zhejiang4.6Replus 5000MTLB-US [208V]
Renesola Zhejiang | Replus 5000MTLB-US [240V] | Y | N | N | 4600 W, 240 Vac Utility Interactive Inverter | 4.6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.8 | 95.2 | 96 | 96.7 | 96.6 | 96.4 | 96.3 | 95.8 | 97.3 | 97.7 | 97.8 | 97.5 | 97.1 | 97.5 | 96.7 | 96.7 | 97.2 | 97.5 | 97.4 | 97.1 | 97.3 | Renesola Zhejiang4.6Replus 5000MTLB-US [240V]
Renesola Zhejiang | Replus 5000MTLB-US [277V] | Y | N | N | 4600 W, 277 Vac Utility Interactive Inverter | 4.6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.43 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.2 | 94.9 | 95.6 | 96.6 | 96.8 | 96.8 | 96.4 | 94.6 | 96.7 | 97.2 | 97.6 | 97.6 | 97.4 | 97.4 | 95.4 | 97.1 | 97.6 | 97.9 | 97.8 | 97.7 | 97.7 | Renesola Zhejiang4.6Replus 5000MTLB-US [277V]
Renesola Zhejiang | Replus 8000TLB-US [208V] | Y | N | N | 8000 W Utility Interactive Inverter | 8.07 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 345 | 480 | 0.81 | 1.61 | 2.42 | 4.03 | 6.05 | 8.07 | 95.6 | 96.7 | 97.1 | 97.2 | 97.1 | 96.9 | 97.1 | 94.9 | 96.3 | 96.8 | 97 | 96.9 | 96.8 | 96.8 | 92.6 | 95 | 95.8 | 96.4 | 96.4 | 96.2 | 96.1 | Renesola Zhejiang8.07Replus 8000TLB-US [208V]
Renesola Zhejiang | Replus 8000TLB-US [240V] | Y | N | N | 8000 W Utility Interactive Inverter | 8.08 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 100 | 380 | 480 | 0.81 | 1.62 | 2.42 | 4.04 | 6.06 | 8.08 | 95.4 | 96.7 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | 95.1 | 96.6 | 97 | 97.3 | 97.3 | 97.2 | 97.1 | 93.2 | 95.5 | 96.2 | 96.8 | 96.4 | 96.9 | 96.3 | Renesola Zhejiang8.08Replus 8000TLB-US [240V]
Renesola Zhejiang | Replus 9000TLB-US [208V] | Y | N | N | 9000 W Utility Interactive Inverter | 9.08 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 345 | 480 | 0.91 | 1.82 | 2.72 | 4.54 | 6.81 | 9.08 | 95.9 | 96.8 | 97.1 | 97.2 | 97 | 96.8 | 97 | 95.3 | 96.5 | 96.9 | 97 | 97 | 96.7 | 96.9 | 93.1 | 95.3 | 96 | 96.4 | 96.4 | 96.2 | 96.2 | Renesola Zhejiang9.08Replus 9000TLB-US [208V]
Renesola Zhejiang | Replus 9000TLB-US [240V] | Y | N | N | 9000 W Utility Interactive Inverter | 9.08 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 100 | 380 | 480 | 0.91 | 1.82 | 2.72 | 4.54 | 6.81 | 9.08 | 95.8 | 79.3 | 97.2 | 97.4 | 97.4 | 97.2 | 96.4 | 95.5 | 96.8 | 97.1 | 97.3 | 97.3 | 97.1 | 97.2 | 93.8 | 95.8 | 96.4 | 96.7 | 96.9 | 96.8 | 96.6 | Renesola Zhejiang9.08Replus 9000TLB-US [240V]
Renesola Zhejiang | Replus 10000TLB-US [208V] | Y | N | N | 10000 W Utility Interactive Inverter | 10.09 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 345 | 480 | 1.01 | 2.02 | 3.03 | 5.04 | 7.57 | 10.09 | 95.8 | 96.9 | 97.1 | 97.2 | 97 | 96.6 | 97 | 95.5 | 96.6 | 96.9 | 97 | 96.9 | 96.5 | 96.8 | 93.1 | 95.4 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | Renesola Zhejiang10.09Replus 10000TLB-US [208V]
Renesola Zhejiang | Replus 10000TLB-US [240V] | Y | N | N | 10000 W Utility Interactive Inverter | 10.09 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 100 | 380 | 480 | 1.01 | 2.02 | 3.03 | 5.04 | 7.56 | 10.09 | 96 | 97 | 97.3 | 97.4 | 97.3 | 97.1 | 97.2 | 95.8 | 96.9 | 97.2 | 97.4 | 97.3 | 97 | 97.2 | 94.3 | 96 | 96.5 | 96.9 | 96.8 | 96.7 | 96.7 | Renesola Zhejiang10.09Replus 10000TLB-US [240V]
Renesola Zhejiang | Replus 10000TL3B-US [277V] | Y | N | N | 10000 W, 277 Vac Utility Interactive Inverter | 10.1 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.01 |  |  | 100 | 420 | 480 | 1.01 | 2.02 | 3.03 | 5.05 | 7.58 | 10.1 | 89.5 | 93.1 | 94.1 | 94.9 | 95 | 95 | 94.6 | 90.1 | 93.9 | 95.2 | 96 | 96.3 | 96.4 | 95.7 | 89.9 | 94.2 | 95.4 | 96.3 | 96.7 | 96.8 | 96 | Renesola Zhejiang10.1Replus 10000TL3B-US [277V]
Renesola Zhejiang | Replus 12000TL3B-US [277V] | Y | N | N | 11620W, 277 Vac Utility Interactive Inverter | 11.62 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.01 |  |  | 250 | 420 | 480 | 1.16 | 2.32 | 3.49 | 5.81 | 8.72 | 11.62 | 89.8 | 93.4 | 94.4 | 95.2 | 94.9 | 95 | 94.6 | 90.2 | 94.2 | 95.3 | 96.2 | 96.4 | 96.5 | 95.9 | 91 | 94.6 | 95.6 | 96.4 | 96.6 | 96.7 | 96.1 | Renesola Zhejiang11.62Replus 12000TL3B-US [277V]
Renesola Zhejiang | Replus 11000TLB-US [240V] | Y | N | N | 11000 W Utility Interactive Inverter | 11.7 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 356 | 380 | 480 | 1.17 | 2.34 | 3.51 | 5.85 | 8.78 | 11.7 | 96 | 97 | 97.3 | 97.3 | 97.2 | 97 | 97.2 | 95.8 | 96.9 | 97.2 | 97.3 | 97.2 | 96.9 | 97.1 | 94.3 | 96 | 96.5 | 97 | 96.8 | 96.5 | 96.6 | Renesola Zhejiang11.7Replus 11000TLB-US [240V]
Renesola Zhejiang | Replus 18000TL3B-US [277V] | Y | N | N | 18306 W, 277 Vac Utility Interactive Inverter | 18.31 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.01 |  |  | 250 | 420 | 480 | 1.83 | 3.66 | 5.49 | 9.15 | 13.73 | 18.31 | 92.3 | 94.9 | 95.4 | 95.2 | 95.5 | 95.4 | 95.3 | 92.5 | 95.8 | 96.4 | 96.8 | 96.9 | 96.6 | 96.6 | 92.9 | 95.8 | 96.5 | 96.9 | 97.1 | 96.8 | 96.7 | Renesola Zhejiang18.31Replus 18000TL3B-US [277V]
Renesola Zhejiang | Replus 20000TL3B-US [277V] | Y | N | N | 20415 W, 277 Vac Utility Interactive Inverter | 20.42 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 250 | 420 | 480 | 2.04 | 4.08 | 6.12 | 10.21 | 15.31 | 20.42 | 92.7 | 95.1 | 95.5 | 95.6 | 95.7 | 95.7 | 95.5 | 93.1 | 96 | 96.5 | 96.8 | 96.8 | 96.8 | 96.6 | 93.5 | 96 | 96.6 | 97 | 97.1 | 97 | 96.8 | Renesola Zhejiang20.42Replus 20000TL3B-US [277V]
Renovo Power Systems | RN3000US | Y | N | N | 3 kW Digiwatts Grid-tie transformerless MPPT Inverter | 3 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 380 | 440 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93 | 95.5 | 96.2 | 96.3 | 95.9 | 95.1 | 95.8 | 94.4 | 96.5 | 97.1 | 97.2 | 97.2 | 96.9 | 97 | 93.5 | 96.1 | 96.9 | 97 | 97.1 | 96.9 | 96.8 | Renovo Power Systems3RN3000US
Renovo Power Systems | RN5000US | Y | N | N | 5 kW Digiwatts Grid-tie transformerless MPPT Inverter | 5 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.3 |  |  | 100 | 345 | 440 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 89.9 | 92.8 | 94.1 | 94.5 | 94.3 | 93.9 | 94.1 | 91.1 | 92.8 | 94.3 | 94.9 | 94.8 | 94.4 | 94.5 | 89.9 | 93.9 | 94.7 | 95.2 | 95.1 | 94.7 | 94.8 | Renovo Power Systems5RN5000US
Resonix | EVSK1750WG [208V] | Y | N | N | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.46 | 90.49 | 92.52 | 94.25 | 94.92 | 95.02 | 93.86 | 85.04 | 91.04 | 93.19 | 94.79 | 95.41 | 95.53 | 94.38 | 85.31 | 91.19 | 93.54 | 95.02 | 95.55 | 95.76 | 94.58 | Resonix1.55EVSK1750WG [208V]
Resonix | EVSK1750WG [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.62 | 90.46 | 92.57 | 94.42 | 95.07 | 95.25 | 93.99 | 84.89 | 90.97 | 93.04 | 94.81 | 95.51 | 95.73 | 94.42 | 85.22 | 91.38 | 93.44 | 95.12 | 95.65 | 95.93 | 94.66 | Resonix1.55EVSK1750WG [240V]
Resonix | EVSK2340WG [208V] | Y | N | N | 2 kW, 208 Vac Utility Interactive Inverter | 2.06 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.29 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 88.28 | 93.12 | 94.41 | 95.27 | 95.43 | 95.37 | 94.87 | 89.63 | 93.68 | 94.91 | 95.73 | 95.84 | 95.8 | 95.34 | 89.74 | 94.01 | 95.11 | 96.13 | 96.38 | 96.07 | 95.77 | Resonix2.06EVSK2340WG [208V]
Resonix | EVSK2340WG [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 2.06 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 86.91 | 92.14 | 93.78 | 94.94 | 95.3 | 95.37 | 94.55 | 87.84 | 92.87 | 94.26 | 95.56 | 95.79 | 95.73 | 95.09 | 88.1 | 93.05 | 94.37 | 95.71 | 96 | 95.94 | 95.28 | Resonix2.06EVSK2340WG [240V]
Resonix | EVSK3510WG [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.57 | 94.41 | 95.16 | 95.47 | 95.31 | 94.62 | 95.1 | 92.05 | 94.92 | 95.58 | 95.89 | 95.76 | 95.37 | 95.56 | 92.22 | 95.17 | 95.79 | 96.25 | 95.93 | 95.8 | 95.78 | Resonix3EVSK3510WG [208V]
Resonix | EVSK3510WG [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.301 | 0.602 | 0.903 | 1.505 | 2.258 | 3.01 | 90 | 93.9 | 94.85 | 95.4 | 95.31 | 94.83 | 94.97 | 90.64 | 94.34 | 95.34 | 95.79 | 95.87 | 95.6 | 95.49 | 91 | 94.59 | 95.44 | 95.97 | 96.01 | 95.77 | 95.65 | Resonix3.01EVSK3510WG [240V]
Resonix | EVSK4700WG [208V] | Y | N | N | 4 kW, 208 Vac Utility Interactive Inverter | 3.98 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.398 | 0.796 | 1.194 | 1.99 | 2.985 | 3.98 | 90.53 | 94.32 | 95.17 | 95.44 | 95.41 | 95.16 | 95.13 | 91.58 | 94.87 | 95.63 | 96.05 | 96 | 95.45 | 95.7 | 91.82 | 95.03 | 95.8 | 96.45 | 96.31 | 95.76 | 96.01 | Resonix3.98EVSK4700WG [208V]
Resonix | EVSK4700WG [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.399 | 0.798 | 1.197 | 1.995 | 2.993 | 3.99 | 90.55 | 94.3 | 95.24 | 95.69 | 95.74 | 95.56 | 95.38 | 91.53 | 94.95 | 95.81 | 96.33 | 96.33 | 96.05 | 95.99 | 91.95 | 95.23 | 95.96 | 96.4 | 96.48 | 96.25 | 96.15 | Resonix3.99EVSK4700WG [240V]
Rhombus Energy Solutions | BESI-50kW-480 [480V] | Y | Y | Y | 50kW, 480 Vac, transformer-less, 3-phase, Multi-Mode Grid Support Utility Interactive Energy Storage Inverter | 49.35 | 480 | 94 | [06/29/2018] | [00021618] | 2018-10-15 | N | N |  | 103 |  |  | 550 | 636 | 840 | 4.935 | 9.87 | 14.805 | 24.675 | 37.0125 | 49.35 | 76.5714 | 88 | 92 | 95.1429 | 96 | 96 | 94.1629 | 79 | 89 | 92 | 95 | 96 | 96 | 94.28 | 79 | 88.8571 | 92 | 94 | 96 | 96 | 94.0629 | Rhombus Energy Solutions49.35BESI-50kW-480 [480V] | 2018-08-15 | 2018-10-15
Rhombus Energy Solutions | BESS-50kW-480 [480V] | Y | Y | Y | 50kW, 480 Vac, transformer-less, 3-phase, Grid Support Utility Interactive Energy Storage Inverter | 49.35 | 480 | 94 | [06/29/2018] | [00021618] | 2018-10-15 | N | N |  | 103 |  |  | 550 | 636 | 840 | 4.935 | 9.87 | 14.805 | 24.675 | 37.0125 | 49.35 | 76.5714 | 88 | 92 | 95.1429 | 96 | 96 | 94.1629 | 79 | 89 | 92 | 95 | 96 | 96 | 94.28 | 79 | 88.8571 | 92 | 94 | 96 | 96 | 94.0629 | Rhombus Energy Solutions49.35BESS-50kW-480 [480V] | 2018-08-15 | 2018-10-15
Ritek | RTMU300SAP2 [240V] | Y | N | N | 289 W, 240 Vac Utility Interactive Inverter | 0.289 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.1 |  |  | 26 | 31 | 43 | 0.03 | 0.06 | 0.09 | 0.14 | 0.22 | 0.29 | 92.1 | 94.4 | 95 | 95.7 | 96.3 | 95.9 | 95.7 | 91.6 | 95.1 | 94.8 | 96.5 | 96.5 | 96.5 | 96.1 | 89.9 | 94.3 | 95.3 | 96.3 | 96.2 | 96.2 | 95.8 | Ritek0.289RTMU300SAP2 [240V]
Sainty Solar | SSI-2K2U [240V] | Y | N | N | 2110 W, 240 Vac Utility Interactive Inverter | 2.11 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.21 | 0.42 | 0.63 | 1.06 | 1.58 | 2.11 | 85.3 | 91.6 | 92.9 | 94.3 | 94.6 | 94.5 | 93.8 | 82.1 | 91.9 | 94.2 | 95.6 | 96.1 | 96.4 | 95 | 82.2 | 91.5 | 93.8 | 95.6 | 96.1 | 96.3 | 95 | Sainty Solar2.11SSI-2K2U [240V]
Sainty Solar | SSI-3K3U [240V] | Y | N | N | 3180 W, 240 Vac Utility Interactive Inverter | 3.18 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.32 | 0.64 | 0.95 | 1.59 | 2.39 | 3.18 | 88.8 | 92.9 | 94.1 | 94.6 | 94.3 | 94 | 94 | 88.8 | 94.4 | 95.3 | 96.2 | 96.3 | 95.9 | 95.7 | 89.5 | 93.7 | 95.3 | 96.2 | 96.3 | 96.1 | 95.7 | Sainty Solar3.18SSI-3K3U [240V]
Sainty Solar | SSI-4K4U [240V] | Y | N | N | 4100W, 240 Vac Utility Interactive Inverter | 4.16 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.42 | 0.83 | 1.25 | 2.08 | 3.12 | 4.16 | 90.6 | 93.8 | 94.5 | 94.8 | 94.6 | 94.2 | 94.4 | 91.4 | 95 | 95.7 | 96.1 | 96.2 | 95.9 | 95.9 | 90.7 | 94.7 | 95.5 | 96.1 | 96.1 | 95.9 | 95.7 | Sainty Solar4.16SSI-4K4U [240V]
Sainty Solar | SSI-5K5U [240V] | Y | N | N | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8 | Sainty Solar5.24SSI-5K5U [240V]
Samil Power | SolarPond 240HF-US [208V] | Y | N | N | 235W, 208 Vac Utility Interactive Inverter | 0.235 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.08 |  |  | 27 | 34 | 40 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 91.1 | 94.3 | 95.2 | 95.5 | 95.8 | 95.5 | 95.4 | 89.8 | 94.1 | 95 | 95.6 | 95.8 | 95.9 | 95.4 | 89.2 | 93.4 | 94.9 | 95.7 | 95.8 | 95.7 | 95.3 | Samil Power0.235SolarPond 240HF-US [208V]
Samil Power | SolarPond 240HF-US [240V] | Y | N | N | 237W, 240 Vac Utility Interactive Inverter | 0.238 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.08 |  |  | 27 | 34 | 40 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.4 | 93.4 | 94.6 | 95.1 | 95.6 | 95.6 | 95 | 89 | 93 | 94.4 | 95.3 | 95.6 | 95.8 | 95 | 88.5 | 92.7 | 94.1 | 95.6 | 95.6 | 95.7 | 95 | Samil Power0.238SolarPond 240HF-US [240V]
Samil Power | SolarRiver3000TL-US [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.22 | 3 | 0.22 | 100 | 400 | 500 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.8 | 96 | 96.6 | 96.6 | 96.2 | 95.7 | 96.19 | 94 | 96.3 | 96.8 | 97 | 97.1 | 96.8 | 96.89 | 93.3 | 96.1 | 96.8 | 96.9 | 97 | 96.9 | 96.74 | Samil Power3SolarRiver3000TL-US [208V]
Samil Power | SolarRiver3000TL-US [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 3 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.67 | 3 | 0.67 | 100 | 400 | 500 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.3 | 95.8 | 96.6 | 96.8 | 96.7 | 96.4 | 96.51 | 94.2 | 96.6 | 97.2 | 97.3 | 97.5 | 97.1 | 97.24 | 93.7 | 96.2 | 96.8 | 97.1 | 97.2 | 97.3 | 96.97 | Samil Power3SolarRiver3000TL-US [240V]
Samil Power | SolarRiver4000TL-US [208V] | Y | N | N | 4 kW, 208 Vac Utility Interactive Inverter | 4 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.21 | 4 | 0.21 | 100 | 400 | 500 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 94.4 | 96.2 | 96.5 | 97 | 96.4 | 96 | 96.44 | 95.1 | 96.7 | 97.2 | 97.3 | 97.2 | 96.9 | 97.1 | 94.7 | 96.2 | 96.7 | 97 | 96.9 | 96.7 | 96.79 | Samil Power4SolarRiver4000TL-US [208V]
Samil Power | SolarRiver4000TL-US [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 4 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.64 | 4 | 0.64 | 100 | 400 | 500 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 94.1 | 95.9 | 96.6 | 97 | 96.8 | 96.6 | 96.65 | 95.2 | 96.8 | 97.3 | 97.7 | 97.6 | 97.3 | 97.44 | 94.4 | 96.5 | 97.3 | 97.5 | 97.4 | 97.3 | 97.24 | Samil Power4SolarRiver4000TL-US [240V]
Samil Power | SolarRiver5000TL-US [208V] | Y | N | N | 5 kW, 208 Vac Utility Interactive Inverter | 5 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.31 | 5 | 0.31 | 100 | 400 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 94.5 | 96.5 | 96.9 | 97.1 | 96.9 | 96.4 | 96.82 | 94.9 | 96.8 | 97.5 | 97.4 | 97.4 | 97.2 | 97.29 | 95.4 | 97 | 97.8 | 97.8 | 97.7 | 97.2 | 97.57 | Samil Power5SolarRiver5000TL-US [208V]
Samil Power | SolarRiver5000TL-US [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter | 5 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.24 | 5 | 0.24 | 100 | 400 | 500 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 94.5 | 96.5 | 96.9 | 97.1 | 96.9 | 96.4 | 96.82 | 94.9 | 96.8 | 97.5 | 97.4 | 97.4 | 97.2 | 97.29 | 95.4 | 97 | 97.8 | 97.8 | 97.7 | 97.2 | 97.57 | Samil Power5SolarRiver5000TL-US [240V]
Samil Power | SolarRiver6000TL-US [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter | 6 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 | 6 | 0.32 | 100 | 400 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.5 | 96.5 | 96.9 | 97.1 | 96.9 | 96.4 | 96.82 | 94.9 | 96.8 | 97.5 | 97.4 | 97.4 | 97.2 | 97.29 | 95.4 | 97 | 97.8 | 97.8 | 97.7 | 97.2 | 97.57 | Samil Power6SolarRiver6000TL-US [208V]
Samil Power | SolarRiver6000TL-US [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter | 6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.68 | 6 | 0.68 | 100 | 400 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.5 | 96.5 | 96.9 | 97.1 | 96.9 | 96.4 | 96.82 | 94.9 | 96.8 | 97.5 | 97.4 | 97.4 | 97.2 | 97.29 | 95.4 | 97 | 97.8 | 97.8 | 97.7 | 97.2 | 97.57 | Samil Power6SolarRiver6000TL-US [240V]
Samil Power | SolarRiver6000TL-US [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter | 6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.85 | 6 | 0.85 | 100 | 400 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 94.5 | 96.5 | 96.9 | 97.1 | 96.9 | 96.4 | 96.82 | 94.9 | 96.8 | 97.5 | 97.4 | 97.4 | 97.2 | 97.29 | 95.4 | 97 | 97.8 | 97.8 | 97.7 | 97.2 | 97.57 | Samil Power6SolarRiver6000TL-US [277V]
Samil Power | SolarRiver7000TL-US [208V] | Y | N | N | 7 kW, 208 Vac Utility Interactive Inverter | 7 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.27 |  |  | 100 | 400 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.5 | 96 | 96.7 | 97 | 96.9 | 96.6 | 96.7 | 94.4 | 96.6 | 97.2 | 97.5 | 97.3 | 97 | 97.1 | 93.3 | 96 | 96.6 | 97.1 | 97.2 | 96.9 | 96.9 | Samil Power7SolarRiver7000TL-US [208V]
Samil Power | SolarRiver7000TL-US [240V] | Y | N | N | 7 kW, 240 Vac Utility Interactive Inverter | 7 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.39 |  |  | 100 | 400 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 92.7 | 95.8 | 96.6 | 97 | 97.1 | 96.8 | 96.8 | 95.3 | 97.3 | 97.8 | 98 | 97.9 | 97.7 | 97.7 | 94.6 | 96.9 | 97.5 | 97.8 | 97.8 | 97.6 | 97.6 | Samil Power7SolarRiver7000TL-US [240V]
Samil Power | SolarRiver7000TL-US [277V] | Y | N | N | 7 kW, 277 Vac Utility Interactive Inverter | 7 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.45 |  |  | 100 | 400 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 91.2 | 94.7 | 95.9 | 96.8 | 97 | 96.9 | 96.5 | 93.5 | 96.4 | 97.1 | 97.7 | 97.7 | 97.7 | 97.4 | 94.9 | 97.1 | 97.6 | 98.1 | 98.1 | 98 | 97.8 | Samil Power7SolarRiver7000TL-US [277V]
Samil Power | SolarRiver8000TL-US [208V] | Y | N | N | 8kW, 208 Vac Utility Interactive Inverter | 8 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.43 |  |  | 100 | 400 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 93.8 | 96.2 | 96.8 | 97 | 96.9 | 96.4 | 96.7 | 94.5 | 96.4 | 97.2 | 97.5 | 97.3 | 96.9 | 97.1 | 93.7 | 96.2 | 96.9 | 97.2 | 97.1 | 96.7 | 96.9 | Samil Power8SolarRiver8000TL-US [208V]
Samil Power | SolarRiver8000TL-US [240V] | Y | N | N | 8kW, 240 Vac Utility Interactive Inverter | 8 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 100 | 400 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 93 | 96 | 96.7 | 97.1 | 96.9 | 96.7 | 96.7 | 95.7 | 97.4 | 97.8 | 97.9 | 97.8 | 97.5 | 97.7 | 95 | 97.1 | 97.5 | 97.8 | 97.7 | 97.4 | 97.5 | Samil Power8SolarRiver8000TL-US [240V]
Samil Power | SolarRiver8000TL-US [277V] | Y | N | N | 8kW, 277 Vac Utility Interactive Inverter | 8 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.28 |  |  | 100 | 400 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 91 | 94.6 | 96 | 96.8 | 97 | 96.9 | 96.5 | 93.5 | 95.8 | 96.8 | 97.5 | 97.6 | 97.5 | 97.2 | 94.5 | 96.5 | 97.3 | 97.7 | 98 | 97.8 | 97.6 | Samil Power8SolarRiver8000TL-US [277V]
Samil Power | SolarRiver9000TL-US [208V] | Y | N | N | 9 kW, 208 Vac Utility Interactive Inverter | 9 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.43 |  |  | 100 | 400 | 480 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 95 | 96.8 | 97.2 | 97.2 | 96.9 | 96.4 | 96.9 | 95.4 | 97 | 97.3 | 97.3 | 97.2 | 96.8 | 97.1 | 94.7 | 96.5 | 97.1 | 97.3 | 97.1 | 96.7 | 97 | Samil Power9SolarRiver9000TL-US [208V]
Samil Power | SolarRiver9000TL-US [240V] | Y | N | N | 9 kW, 240 Vac Utility Interactive Inverter | 9 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.4 |  |  | 100 | 400 | 480 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 94.1 | 96.8 | 97.2 | 97.4 | 97.4 | 97 | 97.2 | 96 | 97.5 | 97.6 | 98.1 | 97.8 | 97.5 | 97.7 | 95.1 | 96.9 | 97.4 | 97.7 | 97.7 | 97.5 | 97.5 | Samil Power9SolarRiver9000TL-US [240V]
Samil Power | SolarRiver9000TL-US [277V] | Y | N | N | 9 kW, 277 Vac Utility Interactive Inverter | 9 | 277 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.52 |  |  | 100 | 400 | 480 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 92.5 | 95.5 | 96.6 | 97.2 | 97.2 | 97.1 | 96.9 | 93.9 | 96.6 | 97.2 | 97.6 | 97.6 | 97.5 | 97.4 | 95.1 | 97 | 97.7 | 97.9 | 97.8 | 97.7 | 97.7 | Samil Power9SolarRiver9000TL-US [277V]
Samil Power | SolarRiver10000TL-US [208V] | Y | N | N | 10 kW, 208 Vac Utility Interactive Inverter | 10 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.44 |  |  | 100 | 400 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 95.3 | 96.9 | 97.3 | 97.1 | 96.8 | 96.3 | 96.8 | 95 | 97 | 97.4 | 97.4 | 97.1 | 96.6 | 97.1 | 94.2 | 96.6 | 97.1 | 97.2 | 96.9 | 96.6 | 96.9 | Samil Power10SolarRiver10000TL-US [208V]
Samil Power | SolarRiver10000TL-US [240V] | Y | N | N | 10 kW, 240 Vac Utility Interactive Inverter | 10 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.38 |  |  | 100 | 400 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.7 | 96.9 | 97.3 | 97.6 | 97.3 | 97 | 97.2 | 95.8 | 97.5 | 98.1 | 98 | 97.8 | 97.5 | 97.8 | 95.4 | 97.1 | 97.4 | 97.7 | 97.6 | 97.4 | 97.5 | Samil Power10SolarRiver10000TL-US [240V]
Samil Power | SolarRiver10000TL-US [277V] | Y | N | N | 10 kW, 277 Vac Utility Interactive Inverter | 10 | 277 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.44 |  |  | 100 | 400 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 93.2 | 96 | 96.7 | 97.2 | 97.3 | 97.1 | 97 | 94.3 | 96.5 | 97.4 | 97.7 | 97.5 | 97.4 | 97.4 | 95.4 | 97.2 | 97.6 | 97.9 | 97.9 | 97.6 | 97.7 | Samil Power10SolarRiver10000TL-US [277V]
SanRex | PV-100K-48T-13 | Y | N | N | 100 kW Utility Interactive Inverter | 99.68 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 90.92 |  |  | 300 | 400 | 520 | 9.97 | 19.94 | 29.9 | 49.84 | 74.76 | 99.68 | 88.3 | 93.1 | 94.6 | 95.8 | 96.2 | 96.2 | 95.4 | 86.6 | 91.8 | 93.6 | 94.9 | 95.4 | 95.4 | 94.5 | 84.6 | 90.6 | 92.6 | 94.1 | 94.6 | 94.7 | 93.7 | SanRex99.68PV-100K-48T-13
SanRex | PV-250K-48T-13 | Y | N | N | 250 kW Utility Interactive Inverter | 251.4 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 20.5 |  |  | 300 | 400 | 520 | 25.14 | 50.28 | 75.42 | 125.7 | 188.6 | 251.4 | 91.9 | 94.8 | 95.7 | 96.1 | 96 | 95.6 | 95.7 | 90 | 93.5 | 94.7 | 95.3 | 95.2 | 94.8 | 94.9 | 88 | 92.3 | 93.7 | 94.5 | 94.6 | 94.2 | 94.1 | SanRex251.4PV-250K-48T-13
SanRex | PV-500K-48T-13 | Y | N | N | 500 kW Utility Interactive Inverter | 501.4 |  | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 46.27 |  |  | 300 | 400 | 520 | 50.14 | 100.3 | 150.4 | 250.7 | 376.1 | 501.4 | 92.1 | 95.2 | 96 | 96.5 | 96.4 | 96.2 | 96.1 | 90.6 | 94.2 | 95.2 | 95.8 | 95.7 | 95.3 | 95.4 | 88.2 | 93.3 | 94.3 | 95.1 | 95.2 | 94.8 | 94.7 | SanRex501.4PV-500K-48T-13
Satcon Technology | AE-30-60-PV-A [480V] | Y | N | N | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter | 30 | 480 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 59 |  |  | 330 | 410 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 82.9 | 89.8 | 92 | 93.5 | 94.2 | 94.3 | 93.1 | 83.5 | 89.7 | 91.9 | 93.5 | 93.9 | 93.8 | 93 | 81 | 88.6 | 91 | 93 | 93.5 | 93.6 | 92.3 | Satcon Technology30AE-30-60-PV-A [480V]
Satcon Technology | AE-30-60-PV-D [208V] | Y | N | N | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter | 30 | 208 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 54 |  |  | 330 | 410 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 82.1 | 89.2 | 91.4 | 93.1 | 93.4 | 93.2 | 92.5 | 81.5 | 88.7 | 91.2 | 92.8 | 93.2 | 93 | 92.1 | 85.2 | 90.5 | 92.5 | 93.5 | 93.8 | 93.5 | 93.1 | Satcon Technology30AE-30-60-PV-D [208V]
Satcon Technology | AE-30-60-PV-E [240V] | Y | N | N | 30 kW, 240 Vac, 1-phase Utility Interactive Inverter | 30 | 240 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 68 |  |  | 330 | 410 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 85.1 | 90.7 | 92.6 | 93.7 | 93.8 | 93.5 | 93.1 | 84.7 | 90.3 | 92.2 | 93.4 | 93.4 | 92.9 | 92.8 | 83.6 | 89.8 | 91.7 | 93 | 93.1 | 92.8 | 92.4 | Satcon Technology30AE-30-60-PV-E [240V]
Satcon Technology | AE-30-60-PV-F [240V] | Y | N | N | 30 kW, 240 Vac, 3-phase Utility Interactive Inverter | 30 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 59 |  |  | 340 | 375 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 91.6 | 92.5 | 93.9 | 95.2 | 95.5 | 95.6 | 94.9 | 91.8 | 91.9 | 93.6 | 95 | 95.3 | 95.4 | 94.7 | 89.9 | 91.2 | 92.9 | 94.5 | 94.9 | 95 | 94.2 | Satcon Technology30AE-30-60-PV-F [240V]
Satcon Technology | PVS-30 [208V] | Y | N | N | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter | 30 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 75.62 |  |  | 305 | 350 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 88.8 | 93.5 | 94.8 | 95.7 | 95.6 | 95.4 | 95.1 | 88 | 93.1 | 94.7 | 95.4 | 95.5 | 95.3 | 95 | 87 | 92.4 | 94.2 | 95 | 95.1 | 95.1 | 94.5 | Satcon Technology30PVS-30 [208V]
Satcon Technology | PVS-30 [240V] | Y | N | N | 30 kW, 240 Vac, 3-phase Utility Interactive Inverter | 30 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 64.58 |  |  | 305 | 355 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 88.2 | 93.8 | 95 | 96 | 95.8 | 95.6 | 95.3 | 88.2 | 93.3 | 94.8 | 95.7 | 95.7 | 95.6 | 95.1 | 86.1 | 92.5 | 94.4 | 95.3 | 95.5 | 95.2 | 94.8 | Satcon Technology30PVS-30 [240V]
Satcon Technology | PVS-30 [480V] | Y | N | N | 30 kW, 480 Vac, 3-phase Utility Interactive Inverter | 30 | 480 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 72.3 |  |  | 305 | 350 | 480 | 3 | 6 | 9 | 15 | 22.5 | 30 | 88.4 | 93.5 | 94.6 | 95.6 | 95.6 | 95.3 | 95.1 | 87.7 | 93.1 | 94.6 | 95.4 | 95.5 | 95.3 | 95 | 86.3 | 92.1 | 93.9 | 94.9 | 95 | 94.8 | 94.3 | Satcon Technology30PVS-30 [480V]
Satcon Technology | AE-50-60-PV-D [208V] | Y | N | N | 50 kW, 208 Vac, 3-phase Utility Interactive Inverter | 50 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 90 |  |  | 327.2 | 410.9 | 474.9 | 5 | 10 | 15 | 25 | 37.5 | 50 | 88.2 | 93 | 94.4 | 95.4 | 95.2 | 95.2 | 94.7 | 86.7 | 92 | 93.8 | 94.9 | 94.8 | 94.8 | 94.2 | 85.8 | 91.2 | 93.2 | 94.6 | 94.5 | 94.6 | 93.8 | Satcon Technology50AE-50-60-PV-D [208V]
Satcon Technology | AE-50-60-PV-F [240V] | Y | N | N | 50 kW, 240 Vac, 3-phase Utility Interactive Inverter | 50 | 240 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 68 |  |  | 340 | 430 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 84.3 | 90.6 | 92.7 | 94.4 | 94.4 | 94.5 | 93.6 | 81.8 | 89.1 | 91.8 | 93.6 | 93.8 | 94 | 92.8 | 80.2 | 88.2 | 91 | 93.2 | 93.5 | 93.8 | 92.3 | Satcon Technology50AE-50-60-PV-F [240V]
Satcon Technology | PVS-50 [208V] | Y | N | N | 50 kW, 208 Vac, 3-phase Utility Interactive Inverter | 50 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 76.5 |  |  | 305 | 350 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.4 | 93.8 | 95.4 | 95.9 | 95.9 | 95.7 | 95.5 | 89.7 | 94.1 | 95.2 | 95.8 | 95.8 | 95.6 | 95.4 | 88.7 | 93 | 94.5 | 95.3 | 95.4 | 95.3 | 94.9 | Satcon Technology50PVS-50 [208V]
Satcon Technology | PVS-50 [240V] | Y | N | N | 50 kW, 240 Vac, 3-phase Utility Interactive Inverter | 50 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 93.97 |  |  | 310 | 365 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.8 | 95 | 95.9 | 96.2 | 96 | 95.5 | 95.7 | 90.4 | 94.8 | 95.3 | 96 | 95.7 | 95.5 | 95.5 | 89.6 | 93.3 | 95.2 | 95.5 | 95.4 | 95 | 95.1 | Satcon Technology50PVS-50 [240V]
Satcon Technology | PVS-50 [480V] | Y | N | N | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter | 50 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 76.5 |  |  | 305 | 350 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.5 | 95 | 95.9 | 96.3 | 96.4 | 96 | 96 | 89.4 | 94.7 | 95.6 | 96.1 | 96.1 | 95.9 | 95.7 | 89.5 | 94.2 | 95.1 | 95.8 | 95.6 | 95.4 | 95.3 | Satcon Technology50PVS-50 [480V]
Satcon Technology | PVS-50-S-MT [208V] | Y | N | N | 50 kW, 208 Vac, 3-phase Utility Interactive Inverter | 50 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 81 | 50 | 81 | 265 | 320 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 91.6 | 95.4 | 96.1 | 96.3 | 96.1 | 95.7 | 95.9 | 91.3 | 95.3 | 96 | 96.2 | 96 | 95.6 | 95.8 | 89 | 94.8 | 95.4 | 95.5 | 95.5 | 95.1 | 95.2 | Satcon Technology50PVS-50-S-MT [208V]
Satcon Technology | PVS-50-S-MT [240V] | Y | N | N | 50 kW, 240 Vac, 3-phase Utility Interactive Inverter | 50 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 78 | 50 | 78 | 265 | 320 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 91.6 | 95.3 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 91 | 95.1 | 95.8 | 96.2 | 95.8 | 95.5 | 95.7 | 87.8 | 94.7 | 95.3 | 95.7 | 95.4 | 95.2 | 95.1 | Satcon Technology50PVS-50-S-MT [240V]
Satcon Technology | PVS-50-S-MT [480V] | Y | N | N | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter | 50 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 78 | 50 | 78 | 265 | 320 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 92.1 | 95.3 | 96 | 96.2 | 96 | 95.7 | 95.9 | 91.5 | 95 | 95.7 | 96.1 | 95.9 | 95.6 | 95.7 | 88.7 | 94.3 | 95.3 | 95.6 | 95.4 | 95.2 | 95.1 | Satcon Technology50PVS-50-S-MT [480V]
Satcon Technology | AE-50-60-PV-A [480V] | Y | N | N | 50 kW, 480 Vac, 3-phase Utility Interactive Inverter | 50.25 | 480 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 100.8 |  |  | 330 | 420 | 480 | 5.03 | 10.05 | 15.08 | 25.13 | 37.69 | 50.25 | 81.1 | 88.9 | 91.7 | 93.7 | 94.6 | 94.7 | 93.2 | 79.9 | 88.2 | 91.1 | 93.3 | 94.3 | 94.7 | 92.8 | 79.3 | 87.7 | 90.6 | 93 | 93.9 | 94.2 | 92.5 | Satcon Technology50.25AE-50-60-PV-A [480V]
Satcon Technology | AE-75-60-PV-A [480V] | Y | N | N | 75 kW, 480 Vac, 3-phase Utility Interactive Inverter | 75 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 99 |  |  | 318.9 | 405.6 | 479.5 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 91.1 | 94.4 | 95.5 | 96.1 | 96 | 95.9 | 95.7 | 90.3 | 93.9 | 95.1 | 95.8 | 95.6 | 95.5 | 95.3 | 89.5 | 93.4 | 94.6 | 95.5 | 95.4 | 95.3 | 95 | Satcon Technology75AE-75-60-PV-A [480V]
Satcon Technology | AE-75-60-PV-D [208V] | Y | N | N | 75 kW, 208 Vac, 3-phase Utility Interactive Inverter | 75 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 99 |  |  | 330 | 415 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 90.9 | 94.4 | 95.5 | 96.1 | 96 | 95.9 | 95.7 | 90.5 | 94 | 95.1 | 95.9 | 95.7 | 95.6 | 95.4 | 89.6 | 93.6 | 94.9 | 95.6 | 95.5 | 95.4 | 95.1 | Satcon Technology75AE-75-60-PV-D [208V]
Satcon Technology | PVS-75 [208V] | Y | N | N | 75 kW, 208 Vac, 3-phase Utility Interactive Inverter | 75 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 65.36 |  |  | 315 | 365 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 91 | 95.5 | 96.1 | 96.6 | 96.4 | 96.1 | 96.1 | 90.9 | 95.3 | 95.9 | 96.4 | 96.3 | 96 | 96 | 89.7 | 94.6 | 95.4 | 96.1 | 95.9 | 95.7 | 95.5 | Satcon Technology75PVS-75 [208V]
Satcon Technology | PVS-75 [240V] | Y | N | N | 75 kW, 240 Vac, 3-phase Utility Interactive Inverter | 75 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 71.84 |  |  | 315 | 365 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.3 | 95.5 | 96.3 | 96.6 | 96.6 | 96.3 | 96.3 | 91.2 | 95.5 | 96 | 96.5 | 96.5 | 96.2 | 96.1 | 90.6 | 94.8 | 95.4 | 96.1 | 96 | 96 | 95.7 | Satcon Technology75PVS-75 [240V]
Satcon Technology | PVS-75 [480V] | Y | N | N | 75 kW, 480 Vac, 3-phase Utility Interactive Inverter | 75 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 69.5 |  |  | 315 | 365 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 92.6 | 95.6 | 96.3 | 96.7 | 96.6 | 96.3 | 96.3 | 92.1 | 95.3 | 96 | 96.5 | 96.4 | 96.2 | 96.2 | 91.3 | 94.9 | 95.7 | 96.1 | 96.1 | 96 | 95.8 | Satcon Technology75PVS-75 [480V]
Satcon Technology | AE-100-60-PV-A [480V] | Y | N | N | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 97.7 |  |  | 330 | 410 | 470 | 10 | 20 | 30 | 50 | 75 | 100 | 88.7 | 93.1 | 94.6 | 95.6 | 95.8 | 95.7 | 95.2 | 87.3 | 92.3 | 93.9 | 95 | 95.3 | 95.2 | 94.6 | 86.6 | 91.8 | 93.6 | 94.8 | 95.1 | 95.1 | 94.4 | Satcon Technology100AE-100-60-PV-A [480V]
Satcon Technology | AE-100-60-PV-A-HE [480V] | Y | N | N | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 97.7 |  |  | 330 | 400 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 93.2 | 95.5 | 96 | 96.1 | 95.6 | 95.3 | 95.7 | 93.3 | 95.3 | 95.8 | 95.9 | 95.9 | 95.2 | 95.7 | 92.9 | 94.7 | 95.5 | 95.4 | 95.2 | 94.8 | 95.2 | Satcon Technology100AE-100-60-PV-A-HE [480V]
Satcon Technology | AE-100-60-PV-D [208V] | Y | N | N | 100 kW, 208 Vac, 3-phase Utility Interactive Inverter | 100 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 91.5 |  |  | 330 | 402 | 470 | 10 | 20 | 30 | 50 | 75 | 100 | 89.3 | 94.1 | 94.5 | 95.6 | 95.3 | 95.1 | 95 | 88.6 | 92.9 | 94.2 | 95 | 95.1 | 94.9 | 94.6 | 89.7 | 92.8 | 94.2 | 94.7 | 94.7 | 94.5 | 94.4 | Satcon Technology100AE-100-60-PV-D [208V]
Satcon Technology | AE-100-60-PV-F [240V] | Y | N | N | 100 kW, 240 Vac, 3-phase Utility Interactive Inverter | 100 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 97.7 |  |  | 330 | 408 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.2 | 93.9 | 94.9 | 95.8 | 95.7 | 95.5 | 95.3 | 89.3 | 93.2 | 94.7 | 95.3 | 95.4 | 95.2 | 94.9 | 88.8 | 93.2 | 94.2 | 95 | 95.3 | 94.9 | 94.7 | Satcon Technology100AE-100-60-PV-F [240V]
Satcon Technology | PVS-100 [208V] | Y | N | N | 100 kW, 208 Vac, 3-phase Utility Interactive Inverter | 100 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 62.34 |  |  | 315 | 365 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 92.6 | 95.7 | 96.4 | 96.6 | 96.5 | 96.2 | 96.3 | 92.4 | 95.5 | 96.2 | 96.5 | 96.4 | 96.1 | 96.2 | 91.3 | 94.9 | 95.7 | 96.1 | 96.1 | 95.8 | 95.8 | Satcon Technology100PVS-100 [208V]
Satcon Technology | PVS-100 [240V] | Y | N | N | 100 kW, 240 Vac, 3-phase Utility Interactive Inverter | 100 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 61.57 |  |  | 315 | 365 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.1 | 95.3 | 96.1 | 96.5 | 96.5 | 96.2 | 96.1 | 90.6 | 94.9 | 95.9 | 96.4 | 96.3 | 96.1 | 96 | 89.4 | 94.3 | 95.4 | 96 | 96 | 95.8 | 95.6 | Satcon Technology100PVS-100 [240V]
Satcon Technology | PVS-100 [480V] | Y | N | N | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 66.13 |  |  | 315 | 365 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 93.2 | 96.1 | 96.5 | 96.7 | 96.5 | 96.1 | 96.4 | 93.6 | 95.9 | 96.4 | 96.5 | 96.4 | 96 | 96.3 | 93 | 95.6 | 96.2 | 96.3 | 96.1 | 95.8 | 96 | Satcon Technology100PVS-100 [480V]
Satcon Technology | SDMS0100208LNIU [208V] | Y | N | N | 100 kW, 208 Vac, 3-phase Inverter with combiner | 100 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 60.38 |  |  | 300 | 430 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.5 | 94.2 | 95.2 | 95.5 | 95.2 | 94.8 | 95 | 89.5 | 92.3 | 95 | 95.8 | 95.6 | 95.3 | 95.1 | 90.1 | 93.5 | 94.7 | 95.9 | 95.8 | 95.5 | 95.3 | Satcon Technology100SDMS0100208LNIU [208V]
Satcon Technology | SDMS0100240LNIU [240V] | Y | N | N | 100 kW, 240 Vac, 3-phase Inverter with combiner | 100 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 61.79 |  |  | 300 | 430 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.1 | 93.5 | 94.6 | 95.1 | 95.1 | 94.7 | 94.7 | 88.1 | 91.6 | 94.4 | 95.4 | 95.5 | 95.2 | 94.8 | 88.7 | 92.8 | 94.2 | 95.5 | 95.7 | 95.3 | 95 | Satcon Technology100SDMS0100240LNIU [240V]
Satcon Technology | SDMS0100480LNIU [480V] | Y | N | N | 100 kW, 480 Vac, 3-phase Inverter with combiner | 100 | 480 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 63.88 |  |  | 300 | 430 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 89.5 | 93.4 | 94.4 | 95.1 | 95 | 94.7 | 94.6 | 87.6 | 91.5 | 94.3 | 95.3 | 95.4 | 95.2 | 94.7 | 88.1 | 92.7 | 94 | 95.4 | 95.6 | 95.4 | 94.9 | Satcon Technology100SDMS0100480LNIU [480V]
Satcon Technology | PVS-110-S-MT [208V] | Y | N | N | 110 kW, 208 Vac, 3-phase Utility Interactive Inverter | 110 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 72.5 |  |  | 265 | 320 | 480 | 11 | 22 | 33 | 55 | 82.5 | 110 | 92.6 | 95.4 | 95.8 | 95.9 | 95.6 | 94.8 | 95.5 | 91.9 | 95 | 95.5 | 95.7 | 95.4 | 94.7 | 95.3 | 89.8 | 93.7 | 94.6 | 95 | 94.8 | 94.1 | 94.5 | Satcon Technology110PVS-110-S-MT [208V]
Satcon Technology | PVS-110-S-MT [240V] | Y | N | N | 110 kW, 240 Vac, 3-phase Utility Interactive Inverter | 110 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 70.6 |  |  | 265 | 320 | 480 | 11 | 22 | 33 | 55 | 82.5 | 110 | 93 | 95.6 | 96.1 | 96.1 | 95.8 | 95.2 | 95.8 | 92.3 | 95.2 | 95.8 | 95.8 | 95.6 | 95 | 95.5 | 90.4 | 94.1 | 94.9 | 95.2 | 95 | 94.5 | 94.8 | Satcon Technology110PVS-110-S-MT [240V]
Satcon Technology | PVS-110-S-MT [480V] | Y | N | N | 110 kW, 480 Vac, 3-phase Utility Interactive Inverter | 110 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 74.3 |  |  | 265 | 320 | 480 | 11 | 22 | 33 | 55 | 82.5 | 110 | 93.2 | 95.8 | 96.1 | 96.3 | 96 | 95.5 | 95.9 | 92.6 | 95.4 | 95.8 | 96 | 95.8 | 95.3 | 95.7 | 90.9 | 94.3 | 95 | 95.3 | 95.3 | 94.8 | 95 | Satcon Technology110PVS-110-S-MT [480V]
Satcon Technology | AE-135-60-PV-A [480V] | Y | N | N | 135 kW, 480 Vac, 3-phase Utility Interactive Inverter | 135 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 98 |  |  | 330 | 415 | 470 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 90.7 | 94.2 | 95.4 | 96.1 | 96.1 | 95.9 | 95.7 | 90 | 93.8 | 95 | 95.6 | 95.7 | 95.5 | 95.3 | 89.4 | 93.4 | 94.7 | 95.4 | 95.5 | 95.4 | 95 | Satcon Technology135AE-135-60-PV-A [480V]
Satcon Technology | AE-135-60-PV-D [208V] | Y | N | N | 135 kW, 208 Vac, 3-phase Utility Interactive Inverter | 135 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 96 |  |  | 330 | 415 | 470 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 91.6 | 94.9 | 95.6 | 96 | 95.9 | 95.5 | 95.7 | 91.1 | 94.5 | 95.4 | 95.9 | 95.7 | 95.3 | 95.4 | 88.7 | 92.7 | 94.2 | 95 | 95.1 | 94.9 | 94.6 | Satcon Technology135AE-135-60-PV-D [208V]
Satcon Technology | PVS-135 [208V] | Y | N | N | 135 kW, 208 Vac, 3-phase Utility Interactive Inverter | 135 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 63.12 |  |  | 310 | 355 | 480 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 92.9 | 95.6 | 95.8 | 96.5 | 96.4 | 96.1 | 96.1 | 92.5 | 95.4 | 96.1 | 96.4 | 96.2 | 95.9 | 96 | 91 | 94 | 95 | 95.7 | 95.8 | 95.7 | 95.4 | Satcon Technology135PVS-135 [208V]
Satcon Technology | PVS-135 [240V] | Y | N | N | 135 kW, 240 Vac, 3-phase Utility Interactive Inverter | 135 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 63.7 |  |  | 320 | 360 | 480 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 92.4 | 95.6 | 95.8 | 96.6 | 96.6 | 96.3 | 96.3 | 92 | 95.3 | 96 | 96.4 | 96.4 | 96.2 | 96.1 | 91 | 94 | 95 | 95.7 | 95.8 | 95.7 | 95.4 | Satcon Technology135PVS-135 [240V]
Satcon Technology | PVS-135 [480V] | Y | N | N | 135 kW, 480 Vac, 3-phase Utility Interactive Inverter | 135 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 63.67 |  |  | 310 | 355 | 480 | 13.5 | 27 | 40.5 | 67.5 | 101.3 | 135 | 92.9 | 95.8 | 96.5 | 96.7 | 96.5 | 96.2 | 96.4 | 92.4 | 95.5 | 96.2 | 96.4 | 96.4 | 96.1 | 96.1 | 90.8 | 94.7 | 95.6 | 96 | 95.9 | 95.7 | 95.6 | Satcon Technology135PVS-135 [480V]
Satcon Technology | PVS-210-S [208V] | Y | N | N | 210 kW, 208 Vac, 3-phase Utility Interactive Inverter | 210 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 160.8 |  |  | 265 | 318 | 480 | 21 | 42 | 63 | 105 | 157.5 | 210 | 93.5 | 95.7 | 96.2 | 96.2 | 96.1 | 95.5 | 96 | 93.1 | 95.5 | 96 | 96 | 95.6 | 95.2 | 95.6 | 91.9 | 94.6 | 95.2 | 95.3 | 95 | 94.6 | 94.9 | Satcon Technology210PVS-210-S [208V]
Satcon Technology | PVS-210-S [240V] | Y | N | N | 210 kW, 240 Vac, 3-phase Utility Interactive Inverter | 210 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 112.9 |  |  | 265 | 318 | 480 | 21 | 42 | 63 | 105 | 157.5 | 210 | 93.2 | 95.7 | 96.2 | 96.3 | 96.1 | 95.6 | 96 | 92.7 | 95.5 | 95.9 | 96 | 95.7 | 95.3 | 95.7 | 91.6 | 94.4 | 95.2 | 95.2 | 95.1 | 94.6 | 95 | Satcon Technology210PVS-210-S [240V]
Satcon Technology | PVS-210-S [480V] | Y | N | N | 210 kW, 480 Vac, 3-phase Utility Interactive Inverter | 210 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 189.8 |  |  | 265 | 318 | 480 | 21 | 42 | 63 | 105 | 157.5 | 210 | 92 | 95.2 | 95.8 | 96.2 | 96 | 95.7 | 95.8 | 91.7 | 94.9 | 95.7 | 95.9 | 95.5 | 95.4 | 95.4 | 90.8 | 94.1 | 95 | 95.3 | 95.1 | 94.8 | 94.9 | Satcon Technology210PVS-210-S [480V]
Satcon Technology | AE-225-60-PV-A [480V] | Y | N | N | 225 kW, 480 Vac, 3-phase Utility Interactive Inverter | 225 | 480 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 114 |  |  | 330 | 430 | 480 | 22.5 | 45 | 67.5 | 112.5 | 168.8 | 225 | 90.2 | 93.5 | 94.8 | 95.5 | 95.5 | 95.4 | 95.1 | 89 | 93 | 94.3 | 95 | 95.1 | 94.8 | 94.6 | 88.5 | 92.7 | 94 | 94.8 | 95 | 94.6 | 94.4 | Satcon Technology225AE-225-60-PV-A [480V]
Satcon Technology | AE-225-60-PV-D [208V] | Y | N | N | 225 kW, 208 Vac, 3-phase Utility Interactive Inverter | 225 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 180 |  |  | 330 | 415 | 470 | 22.5 | 45 | 67.5 | 112.5 | 168.8 | 225 | 92.2 | 95 | 95.7 | 96.1 | 95.9 | 95.5 | 95.7 | 93.2 | 94.7 | 95.5 | 95.8 | 95.7 | 95.3 | 95.5 | 91.8 | 94.4 | 95.2 | 95.6 | 95.5 | 95.2 | 95.2 | Satcon Technology225AE-225-60-PV-D [208V]
Satcon Technology | PVS-250 | Y | N | N | 250 kW, 3-phase Inverter for Medium Voltage Transformer | 250 |  | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 151.8 |  |  | 330 | 368 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 93.8 | 95.4 | 96 | 96.2 | 96 | 95.4 | 95.9 | 93.3 | 95.2 | 95.8 | 96 | 95.8 | 95.2 | 95.7 | 92.1 | 94.6 | 95.3 | 95.6 | 95.2 | 94.7 | 95.1 | Satcon Technology250PVS-250
Satcon Technology | PVS-250 [208V] | Y | N | N | 250 kW, 208 Vac, 3-phase Utility Interactive Inverter | 250 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 105.1 | 250 | 105.1 | 320 | 365 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 95.1 | 96.3 | 96.5 | 96.4 | 96.5 | 96 | 96.4 | 94.4 | 95.9 | 96.4 | 96.3 | 96.3 | 95.8 | 96.2 | 93.7 | 95.9 | 96.2 | 95.9 | 95.8 | 95.3 | 95.8 | Satcon Technology250PVS-250 [208V]
Satcon Technology | PVS-250 [240V] | Y | N | N | 250 kW, 240 Vac, 3-phase Utility Interactive Inverter | 250 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 100 | 250 | 100 | 322 | 365 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 92.5 | 95.8 | 96.4 | 96.6 | 96.5 | 96.2 | 96.3 | 92.3 | 95.6 | 96.2 | 96.4 | 96.3 | 96 | 96.1 | 91.9 | 95.1 | 95.9 | 96 | 95.9 | 95.6 | 95.7 | Satcon Technology250PVS-250 [240V]
Satcon Technology | PVS-250 [480V] | Y | N | N | 250 kW, 480 Vac, 3-phase Utility Interactive Inverter | 250 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 119.7 | 250 | 119.7 | 320 | 365 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 93.4 | 96 | 96.4 | 96.6 | 96.5 | 96 | 96.3 | 93.1 | 95.7 | 96.2 | 96.3 | 96.2 | 95.7 | 96 | 92.3 | 94.9 | 95.8 | 95.9 | 95.7 | 95.2 | 95.5 | Satcon Technology250PVS-250 [480V]
Satcon Technology | PVS-375 [480V] | Y | N | N | 375 kW, 480 Vac, 3-phase Utility Interactive Inverter | 375 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 123.5 |  |  | 320 | 365 | 480 | 37.5 | 75 | 112.5 | 187.5 | 281.3 | 375 | 92.6 | 95.4 | 96 | 96.3 | 96.2 | 95.8 | 96 | 92.1 | 95.1 | 95.7 | 96 | 95.8 | 95.6 | 95.7 | 90.9 | 94.6 | 95 | 95.5 | 95.3 | 95.1 | 95.1 | Satcon Technology375PVS-375 [480V]
Satcon Technology | AE-500-60-PV-A [480V] | Y | N | N | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 208 |  |  | 330 | 405 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.2 | 94.9 | 95.7 | 95.8 | 95.6 | 95.2 | 95.5 | 91.8 | 94.5 | 95.4 | 95.5 | 95.4 | 94.9 | 95.2 | 91.3 | 93.7 | 94.6 | 95.1 | 95 | 94.8 | 94.8 | Satcon Technology500AE-500-60-PV-A [480V]
Satcon Technology | EQX0500US200X-N | Y | N | N | 500 kW, 3-phase Inverter, N for ground type | 500 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 171.5 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.9 | 96.1 | 96.5 | 96.6 | 96.1 | 95.6 | 96.2 | 93.6 | 96 | 96.5 | 96.5 | 96.1 | 95.6 | 96.1 | 92.7 | 95.5 | 96.1 | 96.2 | 95.9 | 95.5 | 95.8 | Satcon Technology500EQX0500US200X-N
Satcon Technology | EQX0500US200X-P | Y | N | N | 500 kW, 3-phase Inverter, P for ground type | 500 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 171.5 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.9 | 96.1 | 96.5 | 96.6 | 96.1 | 95.6 | 96.2 | 93.6 | 96 | 96.5 | 96.5 | 96.1 | 95.6 | 96.1 | 92.7 | 95.5 | 96.1 | 96.2 | 95.9 | 95.5 | 95.8 | Satcon Technology500EQX0500US200X-P
Satcon Technology | EQX0500US480T-N | Y | N | N | 500 kW, 3-phase Inverter, N for ground type | 500 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 116.5 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 92 | 95.4 | 96.2 | 96.7 | 96.6 | 96.4 | 96.3 | 91.7 | 95.3 | 96.1 | 96.6 | 96.6 | 96.5 | 96.3 | 90.8 | 94.8 | 95.8 | 96.4 | 96.4 | 96.3 | 96 | Satcon Technology500EQX0500US480T-N
Satcon Technology | EQX0500US480T-P | Y | N | N | 500 kW, 3-phase Inverter, P for ground type | 500 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 116.5 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 92 | 95.4 | 96.2 | 96.7 | 96.6 | 96.4 | 96.3 | 91.7 | 95.3 | 96.1 | 96.6 | 96.6 | 96.5 | 96.3 | 90.8 | 94.8 | 95.8 | 96.4 | 96.4 | 96.3 | 96 | Satcon Technology500EQX0500US480T-P
Satcon Technology | PVS-500 | Y | N | N | 500 kW, 3-phase Inverter for Medium Voltage Transformer | 500 |  | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2630 |  |  | 320 | 365 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.9 | 95.7 | 96.1 | 96 | 95.4 | 94.6 | 95.5 | 93.3 | 95.4 | 95.8 | 95.8 | 95.2 | 94.5 | 95.3 | 92.9 | 94.9 | 95.4 | 95.5 | 94.9 | 94.2 | 95 | Satcon Technology500PVS-500
Satcon Technology | PVS-500 [480V] | Y | N | N | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 131.1 |  |  | 315 | 365 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 92.9 | 95.7 | 96.2 | 96.5 | 96.4 | 96 | 96.2 | 92.4 | 95.4 | 96.1 | 96.3 | 96.2 | 95.8 | 96 | 91.8 | 95 | 95.7 | 96 | 95.8 | 95.3 | 95.6 | Satcon Technology500PVS-500 [480V]
Satcon Technology | SDMS0500UL320XN [320V] | Y | N | N | 500 kW, 320 Vac, 3-phase Inverter with combiner, N for ground type | 500 | 320 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 98 |  |  | 300 | 430 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 90.51 | 94.95 | 95.18 | 95.47 | 95.31 | 94.7 | 95.09 | 91.29 | 93.9 | 95.72 | 95.96 | 95.59 | 95.09 | 95.4 | 90.71 | 93.8 | 95.8 | 95.9 | 95.76 | 95.19 | 95.46 | Satcon Technology500SDMS0500UL320XN [320V]
Satcon Technology | SDMS0500UL320XP [320V] | Y | N | N | 501 kW, 320 Vac, 3-phase Inverter with combiner, P for ground type | 500 | 320 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 98 |  |  | 300 | 430 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 90.51 | 94.95 | 95.18 | 95.47 | 95.31 | 94.7 | 95.09 | 91.29 | 93.9 | 95.72 | 95.96 | 95.59 | 95.09 | 95.4 | 90.71 | 93.8 | 95.8 | 95.9 | 95.76 | 95.19 | 95.46 | Satcon Technology500SDMS0500UL320XP [320V]
Satcon Technology | SDMS0500UL480TN [480V] | Y | N | N | 500 kW, 480 Vac, 3-phase Inverter with combiner, N for ground type | 500 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 101 |  |  | 300 | 430 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 90.2 | 95.09 | 95.37 | 95.88 | 95.89 | 95.51 | 95.54 | 90.99 | 94.04 | 95.92 | 96.36 | 96.17 | 95.9 | 95.85 | 90.4 | 93.94 | 95.99 | 96.31 | 96.34 | 96 | 95.92 | Satcon Technology500SDMS0500UL480TN [480V]
Satcon Technology | SDMS0500UL480TP [480V] | Y | N | N | 501 kW, 480 Vac, 3-phase Inverter with combiner, P for ground type | 500 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 101 |  |  | 300 | 430 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 90.2 | 95.09 | 95.37 | 95.88 | 95.89 | 95.51 | 95.54 | 90.99 | 94.04 | 95.92 | 96.36 | 96.17 | 95.9 | 95.85 | 90.4 | 93.94 | 95.99 | 96.31 | 96.34 | 96 | 95.92 | Satcon Technology500SDMS0500UL480TP [480V]
Satcon Technology | EPP-1000-0600-32060-200X-U-N | Y | N | N | 1000 kW, 3-phase Inverter, N for ground type | 1000 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 325.5 |  |  | 320 | 360 | 480 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.53 | 96.46 | 96.79 | 96.78 | 96.35 | 95.71 | 96.4 | 94.29 | 96.32 | 96.66 | 96.68 | 96.31 | 95.7 | 96.32 | 93.53 | 95.84 | 96.32 | 96.43 | 96.12 | 95.58 | 96.07 | Satcon Technology1000EPP-1000-0600-32060-200X-U-N
Satcon Technology | EPP-1000-0600-32060-200X-U-P | Y | N | N | 1000 kW, 3-phase Inverter, P for ground type | 1000 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 325.5 |  |  | 320 | 360 | 480 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.53 | 96.46 | 96.79 | 96.78 | 96.35 | 95.71 | 96.4 | 94.29 | 96.32 | 96.66 | 96.68 | 96.31 | 95.7 | 96.32 | 93.53 | 95.84 | 96.32 | 96.43 | 96.12 | 95.58 | 96.07 | Satcon Technology1000EPP-1000-0600-32060-200X-U-P
Satcon Technology | PVS-1000 | Y | N | N | 1000 kW, 3-phase Inverter for Medium Voltage Transformer | 1000 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 396.4 |  |  | 420 | 486 | 670 | 100 | 200 | 300 | 500 | 750 | 1000 | 93.7 | 96.1 | 96.7 | 96.9 | 96.6 | 96.1 | 96.5 | 93.2 | 95.8 | 96.4 | 96.7 | 96.5 | 96 | 96.3 | 91.7 | 94.9 | 95.7 | 96.1 | 95.9 | 95.5 | 95.7 | Satcon Technology1000PVS-1000
Satcon Technology | EPP-1250-1000-52085-320X-U-N | Y | N | N | 1250 kW, 3-phase Inverter, N for ground type | 1250 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 320.4 |  |  | 525 | 595 | 800 | 125 | 250 | 375 | 625 | 937.5 | 1250 | 94.6 | 96.7 | 97.3 | 97.4 | 97.1 | 96.7 | 97 | 94.1 | 96.5 | 97.1 | 97.2 | 97 | 96.5 | 96.9 | 93 | 95.9 | 96.6 | 96.8 | 96.7 | 96.2 | 96.5 | Satcon Technology1250EPP-1250-1000-52085-320X-U-N
Satcon Technology | EPP-1250-1000-52085-320X-U-P | Y | N | N | 1250 kW, 3-phase Inverter, P for ground type | 1250 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 320.4 |  |  | 525 | 595 | 800 | 125 | 250 | 375 | 625 | 937.5 | 1250 | 94.6 | 96.7 | 97.3 | 97.4 | 97.1 | 96.7 | 97 | 94.1 | 96.5 | 97.1 | 97.2 | 97 | 96.5 | 96.9 | 93 | 95.9 | 96.6 | 96.8 | 96.7 | 96.2 | 96.5 | Satcon Technology1250EPP-1250-1000-52085-320X-U-P
Schneider Electric Solar Inverters USA, Inc. | Conext TX 2800 NA [208V] | Y | N | N | 2.65 kW, 208 Vac, Grid Tie Inverter | 2.65 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.23 | 2.65 | 1.23 | 100 | 300 | 480 | 0.27 | 0.53 | 0.8 | 1.33 | 1.99 | 2.65 | 88.5 | 93.2 | 94.5 | 95.2 | 95.2 | 94.8 | 94.7 | 87.9 | 92.9 | 94.2 | 95 | 95 | 94.8 | 94.5 | 85.9 | 91.8 | 93.5 | 94.4 | 94.5 | 94.4 | 93.9 | Schneider Electric Solar Inverters USA, Inc.2.65Conext TX 2800 NA [208V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext TX 2800 NA [240V] | Y | N | N | 2.8 kW, 240 Vac, Grid Tie Inverter | 2.8 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.22 | 2.8 | 1.22 | 100 | 300 | 480 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 88.9 | 93.4 | 94.5 | 95.2 | 95.2 | 94.8 | 94.8 | 88.4 | 93.1 | 94.3 | 95 | 95.1 | 94.7 | 94.6 | 86.4 | 92.2 | 93.7 | 94.6 | 94.7 | 94.3 | 94 | Schneider Electric Solar Inverters USA, Inc.2.8Conext TX 2800 NA [240V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext TX 3300 NA [208V] | Y | N | N | 3.1 kW, 208 Vac, Grid Tie Inverter | 3.1 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.96 | 3.1 | 96 | 100 | 300 | 480 | 0.31 | 0.62 | 0.93 | 1.55 | 2.33 | 3.1 | 89.3 | 93.4 | 94.6 | 95.3 | 95.2 | 94.7 | 94.8 | 88.9 | 93.1 | 94.5 | 95.1 | 95.1 | 94.6 | 94.6 | 86.7 | 92.3 | 93.8 | 94.6 | 94.7 | 94.2 | 94.1 | Schneider Electric Solar Inverters USA, Inc.3.1Conext TX 3300 NA [208V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext TX 3300 NA [240V] | Y | N | N | 3.3 kW, 240 Vac, Grid Tie Inverter | 3.3 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.22 | 3.3 | 1.22 | 100 | 300 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 89.8 | 93.9 | 94.9 | 95.6 | 95.5 | 95.1 | 95.1 | 89.4 | 93.6 | 94.7 | 95.4 | 95.4 | 95 | 95 | 87.8 | 92.8 | 94.2 | 95 | 95 | 94.7 | 94.5 | Schneider Electric Solar Inverters USA, Inc.3.3Conext TX 3300 NA [240V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext TX 3800 NA [208V] | Y | N | N | 3.5 kW, 208 Vac, Grid Tie Inverter | 3.5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.96 | 3.5 | 0.96 | 100 | 300 | 480 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 91.3 | 95 | 95.8 | 96 | 95.8 | 95.3 | 95.6 | 90.9 | 94.6 | 95.6 | 95.8 | 95.6 | 95.1 | 95.4 | 89.2 | 93.8 | 94.9 | 95.3 | 95.2 | 94.7 | 94.8 | Schneider Electric Solar Inverters USA, Inc.3.5Conext TX 3800 NA [208V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext TX 3800 NA [240V] | Y | N | N | 3.8 kW, 240 Vac, Grid Tie Inverter | 3.8 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.21 | 3.8 | 1.21 | 100 | 300 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.3 | 95.4 | 96.2 | 96.3 | 96.1 | 95.5 | 95.9 | 91.8 | 95.1 | 95.9 | 96.1 | 95.8 | 95.4 | 95.7 | 90.1 | 94.2 | 95.2 | 95.6 | 95.4 | 95 | 95.1 | Schneider Electric Solar Inverters USA, Inc.3.8Conext TX 3800 NA [240V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW4024-120/240-60 [120V] | Y | N | N | 4 kVA, 24 Vdc, 120/240 Vac, battery backup, Utility Interactive Inverter | 4 | 120 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 29.65 | 4 | 29.65 | 100 | 26 | 29 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 87.9 | 92.9 | 93.5 | 93 | 91.3 | 89.4 | 91.8 | 87.8 | 92.8 | 93.4 | 92.9 | 91.2 | 89.2 | 91.7 | 87.8 | 92.6 | 93.2 | 92.5 | 91 | 89.1 | 91.5 | Schneider Electric Solar Inverters USA, Inc.4XW4024-120/240-60 [120V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW4024-120/240-60 | Y | N | N | 4 kVA, 24 Vdc, 120/240 Vac, battery backup, Utility Interactive Inverter | 4.09 |  | 91 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 24 |  |  | 100 | 26 | 29 | 0.41 | 0.82 | 1.2 | 2 | 3.1 | 4.1 | 88.8 | 92.9 | 93.3 | 92.5 | 90.5 | 88.4 | 91.2 | 88.6 | 92.7 | 93.1 | 92 | 90.1 | 88.1 | 90.8 | 89 | 92.9 | 93.3 | 92.4 | 90.3 | 88.1 | 91.1 | Schneider Electric Solar Inverters USA, Inc.4.09XW4024-120/240-60 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW4548-120/240-60 | Y | N | N | 4.5 kVA, 48Vdc, 120/240 Vac, battery backup, Utility Interactive Inverter | 4.4 |  | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 26 |  |  | 100 | 53 | 58 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 89.7 | 93.5 | 94.4 | 94.1 | 93 | 91.7 | 93.2 | 88.7 | 93.3 | 94.2 | 94 | 92.9 | 91.5 | 93.1 | 88.6 | 93.2 | 94 | 93.8 | 92.6 | 91.5 | 92.9 | Schneider Electric Solar Inverters USA, Inc.4.4XW4548-120/240-60 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext TX 5000 NA [208V] | Y | N | N | 4.5 kW, 208 Vac, Grid Tie Inverter | 4.5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.98 | 4.5 | 0.98 | 100 | 300 | 480 | 0.45 | 0.9 | 1.35 | 2.25 | 3.38 | 4.5 | 93.1 | 95.8 | 96.4 | 96.4 | 95.9 | 95.2 | 95.9 | 92.5 | 95.6 | 96.2 | 96.2 | 95.8 | 95.1 | 95.7 | 91.2 | 94.7 | 95.5 | 95.7 | 95.4 | 94.8 | 95.2 | Schneider Electric Solar Inverters USA, Inc.4.5Conext TX 5000 NA [208V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW+5548-NA | Y | N | N | 4491 W, 120/240 Vac, 48 Vdc Utility Interactive Inverter with battery backup | 4.5 |  | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 17 |  |  | 100 | 52 | 58 | 0.45 | 0.9 | 1.35 | 2.25 | 3.37 | 4.49 | 92.6 | 94.6 | 94.8 | 94.4 | 93 | 91.7 | 93.5 | 91.6 | 94.6 | 94.9 | 94.4 | 93 | 91.5 | 93.4 | 92.3 | 94.3 | 94.7 | 94.2 | 92.9 | 91.6 | 93.4 | Schneider Electric Solar Inverters USA, Inc.4.5XW+5548-NA |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW+5548-NA [120V] | Y | N | N | 4492 W, 120 Vac, 48 Vdc Utility Interactive Inverter with battery backup | 4.5 | 120 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 8 |  |  | 100 | 52 | 58 | 0.45 | 0.89 | 1.34 | 2.23 | 3.34 | 4.45 | 92.2 | 94.5 | 94.5 | 94 | 92.6 | 91.3 | 93.1 | 92.2 | 94.2 | 94.4 | 93.9 | 92.6 | 91.2 | 93.1 | 92.5 | 94.1 | 94.7 | 93.7 | 92.6 | 91.1 | 93.1 | Schneider Electric Solar Inverters USA, Inc.4.5XW+5548-NA [120V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext TX 5000 NA [240V] | Y | N | N | 5.0 kW, 240 Vac, Grid Tie Inverter | 5 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.25 | 5 | 1.25 | 100 | 300 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 94.1 | 96.2 | 96.7 | 96.7 | 96.2 | 95.4 | 96.3 | 93.7 | 96 | 96.5 | 96.5 | 96.1 | 95.3 | 96.1 | 92.4 | 95.2 | 95.9 | 96 | 95.7 | 95 | 95.6 | Schneider Electric Solar Inverters USA, Inc.5Conext TX 5000 NA [240V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW6048-120-60 [120V] | Y | N | N | 6 kVA, 120Vac, 48 Vdc Utility Interactive Inverter with battery backup | 5.76 | 120 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 45 |  |  | 100 | 52 | 58 | 0.58 | 1.15 | 1.73 | 2.88 | 4.32 | 5.76 | 90 | 93.9 | 94.1 | 93.6 | 92 | 90.4 | 92.5 | 89.8 | 93.7 | 94 | 93.5 | 91.8 | 90.3 | 92.4 | 89.5 | 93.5 | 93.8 | 93.3 | 91.8 | 90.2 | 92.2 | Schneider Electric Solar Inverters USA, Inc.5.76XW6048-120-60 [120V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW+6848-NA | Y | N | N | 6000 W, 120Vac/240 Vac, 48 Vdc Utility Interactive Inverter with battery backup | 5.8 |  | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 6 |  |  | 100 | 52 | 58 | 0.58 | 1.15 | 1.73 | 2.88 | 4.31 | 5.75 | 90.6 | 93.7 | 94.1 | 93.3 | 92 | 90.5 | 92.5 | 90 | 93.5 | 93.9 | 93.3 | 91.9 | 90.3 | 92.3 | 89.8 | 93.5 | 93.7 | 93.2 | 91.7 | 90.1 | 92.2 | Schneider Electric Solar Inverters USA, Inc.5.8XW+6848-NA |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW+6848-NA [120V] | Y | N | N | 5751 W, 120 Vac, 48 Vdc Utility Interactive Inverter with battery backup | 6 | 120 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 100 | 52 | 58 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 91.5 | 94 | 94.3 | 93.6 | 92.1 | 90 | 92.7 | 91.3 | 93.9 | 94.2 | 93.5 | 91.9 | 89.8 | 92.5 | 91.3 | 93.8 | 93.9 | 93.3 | 91.7 | 89.7 | 92.3 | Schneider Electric Solar Inverters USA, Inc.6XW+6848-NA [120V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | XW6048-120/240 | Y | N | N | 6 kVA, 120/240 Vac, 48 Vdc Utility Interactive Inverter with battery backup | 6 |  | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 26 |  |  | 100 | 52 | 58 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 91.4 | 94.1 | 94.2 | 93.5 | 91.6 | 89.8 | 92.3 | 90.8 | 94 | 94.2 | 93.5 | 91.9 | 89.7 | 92.5 | 90.7 | 93.9 | 94 | 93.4 | 91.8 | 89.6 | 92.3 | Schneider Electric Solar Inverters USA, Inc.6XW6048-120/240 |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext CL 18000NA | Y | N | N | 18 kW, 422-528 Vac, 3-phase Utility Interactive Inverter | 18.2 | 422-528 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.2 |  |  | 300 | 670 | 800 | 1.82 | 3.64 | 5.46 | 9.1 | 13.65 | 18.2 | 92.5 | 95.1 | 95.8 | 95.9 | 96.2 | 96.2 | 95.9 | 95.3 | 97.1 | 97.6 | 97.7 | 97.8 | 97.8 | 97.6 | 95.8 | 97.4 | 97.9 | 98.2 | 98.2 | 98.2 | 98 | Schneider Electric Solar Inverters USA, Inc.18.2Conext CL 18000NA |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext CL 25000NA | Y | N | N | 25 kW, 422-528 Vac, 3-phase Utility Interactive Inverter | 25 | 422-528 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.2 |  |  | 500 | 720 | 800 | 2.5 | 5 | 7.5 | 12.5 | 18.75 | 25 | 94.8 | 96.5 | 96.8 | 97 | 97.1 | 97.1 | 96.9 | 97.9 | 98.1 | 98.3 | 98.4 | 98.3 | 98.1 | 98.3 | 96.7 | 97.8 | 98.6 | 98.2 | 98.2 | 98 | 98.1 | Schneider Electric Solar Inverters USA, Inc.25Conext CL 25000NA |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT30-208 [208V] | Y | N | N | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter | 28.8 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 14.4 |  |  | 180 | 221 | 344 | 2.88 | 5.76 | 8.64 | 14.4 | 21.6 | 28.8 | 96 | 96.9 | 96.9 | 96.8 | 96.3 | 95.7 | 96.5 | 95 | 96.3 | 96.5 | 96.4 | 95.9 | 95.3 | 96 | 91.3 | 94.3 | 95.1 | 95.3 | 95.1 | 94.5 | 94.9 | Schneider Electric Solar Inverters USA, Inc.28.8GT30-208 [208V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext CL-60A | Y | N | N | 60 kW Utility Interactive Inverter | 60.391 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.55 |  |  | 550 | 612.5 | 800 | 6.04 | 12.08 | 18.12 | 30.2 | 45.29 | 60.39 | 98.1 | 98.6 | 98.6 | 98.6 | 98.4 | 98.2 | 98.4 | 97.6 | 98.2 | 98.6 | 98.4 | 98.2 | 97.9 | 98.2 | 96.7 | 97.6 | 97.9 | 98 | 97.8 | 97.4 | 97.8 | Schneider Electric Solar Inverters USA, Inc.60.391Conext CL-60A | 2017-05 | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT100-208 [208V] | Y | N | N | 100 kW, 208 Vac 3-phase Utility Interactive Inverter | 100 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 95 | 100 | 95 | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.8 | 94.6 | 95.5 | 96.2 | 96.2 | 95.9 | 95.8 | 89.7 | 93.9 | 94.9 | 95.7 | 95.7 | 95.5 | 95.3 | 86.8 | 92.2 | 93.6 | 94.7 | 94.9 | 94.9 | 94.3 | Schneider Electric Solar Inverters USA, Inc.100GT100-208 [208V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT100-208-PG [208V] | Y | N | N | 100 kW, 208 Vac, 3-phase Utility Interactive Inverter, positive ground | 100 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 95 | 100 | 95 | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 90.8 | 94.6 | 95.5 | 96.2 | 96.2 | 95.9 | 95.8 | 89.7 | 93.9 | 94.9 | 95.7 | 95.7 | 95.5 | 95.3 | 86.8 | 92.2 | 93.6 | 94.7 | 94.9 | 94.9 | 94.3 | Schneider Electric Solar Inverters USA, Inc.100GT100-208-PG [208V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT100-480 [480V] | Y | N | N | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter | 100 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 92 | 100 | 92 | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 92.4 | 95.4 | 96.3 | 96.7 | 96.7 | 96.4 | 96.4 | 91.5 | 94.8 | 95.8 | 96.3 | 96.3 | 95.9 | 96 | 88.8 | 93.4 | 94.7 | 95.5 | 95.7 | 95.2 | 95.1 | Schneider Electric Solar Inverters USA, Inc.100GT100-480 [480V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT100-480-PG [480V] | Y | N | N | 100 kW, 480 Vac, 3-phase Utility Interactive Inverter, positive ground | 100 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 92 | 100 | 92 | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 92.4 | 95.4 | 96.3 | 96.7 | 96.7 | 96.4 | 96.4 | 91.5 | 94.8 | 95.8 | 96.3 | 96.3 | 95.9 | 96 | 88.8 | 93.4 | 94.7 | 95.5 | 95.7 | 95.2 | 95.1 | Schneider Electric Solar Inverters USA, Inc.100GT100-480-PG [480V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext CL125 [600V] | N | Y | Y | 125 kW, 600Vac, 3-phase Gird Support Utility Interactive Inverter with the advanced power conversion technology IGBT to convert the DC power normally from the photovoltaic array to stable three-phase AC power and then feed the power to the utility grid. | 125 | 600 | 98.5 | [05/31/2018] | [MDSP_CL125_V11_V01_A_05] | 2018-10-15 | N | N |  | 5.59 |  |  | 860 | 945 | 1200 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 98.5868 | 98.8265 | 98.8839 | 98.6821 | 98.446 | 98.2553 | 98.5633 | 98.2894 | 98.5842 | 98.5889 | 98.4931 | 98.3594 | 98.1067 | 98.4108 | 98.0841 | 98.4259 | 98.4773 | 98.3848 | 98.097 | 97.626 | 98.1955 | Schneider Electric Solar Inverters USA, Inc.125Conext CL125 [600V] | 2018-08-01 | 2018-10-15
Schneider Electric Solar Inverters USA, Inc. | GT250-480 [480V] | Y | N | N | 250 kW, 480 Vac, 3-phase Utility Interactive Inverter | 250 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 34 | 250 | 34 | 300 | 345 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 94 | 96.2 | 96.8 | 96.8 | 96.5 | 95.9 | 96.5 | 93.4 | 95.6 | 96.3 | 96.4 | 96.1 | 95.5 | 96 | 91.6 | 94.6 | 95.4 | 95.7 | 95.5 | 94.9 | 95.3 | Schneider Electric Solar Inverters USA, Inc.250GT250-480 [480V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT250-480-PG [480V] | Y | N | N | 250 kW, 480 Vac, 3-phase Utility Interactive Inverter, positive ground | 250 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 34 | 250 | 34 | 300 | 345 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 94 | 96.2 | 96.8 | 96.8 | 96.5 | 95.9 | 96.5 | 93.4 | 95.6 | 96.3 | 96.4 | 96.1 | 95.5 | 96 | 91.6 | 94.6 | 95.4 | 95.7 | 95.5 | 94.9 | 95.3 | Schneider Electric Solar Inverters USA, Inc.250GT250-480-PG [480V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT500-480 [480V] | Y | N | N | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 500 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 335.8 | 500 | 335.8 | 310 | 353 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.8 | 96.5 | 96.9 | 96.9 | 96.7 | 96.2 | 96.6 | 92.9 | 95.9 | 96.5 | 96.6 | 96.3 | 95.9 | 96.2 | 90 | 94.5 | 95.5 | 95.9 | 95.8 | 95.4 | 95.5 | Schneider Electric Solar Inverters USA, Inc.500GT500-480 [480V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT500-480-PG [480V] | Y | N | N | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter, positive ground | 500 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 335.8 | 500 | 335.8 | 310 | 353 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.8 | 96.5 | 96.9 | 96.9 | 96.7 | 96.2 | 96.6 | 92.9 | 95.9 | 96.5 | 96.6 | 96.3 | 95.9 | 96.2 | 90 | 94.5 | 95.5 | 95.9 | 95.8 | 95.4 | 95.5 | Schneider Electric Solar Inverters USA, Inc.500GT500-480-PG [480V] |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | GT500-MVX | Y | N | N | 500 kW, 3-phase Inverter for medium voltage applications | 500 |  | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Weighted Efficiency includes MV TP1 Transformer efficiency. | 161 |  |  | 310 | 354 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.7 | 96.3 | 96.7 | 96.7 | 96.1 | 94.9 | 96.2 | 93 | 95.8 | 96.3 | 96.4 | 95.9 | 94.6 | 95.8 | 90 | 94.5 | 95.4 | 95.7 | 95.3 | 94.1 | 95.1 | Schneider Electric Solar Inverters USA, Inc.500GT500-MVX |  | 2018-06-01
Schneider Electric Solar Inverters USA, Inc. | GT500-MVX-PG | Y | N | N | 500 kW, 3-phase Inverter for medium voltage applications, positive ground | 500 |  | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Weighted Efficiency includes MV TP1 Transformer efficiency. | 161 |  |  | 310 | 354 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 93.7 | 96.3 | 96.7 | 96.7 | 96.1 | 94.9 | 96.2 | 93 | 95.8 | 96.3 | 96.4 | 95.9 | 94.6 | 95.8 | 90 | 94.5 | 95.4 | 95.7 | 95.3 | 94.1 | 95.1 | Schneider Electric Solar Inverters USA, Inc.500GT500-MVX-PG |  | 2018-06-01
Schneider Electric Solar Inverters USA, Inc. | Conext Core XC540-NA | Y | N | N | Utility Interactive Photovoltaic Inverter to be used with ABB EcoDry Ultra Transformer | 540 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 196 |  |  | 439 | 529 | 800 | 54 | 108 | 162 | 270 | 405 | 540 | 95.4828 | 97.3332 | 97.7081 | 97.7999 | 97.6167 | 96.8773 | 97.5296 | 95.4218 | 97.0344 | 97.4169 | 97.4748 | 97.285 | 96.6512 | 97.2219 | 93.463 | 96.0098 | 96.6481 | 96.8949 | 96.7092 | 96.0827 | 96.5447 | Schneider Electric Solar Inverters USA, Inc.540Conext Core XC540-NA |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext Core XC630-NA | Y | N | N | Utility Interactive Photovoltaic Inverter to be used with ABB EcoDry Ultra Transformer | 630 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 200 |  |  | 510 | 582 | 800 | 63 | 126 | 189 | 315 | 472.5 | 630 | 95.5924 | 97.6798 | 97.9802 | 97.9365 | 97.8207 | 97.1378 | 97.7339 | 95.944 | 97.5335 | 97.7412 | 97.738 | 97.4997 | 96.8007 | 97.4832 | 94.3888 | 96.6615 | 97.1405 | 97.2963 | 97.0892 | 96.412 | 96.9756 | Schneider Electric Solar Inverters USA, Inc.630Conext Core XC630-NA |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext Core XC680-NA | Y | N | N | Utility Interactive Photovoltaic Inverter to be used with ABB EcoDry Ultra Transformer | 680 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 203 |  |  | 552 | 614 | 800 | 68 | 136 | 204 | 340 | 510 | 680 | 96.7326 | 97.5927 | 98.0772 | 98.1669 | 97.8751 | 97.5268 | 97.8834 | 96.2312 | 97.4394 | 97.7416 | 97.8243 | 97.6143 | 97.1701 | 97.5874 | 94.9986 | 96.6345 | 97.1536 | 97.4238 | 97.2347 | 96.8261 | 97.1248 | Schneider Electric Solar Inverters USA, Inc.680Conext Core XC680-NA |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | Conext Core XC733-NA | Y | N | N | Utility Interactive Photovoltaic Inverter to be used with ABB EcoDry Ultra Transformer | 730.9 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 203 |  |  | 591 | 644 | 800 | 73.09 | 146.18 | 219.27 | 365.45 | 548.175 | 730.9 | 96.0765 | 97.8522 | 98.1843 | 98.2455 | 98.0218 | 97.5302 | 97.9774 | 95.721 | 97.5881 | 97.9165 | 97.997 | 97.7627 | 97.2498 | 97.7143 | 94.9928 | 97.1688 | 97.6099 | 97.7279 | 97.5155 | 97.0024 | 97.4276 | Schneider Electric Solar Inverters USA, Inc.730.9Conext Core XC733-NA |  | 2018-05-01
Schneider Electric Solar Inverters USA, Inc. | CS1666-1-NA [575V] | Y | Y | Y | 1.66 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter with 1666 kVA Maximum Output Continuous Apparent Power | 1666 | 575 | 98 | [07/01/2018] | [SG_ICB_MCU_R10.6-7] | 2018-10-15 | N | N | Weighted Efficiency includes efficiency of 2.0 MVA Square D 3PH distribution transformer, liquid-filled type. | 295 |  |  | 856 | 1024 | 1200 | 167 | 333 | 500 | 833 | 1250 | 1666 | 96.79 | 97.94 | 98.09 | 98.15 | 97.94 | 97.66 | 97.9 | 96.33 | 97.56 | 97.92 | 98.08 | 97.88 | 97.52 | 97.8 | 95.68 | 97.45 | 97.7 | 97.9 | 97.74 | 97.44 | 97.7 | Schneider Electric Solar Inverters USA, Inc.1666CS1666-1-NA [575V] | 2018-08-15 | 2018-10-15
Schneider Electric Solar Inverters USA, Inc. | CS1666-2-NA [575V] | Y | Y | Y | 1.66 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter with 1831 kVA Maximum Output Continuous Apparent Power | 1666 | 575 | 98 | [07/01/2018] | [SG_ICB_MCU_R10.6-7] | 2018-10-15 | N | N | Weighted Efficiency includes efficiency of 2.0 MVA Square D 3PH distribution transformer, liquid-filled type. | 295 |  |  | 856 | 1024 | 1200 | 167 | 333 | 500 | 833 | 1250 | 1666 | 96.79 | 97.94 | 98.09 | 98.15 | 97.94 | 97.66 | 97.9 | 96.33 | 97.56 | 97.92 | 98.08 | 97.88 | 97.52 | 97.8 | 95.68 | 97.45 | 97.7 | 97.9 | 97.74 | 97.44 | 97.7 | Schneider Electric Solar Inverters USA, Inc.1666CS1666-2-NA [575V] | 2018-08-15 | 2018-10-15
Schneider Electric Solar Inverters USA, Inc. | CS1666-3-NA [575V] | Y | Y | Y | 1.66 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter with 1851 kVA Maximum Output Continuous Apparent Power | 1666 | 575 | 98 | [07/01/2018] | [SG_ICB_MCU_R10.6-7] | 2018-10-15 | N | N | Weighted Efficiency includes efficiency of 2.0 MVA Square D 3PH distribution transformer, liquid-filled type. | 295 |  |  | 856 | 1024 | 1200 | 167 | 333 | 500 | 833 | 1250 | 1666 | 96.79 | 97.94 | 98.09 | 98.15 | 97.94 | 97.66 | 97.9 | 96.33 | 97.56 | 97.92 | 98.08 | 97.88 | 97.52 | 97.8 | 95.68 | 97.45 | 97.7 | 97.9 | 97.74 | 97.44 | 97.7 | Schneider Electric Solar Inverters USA, Inc.1666CS1666-3-NA [575V] | 2018-08-15 | 2018-10-15
Schneider Electric Solar Inverters USA, Inc. | CS1800-NA [575V] | Y | Y | Y | 1.8 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter | 1800 | 575 | 98 | [07/01/2018] | [SG_ICB_MCU_R10.6-7] | 2018-10-15 | N | N | Weighted Efficiency includes efficiency of 2.0 MVA Square D 3PH distribution transformer, liquid-filled type. | 295 |  |  | 856 | 1024 | 1200 | 180 | 360 | 540 | 900 | 1350 | 1800 | 96.89 | 97.93 | 98.08 | 98.11 | 97.92 | 97.47 | 97.9 | 96.67 | 97.74 | 98 | 97.99 | 97.8 | 97.45 | 97.8 | 95.89 | 97.43 | 97.67 | 97.87 | 97.7 | 97.34 | 97.6 | Schneider Electric Solar Inverters USA, Inc.1800CS1800-NA [575V] | 2018-08-15 | 2018-10-15
Schneider Electric Solar Inverters USA, Inc. | CS2000-NA [575V] | Y | Y | Y | 2 MW, 1500 Vdc, 575 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter | 2000 | 575 | 97.5 | [07/01/2018] | [SG_ICB_MCU_R10.6-7] | 2018-10-15 | N | N | Formerly Schneider Electric Solar Inverters USA, Inc. Conext SmartGen CS2000-NA. Weighted Efficiency includes efficiency of 2000 KVA Square D 3PH distribution transformer, liquid-filled type (40425642-006-S09-01). | 295 |  |  | 865 | 1042 | 1195 | 200 | 400 | 600 | 1000 | 1500 | 2000 | 96.76 | 97.71 | 97.98 | 97.96 | 97.66 | 97.21 | 97.71 | 96.32 | 97.58 | 97.87 | 97.83 | 97.56 | 97.15 | 97.58 | 95.92 | 97.38 | 97.69 | 97.72 | 97.5 | 97.06 | 97.48 | Schneider Electric Solar Inverters USA, Inc.2000CS2000-NA [575V] | 2018-08-15 | 2018-10-15
Schneider Electric Solar Inverters USA, Inc. | CS2200-NA [600V] | Y | Y | Y | 2.2 MW, 1500 Vdc, 600 Vac, 3-phase, Special Purpose Grid Support Utility Interactive PV Inverter | 2200 | 600 | 98 | [07/01/2018] | [SG_ICB_MCU_R10.6-7] | 2018-10-15 | N | N | Weighted Efficiency includes efficiency of 2.5 MVA Square D 3PH distribution transformer, liquid-filled type. | 295 |  |  | 905 | 1054 | 1200 | 220 | 440 | 660 | 1100 | 1650 | 2200 | 97.9 | 98.28 | 98.33 | 98.2 | 97.82 | 97.24 | 98 | 97.6 | 98.1 | 98.19 | 98.09 | 97.72 | 97.17 | 97.8 | 97.21 | 97.9 | 98.05 | 97.99 | 97.65 | 97.1 | 97.7 | Schneider Electric Solar Inverters USA, Inc.2200CS2200-NA [600V] | 2018-08-15 | 2018-10-15
Schneider Electric Solar Inverters USA, Inc. | CS2400-NA [600V] | Y | N | N | 2.2 MW, 2.4 MVA, 1500Vdc, 600Vac, 3-ph Special Purpose Utility Interactive PV Inverter | 2200 | 600 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Weighted Efficiency includes efficiency of 2.5 MVA Square D 3PH distribution transformer, liquid-filled type. | 295 |  |  | 900 | 1054 | 1200 | 220 | 440 | 660 | 1100 | 1650 | 2200 | 97.4147 | 98.1198 | 98.251 | 98.2091 | 97.9143 | 97.4561 | 97.984 | 97.4181 | 98.0355 | 98.1755 | 98.1244 | 97.8109 | 97.3036 | 97.8907 | 97.0277 | 97.8316 | 98.0273 | 98.0302 | 97.7384 | 97.2377 | 97.7855 | Schneider Electric Solar Inverters USA, Inc.2200CS2400-NA [600V] | 2018-11-01
Schuco USA | SB700U [120V] | Y | N | N | 700W, 120Vac Sunny Boy String Inverter | 0.7 | 120 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.0357 |  |  | 100 | 145 | 200 | 0.07 | 0.14 | 0.21 | 0.35 | 0.53 | 0.7 | 87.17 | 91.46 | 92.68 | 92.98 | 92.42 | 91.45 | 92.26 | 86.53 | 91.26 | 92.47 | 92.32 | 91.44 | 90.36 | 91.49 | 84.83 | 90.18 | 91.07 | 91.63 | 91.03 | 90.2 | 90.83 | Schuco USA0.7SB700U [120V]
Schuco USA | SB700U-SBD [120V] | Y | N | N | 700W, 120Vac Sunny Boy String Inverter with display | 0.7 | 120 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.0357 |  |  | 100 | 145 | 200 | 0.07 | 0.14 | 0.21 | 0.35 | 0.53 | 0.7 | 87.17 | 91.46 | 92.68 | 92.98 | 92.42 | 91.45 | 92.26 | 86.53 | 91.26 | 92.47 | 92.32 | 91.44 | 90.36 | 91.49 | 84.83 | 90.18 | 91.07 | 91.63 | 91.03 | 90.2 | 90.83 | Schuco USA0.7SB700U-SBD [120V]
Schuco USA | SWR1800U [120V] | Y | N | N | 1.8kW, 120Vac Sunny Boy String Inverter | 1.8 | 120 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2659 |  |  | 100 | 200 | 400 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 89.82 | 92.39 | 93.01 | 92.83 | 91.99 | 91 | 92.17 | 89.56 | 92.12 | 92.82 | 92.7 | 91.72 | 90.8 | 91.95 | 86.79 | 90.45 | 91.44 | 91.78 | 91.18 | 90.3 | 91.08 | Schuco USA1.8SWR1800U [120V]
Schuco USA | SWR1800U-SBD [120V] | Y | N | N | 1.8kW, 120Vac Sunny Boy String Inverter with display | 1.8 | 120 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2659 |  |  | 100 | 200 | 400 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 89.82 | 92.39 | 93.01 | 92.83 | 91.99 | 91 | 92.17 | 89.56 | 92.12 | 92.82 | 92.7 | 91.72 | 90.8 | 91.95 | 86.79 | 90.45 | 91.44 | 91.78 | 91.18 | 90.3 | 91.08 | Schuco USA1.8SWR1800U-SBD [120V]
Schuco USA | SWR2100U [240V] | Y | N | N | 2.1kW, 240 Vac Sunny Boy String Inverter | 2.1 | 240 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 100 | 300 | 480 | 0.21 | 0.42 | 0.63 | 1.05 | 1.575 | 2.1 | 91.2 | 93.6 | 94.3 | 94.3 | 93.9 | 93.3 | 93.9 | 90.2 | 92.7 | 93.5 | 94.5 | 93.7 | 93.1 | 93.6 | 86 | 89.9 | 91.3 | 92.1 | 92.3 | 91.8 | 91.8 | Schuco USA2.1SWR2100U [240V]
Schuco USA | SWR2500U [208V] | Y | N | N | 2.1kW, 208 Vac Sunny Boy String Inverter, with display | 2.1 | 208 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.236 |  |  | 100 | 300 | 480 | 0.21 | 0.42 | 0.63 | 1.05 | 1.58 | 2.1 | 90.86 | 93.44 | 94.02 | 93.86 | 93.06 | 92.06 | 93.22 | 89.33 | 92.49 | 93.07 | 93.3 | 92.57 | 91.52 | 92.6 | 85.59 | 89.83 | 91.11 | 91.75 | 91.25 | 90.64 | 91.01 | Schuco USA2.1SWR2500U [208V]
Schuco USA | SWR2500U-SBD [208V] | Y | N | N | 2.1kW, 208 Vac Sunny Boy String Inverter with display | 2.1 | 208 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.236 |  |  | 100 | 300 | 480 | 0.21 | 0.42 | 0.63 | 1.05 | 1.58 | 2.1 | 90.86 | 93.44 | 94.02 | 93.86 | 93.06 | 92.06 | 93.22 | 89.33 | 92.49 | 93.07 | 93.3 | 92.57 | 91.52 | 92.6 | 85.59 | 89.83 | 91.11 | 91.75 | 91.25 | 90.64 | 91.01 | Schuco USA2.1SWR2500U-SBD [208V]
Schuco USA | SWR2500U [240V] | Y | N | N | 2.5 kW, 240 Vac Sunny Boy String Inverter | 2.5 | 240 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.318 |  |  | 100 | 300 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 91.03 | 93.93 | 94.57 | 94.53 | 93.9 | 93.26 | 93.97 | 89.79 | 93.21 | 93.89 | 94.15 | 93.66 | 92.89 | 93.57 | 86.28 | 90.48 | 91.91 | 92.59 | 92.33 | 91.84 | 91.98 | Schuco USA2.5SWR2500U [240V]
Schuco USA | SWR2500U-SBD [240V] | Y | N | N | 2.5 kW, 240 Vac Sunny Boy String Inverter with display | 2.5 | 240 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.318 |  |  | 100 | 300 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 91.03 | 93.93 | 94.57 | 94.53 | 93.9 | 93.26 | 93.97 | 89.79 | 93.21 | 93.89 | 94.15 | 93.66 | 92.89 | 93.57 | 86.28 | 90.48 | 91.91 | 92.59 | 92.33 | 91.84 | 91.98 | Schuco USA2.5SWR2500U-SBD [240V]
Schuco USA | SB3000US [208V] | Y | N | N | 3 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 3 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 100 | 250 | 400 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 94 | 95.8 | 96 | 95.8 | 95.1 | 94.3 | 95.3 | 93.1 | 95.9 | 95.7 | 95.6 | 94.9 | 94 | 95.1 | 91.6 | 94.8 | 95.2 | 94.7 | 94.2 | 93.5 | 94.3 | Schuco USA3SB3000US [208V]
Schuco USA | SB3000US [240V] | Y | N | N | 3 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 3 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 250 | 400 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.4 | 95.9 | 96.3 | 96.5 | 96.1 | 95.6 | 96 | 92.5 | 95.8 | 96 | 96.1 | 95.8 | 95.1 | 95.7 | 90.5 | 94.6 | 95.4 | 95.3 | 95.2 | 94.6 | 95 | Schuco USA3SB3000US [240V]
Schuco USA | SB3300U [240V] | Y | N | N | 3.3 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 3.3 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.16 |  |  | 100 | 250 | 400 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92.6 | 94.6 | 95.2 | 95.4 | 95.2 | 94.6 | 95.1 | 91.8 | 94.1 | 94.8 | 95.1 | 94.9 | 94.5 | 94.7 | 89.2 | 92.4 | 93.6 | 94 | 93.9 | 93.5 | 93.6 | Schuco USA3.3SB3300U [240V]
Schuco USA | SB3800U [208V] | Y | N | N | 3.5 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 3.5 | 208 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.16 |  |  | 100 | 235 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 93.6 | 94.9 | 95.2 | 94.9 | 94.1 | 93.3 | 94.4 | 92.8 | 94.5 | 94.8 | 94.6 | 94 | 93 | 94.1 | 90.3 | 92.7 | 93.4 | 93.5 | 93.1 | 92.2 | 93 | Schuco USA3.5SB3800U [208V]
Schuco USA | SB4000US [208V] | Y | N | N | 4 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 3.5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 310 | 480 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 94.3 | 96.3 | 96.5 | 96.4 | 95.8 | 94.9 | 95.9 | 93.5 | 96.2 | 96.1 | 96.1 | 95.5 | 94.8 | 95.6 | 91.5 | 94.9 | 95.4 | 95.1 | 94.8 | 94 | 94.7 | Schuco USA3.5SB4000US [208V]
Schuco USA | SB3800U [240V] | Y | N | N | 3.8kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 3.8 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.16 |  |  | 100 | 250 | 400 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93.3 | 95 | 95.5 | 95.4 | 95 | 94.3 | 95 | 92.8 | 94.6 | 95.1 | 95.1 | 94.7 | 93.8 | 94.7 | 90.2 | 93 | 93.9 | 94.1 | 93.8 | 93.2 | 93.7 | Schuco USA3.8SB3800U [240V]
Schuco USA | SB4000US [240V] | Y | N | N | 4 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 4 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.17 |  |  | 100 | 310 | 480 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 92.5 | 96.4 | 96.8 | 96.7 | 96.4 | 96 | 96.3 | 91.9 | 96.2 | 96.3 | 96.5 | 96 | 95.5 | 96 | 89.1 | 94.7 | 95.6 | 95.5 | 95.3 | 94.9 | 95.1 | Schuco USA4SB4000US [240V]
Schuco USA | SB5000US [208V] | Y | N | N | 5 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.7 | 96.2 | 96.7 | 96.7 | 96.3 | 96.4 | 89.9 | 95 | 95.7 | 96.2 | 96.4 | 96 | 95.9 | 86.3 | 92.5 | 94.3 | 95 | 95.1 | 95 | 94.5 | Schuco USA5SB5000US [208V]
Schuco USA | SB5000US [240V] | Y | N | N | 5 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91 | 95.7 | 96.2 | 96.8 | 96.8 | 96.5 | 96.4 | 89.7 | 94.9 | 95.7 | 96.2 | 96.4 | 96.2 | 95.9 | 86.2 | 92.5 | 94.3 | 95.2 | 95.2 | 95.1 | 94.6 | Schuco USA5SB5000US [240V]
Schuco USA | SB5000US [277V] | Y | N | N | 5 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.8 | 96.5 | 96.8 | 96.5 | 96.6 | 96.3 | 90 | 95 | 95.8 | 96.2 | 96.5 | 96.2 | 96 | 86.3 | 92.3 | 94.4 | 95.2 | 95.2 | 95.2 | 94.6 | Schuco USA5SB5000US [277V]
Schuco USA | SB6000U [208V] | Y | N | N | Sunny Boy 6000 Watt (208V) Utility Interactive Inverter with Meter | 5.2 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 334 | 480 | 0.57 | 1.11 | 1.63 | 2.7 | 4.01 | 5.32 | 93.1 | 95.2 | 95.6 | 95.6 | 94.8 | 94.2 | 95 | 91.6 | 94.7 | 95.2 | 95.3 | 94.6 | 93.8 | 94.7 | 88.6 | 92.3 | 93.5 | 93.9 | 93.7 | 93.1 | 93.4 | Schuco USA5.2SB6000U [208V]
Schuco USA | SB6000U [240V] | Y | N | N | Sunny Boy 6000 Watt (240V) Utility Interactive Inverter with Meter | 6 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.2 | 95.5 | 95.8 | 95.5 | 94.9 | 94.2 | 95 | 92.3 | 94.9 | 95.2 | 95.2 | 94.6 | 93.8 | 94.7 | 90.1 | 93.3 | 94.1 | 94.3 | 93.9 | 93.2 | 93.8 | Schuco USA6SB6000U [240V]
Schuco USA | SB6000U [277V] | Y | N | N | Sunny Boy 6000 Watt (277V) Utility Interactive Inverter with Meter | 6 | 277 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.23 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.1 | 95.2 | 95.9 | 95.6 | 95.2 | 94.5 | 95.2 | 91.9 | 94.8 | 95.4 | 95.2 | 94.8 | 94.2 | 94.8 | 89.8 | 93.2 | 94.1 | 94.4 | 94 | 93.4 | 93.9 | Schuco USA6SB6000U [277V]
Schuco USA | SB6000US [208V] | Y | N | N | 6 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.8 | 96.5 | 96.9 | 96.5 | 95.9 | 96.3 | 91.2 | 95.6 | 95.9 | 96.3 | 96.1 | 95.6 | 95.9 | 88 | 93.5 | 94.8 | 94.6 | 94.9 | 94.6 | 94.5 | Schuco USA6SB6000US [208V]
Schuco USA | SB6000US [240V] | Y | N | N | 6 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 96.1 | 96.5 | 96.8 | 96.7 | 96 | 96.4 | 91.3 | 95.6 | 96 | 96.3 | 96.3 | 95.9 | 96 | 87.9 | 93.6 | 94.8 | 95.1 | 95 | 94.8 | 94.7 | Schuco USA6SB6000US [240V]
Schuco USA | SB6000US [277V] | Y | N | N | 6 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.3 | 96 | 96.7 | 97 | 96.7 | 96.5 | 96.5 | 91.3 | 95.6 | 96.2 | 96.4 | 96.4 | 96 | 96.1 | 87.8 | 93.6 | 94.9 | 95.2 | 95.1 | 94.9 | 94.7 | Schuco USA6SB6000US [277V]
Schuco USA | SB7000US [208V] | Y | N | N | 7 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 94 | 96.3 | 97.1 | 96.7 | 96.2 | 95.4 | 96.3 | 92.7 | 96.1 | 96.1 | 96.2 | 95.9 | 95.3 | 95.9 | 89.7 | 94.2 | 95 | 94.9 | 94.8 | 94.1 | 94.6 | Schuco USA7SB7000US [208V]
Schuco USA | SB7000US [240V] | Y | N | N | 7 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.2 | 96.8 | 96.9 | 96.5 | 95.8 | 96.5 | 92.3 | 96.1 | 96.1 | 96.4 | 96.1 | 95.6 | 96 | 89.3 | 94.3 | 95.1 | 95.6 | 95 | 94.7 | 94.8 | Schuco USA7SB7000US [240V]
Schuco USA | SB7000US [277V] | Y | N | N | 7 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.3 | 96.8 | 97 | 96.5 | 95.9 | 96.5 | 92.5 | 96.1 | 96.3 | 96.5 | 96.2 | 95.6 | 96.1 | 89.3 | 94.2 | 95.2 | 95 | 95.1 | 94.6 | 94.8 | Schuco USA7SB7000US [277V]
Schuco USA | SB8000US [240V] | Y | N | N | 8kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 7.6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.17 |  |  | 100 | 345 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.04 | 96.48 | 96.84 | 96.82 | 96.5 | 96.01 | 96.53 | 94.59 | 96.19 | 96.61 | 96.63 | 96.3 | 96.29 | 96.33 | 93.13 | 95.28 | 95.83 | 95.98 | 95.72 | 95.94 | 95.67 | Schuco USA7.6SB8000US [240V]
Schuco USA | SB8000US [277V] | Y | N | N | 8kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 |  |  | 100 | 345 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.12 | 96.22 | 96.48 | 96.46 | 96.17 | 95.56 | 96.2 | 94.85 | 95.86 | 96.28 | 96.25 | 95.89 | 95.28 | 95.93 | 93.45 | 95.01 | 95.41 | 95.51 | 95.24 | 94.7 | 95.21 | Schuco USA8SB8000US [277V]
Schuco USA | ST42 [208V] | Y | N | N | 42 kW, 208 Vac Sunny Tower Utility Interactive Inverter with display | 42 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 250 | 310 | 480 | 4.2 | 8.4 | 12.6 | 21 | 31.5 | 42 | 94 | 96.3 | 97.1 | 96.7 | 96.2 | 95.4 | 96.3 | 92.7 | 96.1 | 96.1 | 96.2 | 95.9 | 95.3 | 95.9 | 89.7 | 94.2 | 95 | 94.9 | 94.8 | 94.1 | 94.6 | Schuco USA42ST42 [208V]
Schuco USA | ST42 [277V] | Y | N | N | 42 kW, 277 Vac Sunny Tower Utility Interactive Inverter with display | 42 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 250 | 310 | 480 | 4.2 | 8.4 | 12.6 | 21 | 31.5 | 42 | 93.7 | 96.3 | 96.8 | 97 | 96.5 | 95.9 | 96.5 | 92.5 | 96.1 | 96.3 | 96.5 | 96.2 | 95.6 | 96.1 | 89.3 | 94.2 | 95.2 | 95 | 95.1 | 94.6 | 94.8 | Schuco USA42ST42 [277V]
Sharp | JH-3500U [240V] | Y | N | N | Utility Interactive Inverter 240 Vac L-L, 3.5 kW | 3.5 | 240 | 91 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.65 |  |  | 100 | 276 | 304 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 75 | 83.1 | 87.1 | 90.3 | 91.5 | 92 | 89.7 | 80.9 | 87.8 | 90.6 | 91.7 | 92.6 | 92.4 | 91.5 | 83.3 | 87.8 | 90.7 | 92.2 | 92.7 | 92.7 | 91.7 | Sharp3.5JH-3500U [240V]
Shenzhen BYD | BSG5000-U [240V] | Y | N | N | 4.9 kW 240 Vac Utility Interactive Inverter | 4.88 | 240 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 1.75 |  |  | 100 | 400 | 550 | 0.49 | 0.98 | 1.46 | 2.44 | 3.66 | 4.88 | 89.8 | 93.4 | 94 | 93.9 | 93.2 | 92.1 | 93.2 | 87.7 | 92.1 | 93.3 | 93.5 | 92.9 | 91.8 | 92.8 | 85.8 | 90.7 | 92.3 | 93 | 92.2 | 91.9 | 92.1 | Shenzhen BYD4.88BSG5000-U [240V]
Shenzhen BYD | BSG5000-U [208V] | Y | N | N | 4.9 kW 208 Vac Utility Interactive Inverter | 4.91 | 208 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 1.32 |  |  | 100 | 400 | 550 | 0.49 | 0.98 | 1.47 | 2.46 | 3.69 | 4.91 | 89.8 | 93.1 | 93.9 | 93.6 | 92.8 | 91.6 | 92.9 | 87 | 91.8 | 93 | 93.3 | 92.6 | 91.5 | 92.4 | 84.4 | 91 | 92 | 92.6 | 92.1 | 91 | 91.8 | Shenzhen BYD4.91BSG5000-U [208V]
Shenzhen BYD | BSG250K-U | Y | N | N | 250 kW Utility Interactive Inverter | 250.4 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 151 |  |  | 330 | 370 | 480 | 25.04 | 50.07 | 75.11 | 125.2 | 187.8 | 250.4 | 90.1 | 94.4 | 95.5 | 96.4 | 95.7 | 95.3 | 95.5 | 89.1 | 93.9 | 95.1 | 95.6 | 95.9 | 95.7 | 95.4 | 87.1 | 92.6 | 94.2 | 94.8 | 95.3 | 95 | 94.6 | Shenzhen BYD250.4BSG250K-U
Shenzhen BYD | BSG250K-U/N | Y | N | N | 250 kW Utility Interactive Inverter | 250.4 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 151 |  |  | 330 | 370 | 480 | 25.04 | 50.07 | 75.11 | 125.2 | 187.8 | 250.4 | 90.1 | 94.4 | 95.5 | 96.4 | 95.7 | 95.3 | 95.5 | 89.1 | 93.9 | 95.1 | 95.6 | 95.9 | 95.7 | 95.4 | 87.1 | 92.6 | 94.2 | 94.8 | 95.3 | 95 | 94.6 | Shenzhen BYD250.4BSG250K-U/N
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 4000MTLP-US [208V] | N | Y | N | 4 kW, 208 Vac Grid Support Utility Interactive Inverter | 3.62 | 208 | 95.5 | [10/13/2017] | [KA 1.0] | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.36 | 0.72 | 1.08 | 1.81 | 2.71 | 3.62 | 88.8 | 91.7 | 93.1 | 94.6 | 95.2 | 95.2 | 94.4 | 92.2 | 95.7 | 95.7 | 96.5 | 96.7 | 96.7 | 96.3 | 91.4 | 94.3 | 95.3 | 96.2 | 96.5 | 96.6 | 96 | Shenzhen Growatt New Energy Technology Co., Ltd.3.62Growatt 4000MTLP-US (208V) [SI1] | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 4000MTLP-US [240V] | N | Y | N | 4 kW, 240 Vac Grid Support Utility Interactive Inverter | 4.05 | 240 | 96 | [10/13/2017] | [KA 1.0] | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.4 | 0.81 | 1.21 | 2.02 | 3.04 | 4.05 | 89.5 | 92.1 | 93.7 | 95 | 95.5 | 95.6 | 94.8 | 93.1 | 95.4 | 96.2 | 96.9 | 97.1 | 97.1 | 96.7 | 92.3 | 94.8 | 95.9 | 96.6 | 96.9 | 97 | 96.4 | Shenzhen Growatt New Energy Technology Co., Ltd.4.05Growatt 4000MTLP-US (240V) [SI1] | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 4000MTLP-US [277V] | N | Y | N | 4 kW, 277 Vac Grid Support Utility Interactive Inverter | 4.06 | 277 | 96 | [10/13/2017] | [KA 1.0] | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.41 | 0.81 | 1.22 | 2.03 | 3.04 | 4.06 | 88.3 | 91.5 | 93.1 | 94.6 | 95.3 | 95.5 | 94.4 | 93.6 | 95.7 | 96.6 | 95.3 | 97.4 | 97.4 | 96.6 | 92.7 | 95.1 | 96.3 | 96.9 | 97.2 | 97.3 | 96.8 | Shenzhen Growatt New Energy Technology Co., Ltd.4.06Growatt 4000MTLP-US (277V) [SI1] | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 5000MTLP-US [208V] | N | Y | N | 5 kW, 208 Vac Grid Support Utility Interactive Inverter | 4.59 | 208 | 95.5 | [10/13/2017] | [KA 1.0] | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.46 | 0.92 | 1.38 | 2.3 | 3.44 | 4.59 | 89.9 | 92.5 | 93.8 | 94.9 | 95.1 | 95.1 | 94.6 | 93.2 | 95.3 | 96 | 96.6 | 96.7 | 96.6 | 96.4 | 92.5 | 94.8 | 95.7 | 96.4 | 96.6 | 96.5 | 96.2 | Shenzhen Growatt New Energy Technology Co., Ltd.4.59Growatt 5000MTLP-US (208V) [SI1] | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 5000MTLP-US [277V] | N | Y | N | 5 kW, 277 Vac Grid Support Utility Interactive Inverter | 5.06 | 277 | 96.5 | [10/13/2017] | [KA 1.0] | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.06 | 89.5 | 92.3 | 93.8 | 95 | 95.5 | 95.5 | 94.8 | 94.3 | 96.1 | 96.8 | 97.3 | 97.4 | 97.3 | 97.1 | 93.5 | 95.6 | 96.4 | 97 | 97.2 | 97.2 | 96.9 | Shenzhen Growatt New Energy Technology Co., Ltd.5.06Growatt 5000MTLP-US (277V) [SI1] | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 5000MTLP-US [240V] | N | Y | N | 5 kW, 240 Vac Grid Support Utility Interactive Inverter | 5.07 | 240 | 96 | [10/13/2017] | [KA 1.0] | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.07 | 90.5 | 93 | 94.3 | 95.2 | 95.4 | 95.3 | 94.9 | 93.9 | 95.8 | 96.5 | 97 | 97.1 | 96.9 | 96.8 | 93.1 | 95.3 | 96.1 | 96.8 | 96.9 | 96.9 | 96.6 | Shenzhen Growatt New Energy Technology Co., Ltd.5.07Growatt 5000MTLP-US (240V) [SI1] | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 6000MTLP-US [208V] | N | Y | N | 6 kW, 208 Vac Grid Support Utility Interactive Inverter | 5.34 | 208 | 96 | [10/13/2017] | [KA 1.0] | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.53 | 1.07 | 1.6 | 2.67 | 4.01 | 5.34 | 90.7 | 93.2 | 94.3 | 95 | 95 | 94.9 | 94.7 | 93.9 | 95.7 | 96.3 | 96.7 | 96.6 | 96.4 | 96.4 | 93.3 | 95.3 | 95.9 | 96.5 | 96.5 | 96.3 | 96.2 | Shenzhen Growatt New Energy Technology Co., Ltd.5.34Growatt 6000MTLP-US (208V) [SI1] | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 6000MTLP-US [240V] | N | Y | N | 6 kW, 240 Vac Grid Support Utility Interactive Inverter | 6.08 | 240 | 96 | [10/13/2017] | [KA 1.0] | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.61 | 1.22 | 1.82 | 3.04 | 4.56 | 6.08 | 91.3 | 93.6 | 94.7 | 95.4 | 95.5 | 95.6 | 95.1 | 94.6 | 96.1 | 96.7 | 97 | 97 | 96.8 | 96.8 | 93.9 | 95.6 | 96.3 | 96.8 | 96.8 | 96.7 | 96.6 | Shenzhen Growatt New Energy Technology Co., Ltd.6.08Growatt 6000MTLP-US (240V) [SI1] | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 6000MTLP-US [277V] | N | Y | N | 6 kW, 277 Vac Grid Support Utility Interactive Inverter | 6.08 | 277 | 96.5 | [10/13/2017] | [KA 1.0] | Not Applicable | Y | N |  | 0.05 |  |  | 100 | 482 | 550 | 0.61 | 1.22 | 1.82 | 3.04 | 4.56 | 6.08 | 90.4 | 93 | 94.4 | 95.3 | 95.4 | 95.3 | 94.9 | 94.9 | 96.4 | 96.9 | 97.3 | 97.4 | 97.2 | 97.2 | 94.1 | 95.9 | 96.6 | 97.1 | 97.2 | 97.1 | 96.9 | Shenzhen Growatt New Energy Technology Co., Ltd.6.08Growatt 6000MTLP-US (277V) [SI1] | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 7000MTLP-US [208V] | N | Y | N | 7 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.093 | 208 | 96 | [10/13/2017] | [KA 1.0] | Not Applicable | Y | N |  | 0.05 |  |  | 280 | 385 | 485 | 609.3 | 1218.6 | 1827.9 | 3046.5 | 4569.75 | 6093 | 93.9 | 95.4 | 95.8 | 95.9 | 95.5 | 95.3 | 95.6 | 95.4 | 96.6 | 96.8 | 96.6 | 96.1 | 95.9 | 96.3 | 94.3 | 95.9 | 96.4 | 96.5 | 96.2 | 96 | 96.2 | Shenzhen Growatt New Energy Technology Co., Ltd.6.093Growatt 7000MTLP-US (208V) [SI1] | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 7600MTLP-US [208V] | N | Y | N | 7.6 kW, 208 Vac Grid Support Utility Interactive Inverter | 6.741 | 208 | 96 | [10/13/2017] | [KA 1.0] | Not Applicable | Y | N |  | 0.05 |  |  | 270 | 380 | 480 | 674.1 | 1348.2 | 2022.3 | 3370.51 | 5055.76 | 6741.01 | 94.1 | 95.5 | 95.7 | 95.7 | 95.2 | 95 | 95.3 | 95.7 | 96.7 | 96.8 | 96.6 | 96.1 | 95.9 | 96.3 | 94.7 | 96.2 | 96.5 | 96.5 | 96.1 | 95.8 | 96.2 | Shenzhen Growatt New Energy Technology Co., Ltd.6.74101Growatt 7600MTLP-US (208V) [SI1] | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 7000MTLP-US [240V] | N | Y | N | 7 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.011 | 240 | 96.5 | [10/13/2017] | [KA 1.0] | Not Applicable | Y | N |  | 0.051 |  |  | 270 | 385 | 485 | 701.11 | 1402.22 | 2103.33 | 3505.55 | 5258.33 | 7011.1 | 94 | 95.7 | 95.9 | 96 | 95.8 | 95.5 | 95.8 | 95.7 | 96.8 | 97 | 96.9 | 96.7 | 96.4 | 96.7 | 94.6 | 96.4 | 96.8 | 96.9 | 96.7 | 96.3 | 96.6 | Shenzhen Growatt New Energy Technology Co., Ltd.7.011Growatt 7000MTLP-US (240V) [SI1] | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 7000MTLP-US [277V] | N | Y | N | 7 kW, 277 Vac Grid Support Utility Interactive Inverter | 7.0161 | 277 | 96.5 | [10/13/2017] | [KA 1.0] | Not Applicable | Y | N |  | 0.051 |  |  | 275 | 385 | 480 | 701.61 | 1403.21 | 2104.82 | 3508.04 | 5262.05 | 7016.07 | 92.8 | 95.2 | 95.4 | 95.9 | 96.1 | 95.9 | 95.8 | 93.6 | 96.3 | 96.7 | 96.9 | 96.8 | 96.5 | 96.6 | 95 | 96.6 | 97.1 | 97.3 | 97.2 | 97 | 97.1 | Shenzhen Growatt New Energy Technology Co., Ltd.7.01607Growatt 7000MTLP-US (277V) [SI1] | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 8000MTLP-US [208V] | Y | Y | Y | 8 kW, 208 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 7.107 | 208 | 97 | [10/13/2017] | [KC 1.0] | 2018-10-15 | N | N |  | 3.3 |  |  | 330 | 480 | 550 | 0.7107 | 1.4214 | 2.1321 | 3.5535 | 5.3303 | 7.107 | 95.2319 | 96.8981 | 97.1668 | 97.2152 | 96.9406 | 96.7327 | 96.9445 | 95.3248 | 96.8981 | 97.3535 | 97.5256 | 97.3657 | 97.2044 | 97.2847 | 94.5675 | 96.5387 | 97.0783 | 97.371 | 97.2917 | 97.1309 | 97.1281 | Shenzhen Growatt New Energy Technology Co., Ltd.7.107Growatt 8000MTLP-US (208V) [SI1] | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 7600MTLP-US [240V] | N | Y | N | 7.6 kW, 240 Vac Grid Support Utility Interactive Inverter | 7.604 | 240 | 96.5 | [10/13/2017] | [KC 1.0] | Not Applicable | Y | N |  | 0.051 |  |  | 270 | 380 | 480 | 760.4 | 1520.8 | 2281.19 | 3801.99 | 5702.99 | 7603.98 | 94.3 | 95.8 | 96.2 | 96.1 | 95.8 | 95.3 | 95.8 | 96.1 | 97 | 97.2 | 97.1 | 96.8 | 96.3 | 96.9 | 94.9 | 96.5 | 96.9 | 96.9 | 96.7 | 96.3 | 96.7 | Shenzhen Growatt New Energy Technology Co., Ltd.7.604Growatt 7600MTLP-US (240V) [SI1] | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 7600MTLP-US [277V] | N | Y | N | 7.6 kW, 277 Vac Grid Support Utility Interactive Inverter | 7.652 | 277 | 96.5 | [10/13/2017] | [KC 1.0] | Not Applicable | Y | N |  | 0.051 |  |  | 270 | 380 | 480 | 765.15 | 1530.3 | 2295.45 | 3825.75 | 5738.63 | 7651.5 | 94.3 | 95.8 | 96.2 | 96.1 | 95.8 | 95.3 | 95.8 | 96.1 | 97 | 97.2 | 97.1 | 96.8 | 96.3 | 96.9 | 94.9 | 96.5 | 96.9 | 96.9 | 96.7 | 96.3 | 96.7 | Shenzhen Growatt New Energy Technology Co., Ltd.7.652Growatt 7600MTLP-US (277V) [SI1] | 2017-10-16
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 9000MTLP-US [208V] | Y | Y | Y | 9 kW, 208 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 7.864 | 208 | 97 | [10/13/2017] | [KC 1.0] | 2018-10-15 | N | N |  | 3.3 |  |  | 330 | 480 | 550 | 0.7864 | 1.5728 | 2.3592 | 3.932 | 5.898 | 7.864 | 95.4343 | 96.8634 | 97.1228 | 97.0837 | 96.7601 | 96.5393 | 96.8127 | 95.5184 | 96.9899 | 97.3531 | 97.4463 | 97.1787 | 97.0001 | 97.1711 | 94.827 | 96.6169 | 97.0564 | 97.2473 | 97.0819 | 96.8936 | 96.9907 | Shenzhen Growatt New Energy Technology Co., Ltd.7.864Growatt 90000MTLP-US (208V) [SI1] | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 8000MTLP-US [240V] | Y | Y | Y | 8 kW, 240 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 8.061 | 240 | 97.5 | [10/13/2017] | [KC 1.0] | 2018-10-15 | N | N |  | 3.5 |  |  | 330 | 480 | 550 | 0.8061 | 1.6122 | 2.4183 | 4.0305 | 6.0457 | 8.061 | 95.4816 | 96.806 | 97.2982 | 97.458 | 97.318 | 97.0166 | 97.2309 | 95.7939 | 97.0913 | 97.5954 | 97.859 | 97.7928 | 97.5766 | 97.6572 | 95.2637 | 96.7576 | 97.3124 | 97.6341 | 97.6942 | 97.5279 | 97.4834 | Shenzhen Growatt New Energy Technology Co., Ltd.8.061Growatt 8000MTLP-US (240V) [SI1] | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 8000MTLP-US [277V] | Y | Y | Y | 8 kW, 277 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 8.137 | 277 | 97.5 | [10/13/2017] | [KC 1.0] | 2018-10-15 | N | N |  | 3.7 |  |  | 330 | 480 | 550 | 0.8137 | 1.6274 | 2.4411 | 4.0685 | 6.1028 | 8.137 | 95.4421 | 96.6109 | 97.1824 | 97.5198 | 97.4925 | 97.2428 | 97.3225 | 96.2697 | 97.2044 | 97.777 | 98.0996 | 98.0984 | 97.9494 | 97.9348 | 95.8631 | 96.8898 | 97.4879 | 97.8391 | 97.9642 | 97.8946 | 97.7395 | Shenzhen Growatt New Energy Technology Co., Ltd.8.137Growatt 8000MTLP-US (277V) [SI1] | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 10000MTLP-US [208V] | Y | Y | Y | 10 kW, 208 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 8.63 | 208 | 97 | [10/13/2017] | [KC 1.0] | 2018-10-15 | N | N |  | 3.3 |  |  | 330 | 480 | 550 | 0.863 | 1.726 | 2.589 | 4.315 | 6.4725 | 8.63 | 95.5609 | 96.3702 | 96.5193 | 97.0537 | 96.6088 | 96.4293 | 96.6286 | 95.6227 | 96.7681 | 96.7901 | 97.4531 | 97.1269 | 96.9585 | 97.0684 | 95.0326 | 96.7812 | 97.1518 | 97.3399 | 96.9975 | 96.8805 | 96.9926 | Shenzhen Growatt New Energy Technology Co., Ltd.8.63Growatt 10000MTLP-US (208V) [SI1] | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 9000MTLP-US [240V] | Y | Y | Y | 9 kW, 240 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 9.061 | 240 | 97.5 | [10/13/2017] | [KC 1.0] | 2018-10-15 | N | N |  | 3.5 |  |  | 330 | 480 | 550 | 0.9061 | 1.8122 | 2.7183 | 4.5305 | 6.7957 | 9.061 | 95.9306 | 97.0351 | 97.3624 | 97.4055 | 97.1587 | 96.7832 | 97.1609 | 96.1264 | 97.3308 | 97.7098 | 97.8566 | 97.7061 | 97.4356 | 97.6427 | 95.536 | 96.9828 | 97.3349 | 97.5876 | 97.5568 | 97.3138 | 97.415 | Shenzhen Growatt New Energy Technology Co., Ltd.9.061Growatt 90000MTLP-US (240V) [SI1] | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 9000MTLP-US [277V] | Y | Y | Y | 9 kW, 277 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 9.169 | 277 | 97.5 | [10/13/2017] | [KC 1.0] | 2018-10-15 | N | N |  | 3.7 |  |  | 330 | 480 | 550 | 0.9169 | 1.8338 | 2.7507 | 4.5845 | 6.8768 | 9.169 | 95.6877 | 96.866 | 97.3366 | 97.5417 | 97.445 | 97.1574 | 97.3387 | 96.3449 | 97.2806 | 97.7734 | 98.114 | 98.0647 | 97.8914 | 97.9234 | 95.9346 | 97.0873 | 97.6193 | 97.9244 | 98.0003 | 97.8943 | 97.8051 | Shenzhen Growatt New Energy Technology Co., Ltd.9.169Growatt 90000MTLP-US (277V) [SI1] | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 10000MTLP-US [240V] | Y | Y | Y | 10 kW, 240 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 10.058 | 240 | 97 | [10/13/2017] | [KC 1.0] | 2018-10-15 | N | N |  | 3.5 |  |  | 330 | 480 | 550 | 1.0058 | 2.0116 | 3.0174 | 5.029 | 7.5435 | 10.058 | 95.7496 | 96.5751 | 96.6916 | 96.5323 | 96.917 | 96.6087 | 96.7299 | 95.8602 | 96.9019 | 97.0339 | 97.0528 | 97.6148 | 97.3005 | 97.3055 | 95.3753 | 96.9373 | 97.3973 | 97.6401 | 97.5368 | 97.2343 | 97.4102 | Shenzhen Growatt New Energy Technology Co., Ltd.10.058Growatt 10000MTLP-US (240V) [SI1] | 2017-10-16 | 2018-10-15
Shenzhen Growatt New Energy Technology Co., Ltd. | Growatt 10000MTLP-US [277V] | Y | Y | Y | 10 kW, 277 Vac, 110-480 Vdc Grid Support Utility Interactive Inverter with boosting circuit | 10.165 | 277 | 97.5 | [10/13/2017] | [KC 1.0] | 2018-10-15 | N | N |  | 3.7 |  |  | 330 | 480 | 550 | 1.0165 | 2.033 | 3.0495 | 5.0825 | 7.6238 | 10.165 | 95.5795 | 96.4291 | 96.9301 | 97.5168 | 97.3177 | 97.0515 | 97.1857 | 96.0695 | 97.219 | 97.3929 | 98.1228 | 97.9602 | 97.7314 | 97.8021 | 95.8737 | 97.1605 | 97.9253 | 97.9533 | 97.9509 | 97.7632 | 97.8163 | Shenzhen Growatt New Energy Technology Co., Ltd.10.165Growatt 10000MTLP-US (277V) [SI1] | 2017-10-16 | 2018-10-15
Shenzhen Sinexcel Electric Co., Ltd | Rainbow PVI-10.0-I-US | Y | N | N | Photovoltaic Inverter for grid connected with NEMA 4 enclosure | 9.98 |  | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 250 | 386.5 | 432 | 0.998 | 1.997 | 2.995 | 4.991 | 7.487 | 9.983 | 90.3 | 93.7 | 95.2 | 95.6 | 95.2 | 94.9 | 95 | 91 | 94.8 | 95.5 | 95.8 | 95.6 | 95.4 | 95.4 | 91.8 | 94.8 | 95.3 | 96 | 96 | 95.5 | 95.6 | Shenzhen Sinexcel Electric Co., Ltd9.98Rainbow PVI-10.0-I-US |  | 2018-02-15
Shenzhen Sinexcel Electric Co., Ltd | Rainbow PVI-12.5-I-US | Y | N | N | Photovoltaic Inverter for grid connected with NEMA 4 enclosure | 12.51 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 250 | 386.5 | 432 | 1.251 | 2.503 | 3.754 | 6.257 | 9.386 | 1.251 | 90.9 | 94 | 95.7 | 95.1 | 94.9 | 94.3 | 94.8 | 88 | 93.4 | 95.6 | 95.3 | 95.4 | 95.1 | 95 | 87.8 | 94.7 | 95 | 95.1 | 95.2 | 94.9 | 94.8 | Shenzhen Sinexcel Electric Co., Ltd12.51Rainbow PVI-12.5-I-US |  | 2018-02-15
Shenzhen Sinexcel Electric Co., Ltd | PWS2-30K-NA [480V] | Y | Y | Y | 30 kW, 480 Vac wall-mounted, bi-directional Grid Support Utility Interactive Energy Storage Inverter | 30.02 | 480 | 96.5 | [9/18/2017] | [V126] | 2018-10-15 | N | N |  | 1.857 |  |  | 350 | 600 | 750 | 3.002 | 6.004 | 9.006 | 15.01 | 22.515 | 30.02 | 91.2328 | 94.2776 | 95.1804 | 95.6343 | 95.5611 | 95.1895 | 95.2749 | 94.0804 | 95.9185 | 96.6069 | 97.0086 | 97.0306 | 96.8722 | 96.7936 | 94.9891 | 96.635 | 97.1812 | 97.4446 | 97.4471 | 97.2664 | 97.2667 | Shenzhen Sinexcel Electric Co., Ltd30.02PWS2-30K-NA [SI1] | 2017-11-01 | 2018-10-15
Shenzhen Sinexcel Electric Co., Ltd | PWS1-50K-NA [480V] | N | Y | Y | 50 kW, 480 Vac Grid Support Utility Interactive Inverter with 1 Inverter modules | 48.58 | 480 | 94 | [4/23/2017] | [1320, 130, 1420] | 2018-10-15 | N | N |  | 860 |  |  | 500 | 650 | 850 | 4.858 | 9.716 | 14.574 | 24.29 | 36.435 | 48.58 | 87.3239 | 92.4174 | 93.9642 | 94.911 | 94.9348 | 94.6249 | 94.3675 | 86.4796 | 91.8343 | 93.5215 | 94.5382 | 94.6245 | 94.3137 | 93.9931 | 85.5066 | 91.2148 | 92.8921 | 94.1271 | 94.1483 | 93.9232 | 93.4895 | Shenzhen Sinexcel Electric Co., Ltd48.58PWS1-50K-NA [480V] | 2017-07-01 | 2018-10-15
Shenzhen Sinexcel Electric Co., Ltd | PWS1-100K-NA [480V] | N | Y | Y | 100 kW, 480 Vac Grid Support Utility Interactive Inverter with 2 Inverter modules | 98.013 | 480 | 94 | [4/23/2017] | [1320, 130, 1420] | 2018-10-15 | N | N |  | 997 |  |  | 500 | 650 | 850 | 9.8013 | 19.6026 | 29.4039 | 49.0065 | 73.5097 | 98.013 | 87.3115 | 92.4599 | 94.0486 | 95.0349 | 95.1062 | 94.7968 | 94.5048 | 86.5716 | 91.9322 | 93.5785 | 94.5421 | 94.644 | 94.3807 | 94.0231 | 85.5959 | 91.2784 | 92.9994 | 94.0717 | 94.2626 | 94.044 | 93.5641 | Shenzhen Sinexcel Electric Co., Ltd98.013PWS1-100K-NA [480V] | 2017-07-01 | 2018-10-15
Shenzhen Sinexcel Electric Co., Ltd | PWS1-150K-NA [480V] | N | Y | Y | 150 kW, 480 Vac Grid Support Utility Interactive Inverter with 3 Inverter modules | 147.47 | 480 | 94.5 | [4/23/2017] | [1320, 130, 1420] | 2018-10-15 | N | N |  | 1360 |  |  | 500 | 650 | 850 | 14.747 | 29.494 | 44.241 | 73.735 | 110.6025 | 147.47 | 88.5911 | 93.0981 | 94.4501 | 95.1722 | 95.219 | 94.8928 | 94.7294 | 87.8328 | 92.6191 | 94.0834 | 94.9672 | 95.0226 | 94.7007 | 94.4744 | 86.7442 | 91.8963 | 93.4554 | 94.3477 | 94.4727 | 94.2361 | 93.8746 | Shenzhen Sinexcel Electric Co., Ltd147.47PWS1-150K-NA [480V] | 2017-07-01 | 2018-10-15
Shenzhen Sinexcel Electric Co., Ltd | PWS1-250K-NA [480V] | N | Y | Y | 250 kW, 480 Vac Grid Support Utility Interactive Inverter with 5 Inverter modules | 244.026 | 480 | 95 | [4/23/2017] | [1320, 130, 1420] | 2018-10-15 | N | N |  | 1860 |  |  | 500 | 650 | 850 | 24.4026 | 48.8052 | 73.2078 | 122.013 | 183.0195 | 244.026 | 91.3922 | 94.968 | 95.7012 | 96.033 | 95.7801 | 95.4154 | 95.5894 | 90.4456 | 94.3962 | 95.2142 | 95.5745 | 95.3838 | 95.0192 | 95.1384 | 89.2163 | 93.5746 | 94.5987 | 95.0795 | 94.9604 | 94.63 | 94.6264 | Shenzhen Sinexcel Electric Co., Ltd244.026PWS1-250K-NA [480V] | 2017-07-01 | 2018-10-15
Shenzhen Sinexcel Electric Co., Ltd | PWS1-500KTL-NA [400V] | N | Y | Y | 500 kW, 400 Vac Grid Support Utility-Interactive Energy Storage Inverter | 498.34 | 400 | 96 | [02/26/2018] | [1400] | 2018-10-15 | N | N | Efficiency data inclusive of transformer effect based on 500 kVA Low-Voltage Dry-Type Distribution Transformers Table in DOE2016. | 289.9 |  |  | 640 | 750 | 900 | 49.83 | 99.67 | 149.5 | 249.17 | 373.76 | 498.34 | 93.95 | 96 | 96.6 | 96.83 | 96.64 | 96.31 | 96.52 | 93.16 | 95.61 | 96.3 | 96.61 | 96.47 | 96.13 | 96.28 | 92.19 | 95.03 | 95.86 | 96.27 | 96.14 | 95.84 | 95.9 | Shenzhen Sinexcel Electric Co., Ltd498.34PWS1-500KTL-NA [400V] | 2018-05-01 | 2018-10-15
Siemens Industry | SMIINT215R60XX [208V] | Y | N | N | 215 W, 208 Vac Inverter with integrated ground, XX are connector types | 0.215 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.054 |  |  | 27.5 | 33 | 38.7 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 95.2 | 96.1 | 96.4 | 96.6 | 96.6 | 96.3 | 96.5 | 95.1 | 96.1 | 96.3 | 96.6 | 96.6 | 96.5 | 96.5 | 95 | 96 | 96.2 | 96.5 | 96.6 | 96.6 | 96.5 | Siemens Industry0.215SMIINT215R60XX [208V]
Siemens Industry | SMIINT215R60XX [240V] | Y | N | N | 215 W, 240 Vac Inverter with integrated ground, XX are connector types | 0.215 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.054 |  |  | 27.5 | 33 | 38.7 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 95.2 | 96.1 | 96.4 | 96.6 | 96.6 | 96.3 | 96.5 | 95.1 | 96.1 | 96.3 | 96.6 | 96.6 | 96.5 | 96.5 | 95 | 96 | 96.2 | 96.5 | 96.6 | 96.6 | 96.5 | Siemens Industry0.215SMIINT215R60XX [240V]
Siemens Industry | SMIINV215R60XX [208V] | Y | N | N | 215 W, 208 Vac Inverter, XX are connector types | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.6 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Siemens Industry0.215SMIINV215R60XX [208V]
Siemens Industry | SMIINV215R60XX [240V] | Y | N | N | 215 W, 240 Vac Inverter, XX are connector types | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.05 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.6 | 95.5 | 95.9 | 96.1 | 95.7 | 95.1 | 95.7 | 94.6 | 95.5 | 95.9 | 96.2 | 96.1 | 95.8 | 96 | 94.6 | 95.5 | 95.8 | 96.1 | 96.2 | 96.1 | 96.1 | Siemens Industry0.215SMIINV215R60XX [240V]
Siemens Industry | SMIINT250R60XX [208V] | Y | N | N | 240 W, 208 Vac Inverter with integrated ground, XX are connector types | 0.24 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.043 |  |  | 27 | 32 | 38 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 94.7 | 95.7 | 96.1 | 96.3 | 96 | 95.5 | 96 | 94.7 | 95.7 | 96 | 96.3 | 96.2 | 95.8 | 96.1 | 94.5 | 95.5 | 95.8 | 96.1 | 96.2 | 96 | 96 | Siemens Industry0.24SMIINT250R60XX [208V]
Siemens Industry | SMIINT250R60XX [240V] | Y | N | N | 240 W, 240 Vac Inverter with integrated ground, XX are connector types | 0.24 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.046 |  |  | 27 | 32 | 38 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 95.6 | 96 | 96.3 | 96.5 | 96.4 | 96.1 | 96.4 | 95 | 96 | 96.2 | 96.5 | 96.6 | 96.4 | 96.4 | 94.9 | 96 | 96 | 96.4 | 96.5 | 96.5 | 96.4 | Siemens Industry0.24SMIINT250R60XX [240V]
Siemens Industry | SINVERT PVM12 UL [480V] | Y | N | N | 12 kW, 480 Vac, 3-phase Utility Interactive Inverter | 12.12 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.87 |  |  | 450 | 720 | 900 | 1.21 | 2.42 | 3.64 | 6.06 | 9.09 | 12.12 | 94.9 | 96.1 | 96.9 | 97.4 | 97.5 | 97.3 | 97.2 | 96 | 96.5 | 97.4 | 97.9 | 98.1 | 98.1 | 97.8 | 95.2 | 95.9 | 96.8 | 97.4 | 97.6 | 97.7 | 97.3 | Siemens Industry12.12SINVERT PVM12 UL [480V]
Siemens Industry | SINVERT PVM16 UL [480V] | Y | N | N | 16 kW, 480 Vac, 3-phase Utility Interactive Inverter | 16.1 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.09 |  |  | 500 | 720 | 900 | 1.61 | 3.22 | 4.83 | 8.05 | 12.08 | 16.1 | 96 | 96.8 | 97.4 | 97.6 | 97.6 | 97.4 | 97.5 | 96.6 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.9 | 95.9 | 96.5 | 97.2 | 97.6 | 97.7 | 97.7 | 97.5 | Siemens Industry16.1SINVERT PVM16 UL [480V]
Siemens Industry | SINVERT PVM20 UL [480V] | Y | N | N | 20 kW, 480 Vac, 3-phase Utility Interactive Inverter | 19.65 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.09 |  |  | 550 | 720 | 900 | 1.97 | 3.93 | 5.9 | 9.83 | 14.74 | 19.65 | 96.5 | 97.3 | 97.7 | 97.8 | 97.7 | 97.5 | 97.6 | 96.7 | 97.5 | 97.9 | 98.1 | 98.1 | 98 | 98 | 96 | 96.6 | 97.2 | 97.6 | 97.6 | 97.5 | 97.4 | Siemens Industry19.65SINVERT PVM20 UL [480V]
Siemens Industry | SINVERT PVM24 UL [480V] | Y | N | N | 22.2 kW, 480 Vac, 3-phase Utility Interactive Inverter | 22.23 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.49 |  |  | 600 | 720 | 900 | 2.22 | 4.45 | 6.67 | 11.12 | 16.67 | 22.23 | 97.2 | 97.7 | 97.9 | 97.9 | 97.8 | 97.6 | 97.8 | 97.3 | 97.7 | 98 | 98.1 | 98 | 97.8 | 98 | 96.7 | 97.1 | 97.5 | 97.7 | 97.6 | 97.5 | 97.6 | Siemens Industry22.23SINVERT PVM24 UL [480V]
Siemens Industry | SINVERT PVS351 UL [480V] | Y | N | N | 350 kW, 480 Vac, 3-phase Inverter (Master Unit) | 350 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 25 |  |  | 330 | 400 | 480 | 35 | 70 | 105 | 175 | 262.5 | 350 | 94.7 | 96.3 | 96.9 | 96.9 | 96.8 | 96.8 | 96.7 | 84.8 | 90.7 | 93 | 94.6 | 95.5 | 95.2 | 94.3 | 91.8 | 95.5 | 97.7 | 97.7 | 97.4 | 96.6 | 97.1 | Siemens Industry350SINVERT PVS351 UL [480V]
Siemens Industry | SINVERT PVS701 UL [480V] | Y | N | N | 700 kW, 480 Vac, 3-phase Inverter (Master Unit, 1 Slave Unit) | 700 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 50 |  |  | 330 | 400 | 480 | 70 | 140 | 210 | 350 | 525 | 700 | 94.7 | 96.3 | 96.9 | 96.9 | 96.8 | 96.8 | 96.7 | 84.8 | 90.7 | 93 | 94.6 | 95.5 | 95.2 | 94.3 | 91.8 | 95.5 | 97.7 | 97.7 | 97.4 | 96.6 | 97.1 | Siemens Industry700SINVERT PVS701 UL [480V]
Siemens Industry | SINVERT PVS1051 UL [480V] | Y | N | N | 1050 kW, 480 Vac, 3-phase Inverter (Master Unit, 2 Slave Units) | 1050 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 75 |  |  | 330 | 400 | 480 | 105 | 210 | 315 | 525 | 787.5 | 1050 | 94.7 | 96.3 | 96.9 | 96.9 | 96.8 | 96.8 | 96.7 | 84.8 | 90.7 | 93 | 94.6 | 95.5 | 95.2 | 94.3 | 91.8 | 95.5 | 97.7 | 97.7 | 97.4 | 96.6 | 97.1 | Siemens Industry1050SINVERT PVS1051 UL [480V]
Siemens Industry | SINVERT PVS1401 UL [480V] | Y | N | N | 1400 kW, 480 Vac, 3-phase Inverter (Master Unit, 3 Slave Units) | 1400 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 100 |  |  | 330 | 400 | 480 | 140 | 280 | 420 | 700 | 1050 | 1400 | 94.7 | 96.3 | 96.9 | 96.9 | 96.8 | 96.8 | 96.7 | 84.8 | 90.7 | 93 | 94.6 | 95.5 | 95.2 | 94.3 | 91.8 | 95.5 | 97.7 | 97.7 | 97.4 | 96.6 | 97.1 | Siemens Industry1400SINVERT PVS1401 UL [480V]
Silicon Energy | SiE 3840 [208V] | Y | N | N | 3.3 kW, 208 Vac Utility Interactive Inverter | 3.4 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 12 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2 | Silicon Energy3.4SiE 3840 [208V]
Silicon Energy | SiE 3840 [240V] | Y | N | N | 3.8 kW, 240 Vac Utility Interactive Inverter | 3.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 11 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2 | Silicon Energy3.9SiE 3840 [240V]
Silicon Energy | SiE 5300 [208V] | Y | N | N | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 13.95 |  |  | 100 | 275 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.5 | 95.6 | 96.2 | 96.1 | 95.9 | 95.3 | 95.9 | 93 | 95.3 | 96 | 95.9 | 95.9 | 95.2 | 95.7 | 91.7 | 94.4 | 95.2 | 95.7 | 95.5 | 95 | 95.3 | Silicon Energy4.6SiE 5300 [208V]
Silicon Energy | SiE 5300 [240V] | Y | N | N | 5.3 kW, 240 Vac Utility Interactive Inverter | 5.3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 14 |  |  | 100 | 275 | 400 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 94.3 | 96.1 | 96.3 | 96.4 | 96 | 95.2 | 96 | 93.8 | 95.9 | 96.1 | 96.3 | 95.8 | 95.2 | 95.8 | 92.5 | 95 | 95.7 | 96 | 95.5 | 94.9 | 95.4 | Silicon Energy5.3SiE 5300 [240V]
SMA America | SB 240-US-10 [240V] | Y | N | N | 240 W, 240 Vac Microinverter | 0.24 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 |  |  | 30 | 30 | 32 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 95.2 | 95.7 | 95.9 | 95.9 | 95.9 | 95.8 | 95.8 | 95.2 | 95.7 | 95.8 | 95.9 | 95.8 | 95.8 | 95.8 | 95.1 | 95.6 | 95.8 | 95.8 | 95.8 | 95.8 | 95.8 | SMA America0.24SB 240-US-10 [240V]
SMA America | SB700U [120V] | Y | N | N | 700 W, 120Vac Sunny Boy String Inverter | 0.7 | 120 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.0357 |  |  | 100 | 145 | 200 | 0.07 | 0.14 | 0.21 | 0.35 | 0.53 | 0.7 | 87.17 | 91.46 | 92.68 | 92.98 | 92.42 | 91.45 | 92.26 | 86.53 | 91.26 | 92.47 | 92.32 | 91.44 | 90.36 | 91.49 | 84.83 | 90.18 | 91.07 | 91.63 | 91.03 | 90.2 | 90.83 | SMA America0.7SB700U [120V]
SMA America | SB700U-SBD [120V] | Y | N | N | 700 W, 120Vac Sunny Boy String Inverter with display | 0.7 | 120 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.0357 |  |  | 100 | 145 | 200 | 0.07 | 0.14 | 0.21 | 0.35 | 0.53 | 0.7 | 87.17 | 91.46 | 92.68 | 92.98 | 92.42 | 91.45 | 92.26 | 86.53 | 91.26 | 92.47 | 92.32 | 91.44 | 90.36 | 91.49 | 84.83 | 90.18 | 91.07 | 91.63 | 91.03 | 90.2 | 90.83 | SMA America0.7SB700U-SBD [120V]
SMA America | SB1100U [240V] | Y | N | N | 1100 W, 240 Vac Sunny Boy String Inverter | 1.1 | 240 | 91 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.13 |  |  | 100 | 200 | 325 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 83.92 | 91.62 | 92.57 | 92.42 | 91.86 | 90.91 | 91.68 | 87.08 | 90.82 | 91.84 | 92.02 | 91.37 | 90.5 | 91.32 | 83.95 | 88.75 | 92.38 | 90.95 | 90.75 | 90.01 | 90.58 | SMA America1.1SB1100U [240V]
SMA America | SB1100U-SBD [240V] | Y | N | N | 1100 W, 240 Vac Sunny Boy String Inverter | 1.1 | 240 | 91 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.13 |  |  | 100 | 200 | 325 | 0.11 | 0.22 | 0.33 | 0.55 | 0.83 | 1.1 | 83.92 | 91.62 | 92.57 | 92.42 | 91.86 | 90.91 | 91.68 | 87.08 | 90.82 | 91.84 | 92.02 | 91.37 | 90.5 | 91.32 | 83.95 | 88.75 | 92.38 | 90.95 | 90.75 | 90.01 | 90.58 | SMA America1.1SB1100U-SBD [240V]
SMA America | SWR1800U [120V] | Y | N | N | 1.8 kW, 120Vac Sunny Boy String Inverter | 1.8 | 120 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2659 |  |  | 100 | 200 | 400 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 89.82 | 92.39 | 93.01 | 92.83 | 91.99 | 91 | 92.17 | 89.56 | 92.12 | 92.82 | 92.7 | 91.72 | 90.8 | 91.95 | 86.79 | 90.45 | 91.44 | 91.78 | 91.18 | 90.3 | 91.08 | SMA America1.8SWR1800U [120V]
SMA America | SWR1800U-SBD [120V] | Y | N | N | 1.8 kW, 120Vac Sunny Boy String Inverter with display | 1.8 | 120 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2659 |  |  | 100 | 200 | 400 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 89.82 | 92.39 | 93.01 | 92.83 | 91.99 | 91 | 92.17 | 89.56 | 92.12 | 92.82 | 92.7 | 91.72 | 90.8 | 91.95 | 86.79 | 90.45 | 91.44 | 91.78 | 91.18 | 90.3 | 91.08 | SMA America1.8SWR1800U-SBD [120V]
SMA America | SB2000HFUS-30 [208V] | Y | N | N | 2 kW, 208 Vac Sunny Boy Utility Interactive Inverter | 2.03 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0 |  |  | 100 | 400 | 480 | 0.2 | 0.41 | 0.61 | 1.02 | 1.52 | 2.03 | 92.2 | 95.2 | 96 | 96.3 | 95.9 | 95.2 | 95.8 | 95.1 | 96.8 | 97.4 | 97.4 | 97.2 | 96.6 | 97.1 | 96.4 | 97.8 | 98.1 | 98 | 97.6 | 97.1 | 97.7 | SMA America2.03SB2000HFUS-30 [208V]
SMA America | SB2000HFUS-30 [240V] | Y | N | N | 2 kW, 240 Vac Sunny Boy Utility Interactive Inverter | 2.05 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0 |  |  | 100 | 400 | 480 | 0.21 | 0.41 | 0.62 | 1.03 | 1.54 | 2.05 | 92.6 | 95.2 | 96.2 | 96.6 | 96.4 | 95.9 | 96.2 | 93.9 | 97 | 97.3 | 97.6 | 97.6 | 97.2 | 97.3 | 95.8 | 97.6 | 98 | 98.1 | 97.9 | 97.6 | 97.8 | SMA America2.05SB2000HFUS-30 [240V]
SMA America | SWR2100U [240V] | Y | N | N | 2.1 kW, 240 Vac Sunny Boy String Inverter | 2.1 | 240 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 100 | 300 | 480 | 0.21 | 0.42 | 0.63 | 1.05 | 1.575 | 2.1 | 91.2 | 93.6 | 94.3 | 94.3 | 93.9 | 93.3 | 93.9 | 90.2 | 92.7 | 93.5 | 94.5 | 93.7 | 93.1 | 93.6 | 86 | 89.9 | 91.3 | 92.1 | 92.3 | 91.8 | 91.8 | SMA America2.1SWR2100U [240V]
SMA America | SWR2100U-SBD [240V] | Y | N | N | 2.1 kW, 240 Vac Sunny Boy String Inverter | 2.1 | 240 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 100 | 300 | 480 | 0.21 | 0.42 | 0.63 | 1.05 | 1.575 | 2.1 | 91.2 | 93.6 | 94.3 | 94.3 | 93.9 | 93.3 | 93.9 | 90.2 | 92.7 | 93.5 | 94.5 | 93.7 | 93.1 | 93.6 | 86 | 89.9 | 91.3 | 92.1 | 92.3 | 91.8 | 91.8 | SMA America2.1SWR2100U-SBD [240V]
SMA America | SWR2500U [208V] | Y | N | N | 2.1 kW, 208 Vac Sunny Boy String Inverter | 2.1 | 208 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.236 |  |  | 100 | 300 | 480 | 0.21 | 0.42 | 0.63 | 1.05 | 1.58 | 2.1 | 90.86 | 93.44 | 94.02 | 93.86 | 93.06 | 92.06 | 93.22 | 89.33 | 92.49 | 93.07 | 93.3 | 92.57 | 91.52 | 92.6 | 85.59 | 89.83 | 91.11 | 91.75 | 91.25 | 90.64 | 91.01 | SMA America2.1SWR2500U [208V]
SMA America | SWR2500U-SBD [208V] | Y | N | N | 2.1 kW, 208 Vac Sunny Boy String Inverter with display | 2.1 | 208 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.236 |  |  | 100 | 300 | 480 | 0.21 | 0.42 | 0.63 | 1.05 | 1.58 | 2.1 | 90.86 | 93.44 | 94.02 | 93.86 | 93.06 | 92.06 | 93.22 | 89.33 | 92.49 | 93.07 | 93.3 | 92.57 | 91.52 | 92.6 | 85.59 | 89.83 | 91.11 | 91.75 | 91.25 | 90.64 | 91.01 | SMA America2.1SWR2500U-SBD [208V]
SMA America | SWR2500U [240V] | Y | N | N | 2.5 kW, 240 Vac Sunny Boy String Inverter | 2.5 | 240 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.318 |  |  | 100 | 300 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 91.03 | 93.93 | 94.57 | 94.53 | 93.9 | 93.26 | 93.97 | 89.79 | 93.21 | 93.89 | 94.15 | 93.66 | 92.89 | 93.57 | 86.28 | 90.48 | 91.91 | 92.59 | 92.33 | 91.84 | 91.98 | SMA America2.5SWR2500U [240V]
SMA America | SWR2500U-SBD [240V] | Y | N | N | 2.5 kW, 240 Vac Sunny Boy String Inverter with display | 2.5 | 240 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.318 |  |  | 100 | 300 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 91.03 | 93.93 | 94.57 | 94.53 | 93.9 | 93.26 | 93.97 | 89.79 | 93.21 | 93.89 | 94.15 | 93.66 | 92.89 | 93.57 | 86.28 | 90.48 | 91.91 | 92.59 | 92.33 | 91.84 | 91.98 | SMA America2.5SWR2500U-SBD [240V]
SMA America | SB2500HFUS-30 [208V] | Y | N | N | 2.5 kW, 208 Vac Sunny Boy Utility Interactive Inverter | 2.53 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 |  |  | 100 | 415 | 480 | 0.25 | 0.51 | 0.76 | 1.27 | 1.9 | 2.53 | 94.3 | 95.7 | 96.4 | 96.4 | 96 | 95.1 | 96 | 95.6 | 96.8 | 97.2 | 97.2 | 96.9 | 96.3 | 96.9 | 95 | 96.8 | 97.3 | 97.4 | 97.1 | 96.5 | 97.1 | SMA America2.53SB2500HFUS-30 [208V]
SMA America | SB2500HFUS-30 [240V] | Y | N | N | 2.5 kW, 240 Vac Sunny Boy Utility Interactive Inverter | 2.53 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.12 |  |  | 100 | 415 | 480 | 0.25 | 0.51 | 0.76 | 1.26 | 1.9 | 2.53 | 93.4 | 95.3 | 96.1 | 96.1 | 96.2 | 95.5 | 96 | 93.6 | 96 | 96.7 | 97.1 | 97 | 96.6 | 96.8 | 93.6 | 96.1 | 96.9 | 97.2 | 97.1 | 96.7 | 96.9 | SMA America2.53SB2500HFUS-30 [240V]
SMA America | SB3000US [208V] | Y | N | N | 3 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 3 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 100 | 250 | 400 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 94 | 95.8 | 96 | 95.8 | 95.1 | 94.3 | 95.3 | 93.1 | 95.9 | 95.7 | 95.6 | 94.9 | 94 | 95.1 | 91.6 | 94.8 | 95.2 | 94.7 | 94.2 | 93.5 | 94.3 | SMA America3SB3000US [208V]
SMA America | SB3000US [240V] | Y | N | N | 3 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 3 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 250 | 400 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.4 | 95.9 | 96.3 | 96.5 | 96.1 | 95.6 | 96 | 92.5 | 95.8 | 96 | 96.1 | 95.8 | 95.1 | 95.7 | 90.5 | 94.6 | 95.4 | 95.3 | 95.2 | 94.6 | 95 | SMA America3SB3000US [240V]
SMA America | SB3000US-12 [208V] | Y | N | N | 3 kW, 208 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 3 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 100 | 250 | 400 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 94 | 95.8 | 96 | 95.8 | 95.1 | 94.3 | 95.3 | 93.1 | 95.9 | 95.7 | 95.6 | 94.9 | 94 | 95.1 | 91.6 | 94.8 | 95.2 | 94.7 | 94.2 | 93.5 | 94.3 | SMA America3SB3000US-12 [208V]
SMA America | SB3000US-12 [240V] | Y | N | N | 3 kW, 240 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 3 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 250 | 400 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.4 | 95.9 | 96.3 | 96.5 | 96.1 | 95.6 | 96 | 92.5 | 95.8 | 96 | 96.1 | 95.8 | 95.1 | 95.7 | 90.5 | 94.6 | 95.4 | 95.3 | 95.2 | 94.6 | 95 | SMA America3SB3000US-12 [240V]
SMA America | SB3000HFUS-30 [208V] | Y | N | N | 3 kW, 208 Vac Sunny Boy Utility Interactive Inverter | 3.01 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 100 | 415 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3.01 | 94.2 | 96 | 96.4 | 96.2 | 95.5 | 94.2 | 95.7 | 95.4 | 96.7 | 96.8 | 96.8 | 96.3 | 95.5 | 96.4 | 96.2 | 97.4 | 97.6 | 97.4 | 96.8 | 96 | 97 | SMA America3.01SB3000HFUS-30 [208V]
SMA America | SB3.0-1SP-US-40 [208V] | Y | Y | Y | 3.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter | 3.03 | 208 | 96 | [2/21/2017] | [02.03.00.R] | 2018-10-15 | Y | N |  | 5.36 |  |  | 155 | 365 | 480 | 0.3032 | 0.6064 | 0.9096 | 1.516 | 2.274 | 3.032 | 92.0828 | 94.9078 | 95.6295 | 95.9916 | 95.9966 | 95.7315 | 95.7273 | 92.071 | 95.6597 | 96.4583 | 97.0435 | 97.2021 | 97.084 | 96.7913 | 88.5154 | 94.503 | 95.7227 | 96.4246 | 96.7724 | 96.6443 | 96.1233 | SMA America3.03SB3.0-1SP-US-40 [208V] | 2018-08-01 | 2018-10-15
SMA America | SB3.0-1TP-US-40 [208V] | Y | Y | Y | 3.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 3.03 | 208 | 96 | [06/28/2018] | [02.03.00.R] | 2018-10-15 | Y | N |  | 5.36 |  |  | 155 | 365 | 480 | 0.3032 | 0.6064 | 0.9096 | 1.516 | 2.274 | 3.032 | 92.0828 | 94.9078 | 95.6295 | 95.9916 | 95.9966 | 95.7315 | 95.7273 | 92.071 | 95.6597 | 96.4583 | 97.0435 | 97.2021 | 97.084 | 96.7913 | 88.5154 | 94.503 | 95.7227 | 96.4246 | 96.7724 | 96.6443 | 96.1233 | SMA America3.03SB3.0-1TP-US-40 [208V] | 2018-08-01 | 2018-10-15
SMA America | SB3.0-1SP-US-40 [240V] | Y | Y | Y | 3.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter | 3.04 | 240 | 96.5 | [2/21/2017] | [02.03.00.R] | 2018-10-15 | Y | N |  | 5.39 |  |  | 155 | 365 | 480 | 0.30403 | 0.60805 | 0.91208 | 1.5201 | 2.2802 | 3.0403 | 90.9512 | 94.442 | 95.3831 | 95.9418 | 96.0378 | 95.9409 | 95.651 | 92.0355 | 95.7848 | 96.6411 | 97.1637 | 97.5164 | 97.5821 | 97.0347 | 88.5098 | 94.4385 | 95.7364 | 96.6779 | 97.025 | 97.0008 | 96.3263 | SMA America3.04SB3.0-1SP-US-40 [240V] | 2018-08-01 | 2018-10-15
SMA America | SB3.0-1TP-US-40 [240V] | Y | Y | Y | 3.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 3.04 | 240 | 96.5 | [06/28/2018] | [02.03.00.R] | 2018-10-15 | Y | N |  | 5.39 |  |  | 155 | 365 | 480 | 0.30403 | 0.60805 | 0.91208 | 1.5201 | 2.2802 | 3.0403 | 90.9512 | 94.442 | 95.3831 | 95.9418 | 96.0378 | 95.9409 | 95.651 | 92.0355 | 95.7848 | 96.6411 | 97.1637 | 97.5164 | 97.5821 | 97.0347 | 88.5098 | 94.4385 | 95.7364 | 96.6779 | 97.025 | 97.0008 | 96.3263 | SMA America3.04SB3.0-1TP-US-40 [240V] | 2018-08-01 | 2018-10-15
SMA America | SB3000TL-US-22 [208V] | Y | N | N | 3 kW, 208 Vac Sunny Boy Utility Interactive Inverter | 3.05 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.53 |  |  | 100 | 400 | 480 | 0.31 | 0.61 | 0.92 | 1.53 | 2.29 | 3.05 | 92.7 | 95.3 | 95.8 | 96.1 | 96.1 | 95.9 | 95.9 | 92.6 | 95.7 | 96.5 | 97.2 | 97.2 | 97.1 | 96.8 | 92.2 | 95.4 | 96.5 | 96.9 | 97 | 97 | 96.6 | SMA America3.05SB3000TL-US-22 [208V] |  | 2018-03-15
SMA America | SB3000TL-US-22 [240V] | Y | N | N | 3 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 3.05 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.49 |  |  | 100 | 400 | 480 | 0.31 | 0.61 | 0.92 | 1.53 | 2.29 | 3.05 | 92.1 | 95 | 95.8 | 96.2 | 96.2 | 96 | 95.9 | 93.7 | 96.5 | 97.1 | 97.6 | 97.5 | 97.5 | 97.3 | 92.1 | 95.6 | 96.5 | 97.2 | 97.3 | 97.4 | 96.9 | SMA America3.05SB3000TL-US-22 [240V] |  | 2018-03-15
SMA America | SB3000HFUS-30 [240V] | Y | N | N | 3 kW, 240 Vac Sunny Boy Utility Interactive Inverter | 3.07 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 |  |  | 100 | 415 | 480 | 0.31 | 0.61 | 0.92 | 1.54 | 2.3 | 3.07 | 93.8 | 95.9 | 96.4 | 96.4 | 95.9 | 94.9 | 95.9 | 94.4 | 96.3 | 96.7 | 96.9 | 96.7 | 96.1 | 96.6 | 95.7 | 97.1 | 97.4 | 97.4 | 97.1 | 96.5 | 97.1 | SMA America3.07SB3000HFUS-30 [240V]
SMA America | SB3300U [240V] | Y | N | N | 3.3 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 3.3 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.16 |  |  | 100 | 250 | 400 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 92.6 | 94.6 | 95.2 | 95.4 | 95.2 | 94.6 | 95.06 | 91.8 | 94.1 | 94.8 | 95.1 | 94.9 | 94.5 | 94.74 | 89.2 | 92.4 | 93.6 | 94 | 93.9 | 93.5 | 93.61 | SMA America3.3SB3300U [240V]
SMA America | SB4000US(CL) [208V] | Y | N | N | 4 kW, 208 Vac, current limited Utility Interactive Inverter with display | 3.3 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 310 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 94.3 | 96.3 | 96.5 | 96.4 | 95.8 | 94.9 | 95.9 | 93.5 | 96.2 | 96.1 | 96.1 | 95.5 | 94.8 | 95.6 | 91.5 | 94.9 | 95.4 | 95.1 | 94.8 | 94 | 94.7 | SMA America3.3SB4000US(CL) [208V]
SMA America | SB3800U [208V] | Y | N | N | 3.5 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 3.5 | 208 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.161 |  |  | 100 | 235 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.625 | 3.5 | 93.59 | 94.88 | 95.15 | 94.87 | 94.14 | 93.33 | 94.39 | 92.81 | 94.5 | 94.78 | 94.62 | 93.98 | 92.95 | 94.14 | 90.26 | 92.72 | 93.44 | 93.46 | 93.06 | 92.23 | 93.02 | SMA America3.5SB3800U [208V]
SMA America | SB4000US [208V] | Y | N | N | 4 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 3.5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 310 | 480 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 94.3 | 96.3 | 96.5 | 96.4 | 95.8 | 94.9 | 95.9 | 93.5 | 96.2 | 96.1 | 96.1 | 95.5 | 94.8 | 95.6 | 91.5 | 94.9 | 95.4 | 95.1 | 94.8 | 94 | 94.7 | SMA America3.5SB4000US [208V]
SMA America | SB4000US-12 [208V] | Y | N | N | 3.5 kW, 208 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 3.5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 310 | 480 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 94.3 | 96.3 | 96.5 | 96.4 | 95.8 | 94.9 | 95.9 | 93.5 | 96.2 | 96.1 | 96.1 | 95.5 | 94.8 | 95.6 | 91.5 | 94.9 | 95.4 | 95.1 | 94.8 | 94 | 94.7 | SMA America3.5SB4000US-12 [208V]
SMA America | SB3.8-1SP-US-40 [208V] | Y | Y | Y | 3.8 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter | 3.6 | 208 | 96.5 | [2/21/2017] | [02.03.00.R] | 2018-10-15 | Y | N |  | 5.36 |  |  | 195 | 365 | 480 | 0.36045 | 0.72091 | 1.0814 | 1.8023 | 2.7034 | 3.6045 | 92.9308 | 95.4761 | 96.03 | 96.4729 | 96.3788 | 96.1527 | 96.1623 | 92.5315 | 95.951 | 96.6213 | 97.0596 | 97.2247 | 96.9787 | 96.8539 | 89.8079 | 94.9193 | 95.9971 | 96.5769 | 96.77 | 96.8496 | 96.2697 | SMA America3.6SB3.8-1SP-US-40 [208V] | 2018-08-01 | 2018-10-15
SMA America | SB3.8-1TP-US-40 [208V] | Y | Y | Y | 3.8 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 3.6 | 208 | 96.5 | [06/28/2018] | [02.03.00.R] | 2018-10-15 | Y | N |  | 5.36 |  |  | 195 | 365 | 480 | 0.36045 | 0.72091 | 1.0814 | 1.8023 | 2.7034 | 3.6045 | 92.9308 | 95.4761 | 96.03 | 96.4729 | 96.3788 | 96.1527 | 96.1623 | 92.5315 | 95.951 | 96.6213 | 97.0596 | 97.2247 | 96.9787 | 96.8539 | 89.8079 | 94.9193 | 95.9971 | 96.5769 | 96.77 | 96.8496 | 96.2697 | SMA America3.6SB3.8-1TP-US-40 [208V] | 2018-08-01 | 2018-10-15
SMA America | SB3800U [240V] | Y | N | N | 3.8 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 3.8 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.161 |  |  | 100 | 250 | 400 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93.32 | 95.02 | 95.5 | 95.39 | 94.98 | 94.27 | 95.03 | 92.75 | 94.63 | 95.08 | 95.07 | 94.69 | 93.81 | 94.69 | 90.15 | 92.98 | 93.89 | 94.08 | 93.82 | 93.21 | 93.66 | SMA America3.8SB3800U [240V]
SMA America | SB4000US(CL) [240V] | Y | N | N | 4 kW, 240 Vac, current limited Utility Interactive Inverter with display | 3.8 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.17 |  |  | 100 | 310 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.5 | 96.4 | 96.8 | 96.7 | 96.4 | 96 | 96.3 | 91.9 | 96.2 | 96.3 | 96.5 | 96 | 95.5 | 96 | 89.1 | 94.7 | 95.6 | 95.5 | 95.3 | 94.9 | 95.1 | SMA America3.8SB4000US(CL) [240V]
SMA America | SBS3.8-US-10 [240V] | N | Y | Y | 3.8 kW, 240 Vac, 1-phase, Sunny Boy Storage- Permanently-connected, Transformerless Multimode - Grid Support Utility Interactive and Standalone functionality - Inverter | 3.8129 | 240 | 96.5 | [12/14/2017] | [1.00.04.R] | 2018-10-15 | N | N |  | 6.53 |  |  | 220 | 360 | 550 | 0.38129 | 0.76257 | 1.1439 | 1.9064 | 2.8596 | 3.8129 | 92.6936 | 95.522 | 96.0988 | 96.4348 | 96.4124 | 96.2874 | 96.18 | 93.606 | 96.4562 | 97.1022 | 97.4216 | 97.4656 | 97.3776 | 97.2035 | 88.5644 | 94.7228 | 96.0868 | 96.8482 | 97.0258 | 97.0206 | 96.422 | SMA America3.81286SBS3.8-US-10 [240V] | 2018-07-02 | 2018-10-15
SMA America | SB3.8-1SP-US-40 [240V] | Y | Y | Y | 3.8 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter | 3.85 | 240 | 96.5 | [2/21/2017] | [02.03.00.R] | 2018-10-15 | Y | N |  | 5.39 |  |  | 195 | 365 | 480 | 0.38543 | 0.77085 | 1.1563 | 1.9271 | 2.8907 | 3.8543 | 92.6814 | 95.3701 | 96.0702 | 96.4553 | 96.4439 | 96.2328 | 96.1867 | 93.6802 | 96.4354 | 96.8953 | 97.4346 | 97.5877 | 97.468 | 97.2525 | 90.8056 | 95.3096 | 96.4049 | 96.9099 | 97.1557 | 97.3074 | 96.6753 | SMA America3.85SB3.8-1SP-US-40 [240V] | 2018-08-01 | 2018-10-15
SMA America | SB3.8-1TP-US-40 [240V] | Y | Y | Y | 3.8 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 3.85 | 240 | 96.5 | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | Y | N |  | 5.39 |  |  | 195 | 365 | 480 | 0.38543 | 0.77085 | 1.1563 | 1.9271 | 2.8907 | 3.8543 | 92.6814 | 95.3701 | 96.0702 | 96.4553 | 96.4439 | 96.2328 | 96.1867 | 93.6802 | 96.4354 | 96.8953 | 97.4346 | 97.5877 | 97.468 | 97.2525 | 90.8056 | 95.3096 | 96.4049 | 96.9099 | 97.1557 | 97.3074 | 96.6753 | SMA America3.85SB3.8-1TP-US-40 [240V] | 2018-08-01 | 2018-10-15
SMA America | SB3800TL-US-22 [208V] | Y | N | N | 3.8 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 3.85 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.53 |  |  | 100 | 400 | 480 | 0.39 | 0.77 | 1.16 | 1.93 | 2.89 | 3.85 | 93.8 | 95.7 | 96.1 | 96.1 | 96 | 95.6 | 95.9 | 93.7 | 96.2 | 97.1 | 97.2 | 97.1 | 96.9 | 96.9 | 93.7 | 96 | 96.7 | 97 | 97 | 96.9 | 96.8 | SMA America3.85SB3800TL-US-22 [208V]
SMA America | SB3800TL-US-22 [240V] | Y | N | N | 3 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 3.85 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.49 |  |  | 100 | 400 | 480 | 0.39 | 0.77 | 1.16 | 1.93 | 2.89 | 3.85 | 93.3 | 95.6 | 96 | 96.2 | 96 | 95.7 | 95.9 | 95.3 | 96.9 | 97.4 | 97.5 | 97.5 | 97.4 | 97.4 | 93.1 | 96.4 | 97 | 97.4 | 97.3 | 97.3 | 97.1 | SMA America3.85SB3800TL-US-22 [240V]
SMA America | SB4000US [240V] | Y | N | N | 4 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 4 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.17 |  |  | 100 | 310 | 480 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 92.5 | 96.4 | 96.8 | 96.7 | 96.4 | 96 | 96.3 | 91.9 | 96.2 | 96.3 | 96.5 | 96 | 95.5 | 96 | 89.1 | 94.7 | 95.6 | 95.5 | 95.3 | 94.9 | 95.1 | SMA America4SB4000US [240V]
SMA America | SB4000US-12 [240V] | Y | N | N | 4 kW, 240 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 4 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.17 |  |  | 100 | 310 | 480 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 92.5 | 96.4 | 96.8 | 96.7 | 96.4 | 96 | 96.3 | 91.9 | 96.2 | 96.3 | 96.5 | 96 | 95.5 | 96 | 89.1 | 94.7 | 95.6 | 95.5 | 95.3 | 94.9 | 95.1 | SMA America4SB4000US-12 [240V]
SMA America | Sunny Island SI4548 | Y | N | N | 4 kW multi-mode Inverter | 4 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0 |  |  | 100 | 48 | 63 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 93.8 | 94.5 | 95.9 | 95.3 | 94.8 | 93.5 | 94.9 | 93.8 | 94.6 | 95.6 | 95.2 | 94.6 | 93.2 | 94.7 | 93.8 | 95.1 | 95.1 | 94.8 | 94.2 | 92.8 | 94.4 | SMA America4Sunny Island SI4548
SMA America | SB3800US [240V] | Y | N | N | 3.8 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 4.05 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 100 | 310 | 480 | 0.405 | 0.81 | 1.215 | 2.025 | 3.038 | 4.05 | 94.59 | 96.32 | 96.71 | 96.78 | 96.38 | 95.83 | 96.4 | 93.53 | 95.5 | 96.13 | 96.31 | 96.03 | 95.47 | 95.95 | 91.56 | 94.38 | 95.28 | 95.58 | 95.55 | 95.08 | 95.29 | SMA America4.05SB3800US [240V]
SMA America | SB3800US-12 [240V] | Y | N | N | 3.8 kW, 240 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 4.05 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 100 | 310 | 480 | 0.405 | 0.81 | 1.215 | 2.025 | 3.038 | 4.05 | 94.59 | 96.32 | 96.71 | 96.78 | 96.38 | 95.83 | 96.4 | 93.53 | 95.5 | 96.13 | 96.31 | 96.03 | 95.47 | 95.95 | 91.56 | 94.38 | 95.28 | 95.58 | 95.55 | 95.08 | 95.29 | SMA America4.05SB3800US-12 [240V]
SMA America | SB4000TL-US-22 [208V] | Y | N | N | 4 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 4.05 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.53 |  |  | 100 | 400 | 480 | 0.41 | 0.81 | 1.22 | 2.03 | 3.04 | 4.05 | 94.1 | 95.8 | 96.1 | 96.1 | 95.9 | 95.4 | 95.9 | 94.1 | 96.3 | 97.2 | 97.2 | 97.1 | 96.8 | 97 | 93.4 | 96.2 | 96.8 | 97 | 97 | 96.8 | 96.8 | SMA America4.05SB4000TL-US-22 [208V]
SMA America | SB4000TL-US-22 [240V] | Y | N | N | 3.8 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 4.05 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.49 |  |  | 100 | 400 | 480 | 0.41 | 0.81 | 1.22 | 2.03 | 3.04 | 4.05 | 93.5 | 95.6 | 96 | 96.2 | 96 | 95.7 | 95.9 | 95.3 | 97.1 | 97.4 | 97.5 | 97.5 | 97.3 | 97.4 | 93.8 | 96.4 | 97.2 | 97.4 | 97.4 | 97.3 | 97.2 | SMA America4.05SB4000TL-US-22 [240V]
SMA America | SB5000TL-US-22 [208V] | Y | N | N | 5 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter | 4.58 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.53 |  |  | 100 | 400 | 480 | 0.46 | 0.92 | 1.37 | 2.29 | 3.43 | 4.58 | 94.5 | 95.9 | 96.1 | 96.1 | 95.7 | 95.4 | 95.8 | 94.7 | 96.5 | 97.2 | 97.1 | 97 | 96.7 | 96.9 | 94 | 96.5 | 96.9 | 97 | 96.9 | 96.6 | 96.8 | SMA America4.58SB5000TL-US-22 [208V]
SMA America | SB5000US [208V] | Y | N | N | 5 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.7 | 96.2 | 96.7 | 96.7 | 96.3 | 96.4 | 89.9 | 95 | 95.7 | 96.2 | 96.4 | 96 | 95.9 | 86.3 | 92.5 | 94.3 | 95 | 95.1 | 95 | 94.5 | SMA America5SB5000US [208V]
SMA America | SB5000US [240V] | Y | N | N | 5 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91 | 95.7 | 96.2 | 96.8 | 96.8 | 96.5 | 96.4 | 89.7 | 94.9 | 95.7 | 96.2 | 96.4 | 96.2 | 95.9 | 86.2 | 92.5 | 94.3 | 95.2 | 95.2 | 95.1 | 94.6 | SMA America5SB5000US [240V]
SMA America | SB5000US [277V] | Y | N | N | 5 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.8 | 96.5 | 96.8 | 96.5 | 96.6 | 96.3 | 90 | 95 | 95.8 | 96.2 | 96.5 | 96.2 | 96 | 86.3 | 92.3 | 94.4 | 95.2 | 95.2 | 95.2 | 94.6 | SMA America5SB5000US [277V]
SMA America | SB5000US-11 [208V] | Y | N | N | 5 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.7 | 96.2 | 96.7 | 96.7 | 96.3 | 96.4 | 89.9 | 95 | 95.7 | 96.2 | 96.4 | 96 | 95.9 | 86.3 | 92.5 | 94.3 | 95 | 95.1 | 95 | 94.5 | SMA America5SB5000US-11 [208V]
SMA America | SB5000US-11 [240V] | Y | N | N | 5 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91 | 95.7 | 96.2 | 96.8 | 96.8 | 96.5 | 96.4 | 89.7 | 94.9 | 95.7 | 96.2 | 96.4 | 96.2 | 95.9 | 86.2 | 92.5 | 94.3 | 95.2 | 95.2 | 95.1 | 94.6 | SMA America5SB5000US-11 [240V]
SMA America | SB5000US-11 [277V] | Y | N | N | 5 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 5 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.8 | 96.5 | 96.8 | 96.5 | 96.6 | 96.3 | 90 | 95 | 95.8 | 96.2 | 96.5 | 96.2 | 96 | 86.3 | 92.3 | 94.4 | 95.2 | 95.2 | 95.2 | 94.6 | SMA America5SB5000US-11 [277V]
SMA America | SB5000US-12 [208V] | Y | N | N | 5 kW, 208 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.7 | 96.2 | 96.7 | 96.7 | 96.3 | 96.4 | 89.9 | 95 | 95.7 | 96.2 | 96.4 | 96 | 95.9 | 86.3 | 92.5 | 94.3 | 95 | 95.1 | 95 | 94.5 | SMA America5SB5000US-12 [208V]
SMA America | SB5000US-12 [240V] | Y | N | N | 5 kW, 240 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91 | 95.7 | 96.2 | 96.8 | 96.8 | 96.5 | 96.4 | 89.7 | 94.9 | 95.7 | 96.2 | 96.4 | 96.2 | 95.9 | 86.2 | 92.5 | 94.3 | 95.2 | 95.2 | 95.1 | 94.6 | SMA America5SB5000US-12 [240V]
SMA America | SB5000US-12 [277V] | Y | N | N | 5 kW, 277 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 5 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.8 | 96.5 | 96.8 | 96.5 | 96.6 | 96.3 | 90 | 95 | 95.8 | 96.2 | 96.5 | 96.2 | 96 | 86.3 | 92.3 | 94.4 | 95.2 | 95.2 | 95.2 | 94.6 | SMA America5SB5000US-12 [277V]
SMA America | Sunny Island SI6048 | Y | N | N | 5 kW multi-mode Inverter | 5 |  | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0 |  |  | 41 | 48 | 63 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.8 | 95.9 | 95.9 | 94.8 | 93.5 | 92.1 | 94.1 | 93.8 | 95.6 | 95.7 | 94.6 | 93.2 | 91.7 | 93.9 | 93.8 | 95.1 | 95.2 | 94.2 | 92.8 | 91.4 | 93.5 | SMA America5Sunny Island SI6048
SMA America | SBS5.0-US-10 [240V] | N | Y | Y | 5.0 kW, 240 Vac, 1-phase, Sunny Boy Storage- Permanently-connected, Transformerless Multimode - Grid Support Utility Interactive and Standalone functionality - Inverter | 5.016 | 240 | 96.5 | [12/14/2017] | [1.00.04.R] | 2018-10-15 | N | N |  | 6.53 |  |  | 220 | 360 | 550 | 0.5016 | 1.0032 | 1.5048 | 2.508 | 3.762 | 5.016 | 93.7572 | 95.9944 | 96.3534 | 96.4338 | 96.3082 | 96.1104 | 96.2124 | 94.6136 | 96.9314 | 97.3164 | 97.4512 | 97.3954 | 97.2108 | 97.2539 | 92.4176 | 95.7396 | 96.5304 | 96.9972 | 97.034 | 96.5908 | 96.6943 | SMA America5.01595SBS5.0-US-10 [240V] | 2018-07-02 | 2018-10-15
SMA America | SB5.0-1SP-US-40 [240V] | Y | Y | Y | 5.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter | 5.05 | 240 | 97 | [2/21/2017] | [02.03.00.R] | 2018-10-15 | Y | N |  | 5.21 |  |  | 220 | 365 | 480 | 0.51 | 1.01 | 1.52 | 2.53 | 3.79 | 5.05 | 93.3 | 96 | 96.5 | 96.7 | 96.6 | 96.4 | 96.4 | 93.4 | 96.9 | 97.2 | 97.5 | 97.4 | 97.2 | 97.2 | 91.2 | 96.2 | 96.8 | 97.2 | 97.4 | 97.3 | 97 | SMA America5.05SB5.0-1SP-US-40 [240V] | 2018-08-01 | 2018-10-15
SMA America | SB5.0-1TP-US-40 [240V] | Y | Y | Y | 5.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 5.05 | 240 | 97 | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | Y | N |  | 5.21 |  |  | 220 | 365 | 480 | 0.51 | 1.01 | 1.52 | 2.53 | 3.79 | 5.05 | 93.3 | 96 | 96.5 | 96.7 | 96.6 | 96.4 | 96.4 | 93.4 | 96.9 | 97.2 | 97.5 | 97.4 | 97.2 | 97.2 | 91.2 | 96.2 | 96.8 | 97.2 | 97.4 | 97.3 | 97 | SMA America5.05SB5.0-1TP-US-40 [240V] | 2018-08-01 | 2018-10-15
SMA America | SB5000TL-US-22 [240V] | Y | N | N | 5 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 5.05 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.49 |  |  | 100 | 400 | 480 | 0.51 | 1.01 | 1.52 | 2.53 | 3.79 | 5.05 | 94.3 | 95.9 | 96.2 | 96.2 | 95.8 | 95.5 | 95.8 | 95.9 | 97.2 | 97.6 | 97.6 | 97.3 | 97 | 97.3 | 95.1 | 97 | 97.2 | 97.5 | 97.3 | 97.1 | 97.2 | SMA America5.05SB5000TL-US-22 [240V]
SMA America | SB5.0-1SP-US-40 [208V] | Y | Y | Y | 5.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter | 5.06 | 208 | 96.5 | [2/21/2017] | [02.03.00.R] | 2018-10-15 | Y | N |  | 5.06 |  |  | 220 | 365 | 480 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.06 | 94.7 | 96.3 | 96.6 | 96.6 | 96.4 | 96 | 96.4 | 94.7 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 97 | 91.1 | 96.1 | 96.7 | 96.9 | 97 | 96.8 | 96.6 | SMA America5.06SB5.0-1SP-US-40 [208V] | 2018-08-01 | 2018-10-15
SMA America | SB5.0-1TP-US-40 [208V] | Y | Y | Y | 5.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 5.06 | 208 | 96.5 | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | Y | N |  | 5.06 |  |  | 220 | 365 | 480 | 0.51 | 1.01 | 1.52 | 2.53 | 3.8 | 5.06 | 94.7 | 96.3 | 96.6 | 96.6 | 96.4 | 96 | 96.4 | 94.7 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 97 | 91.1 | 96.1 | 96.7 | 96.9 | 97 | 96.8 | 96.6 | SMA America5.06SB5.0-1TP-US-40 [208V] | 2018-08-01 | 2018-10-15
SMA America | SB6000TL-US-22 [208V] | Y | N | N | 5 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 5.2 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.51 |  |  | 100 | 412 | 480 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 94.5 | 96 | 96.3 | 96.3 | 96 | 95.6 | 96 | 94.3 | 96.4 | 96.8 | 97 | 96.9 | 96.7 | 96.8 | 93.3 | 95.9 | 96.5 | 96.7 | 96.7 | 96.5 | 96.5 | SMA America5.2SB6000TL-US-22 [208V]
SMA America | SB6000U [208V] | Y | N | N | 6000 W, 208 Vac Sunny Boy Utility Interactive Inverter with meter | 5.2 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2042 |  |  | 100 | 334 | 480 | 0.57 | 1.11 | 1.63 | 2.7 | 4.01 | 5.32 | 93.09 | 95.24 | 95.6 | 95.61 | 94.78 | 94.16 | 94.98 | 91.6 | 94.65 | 95.15 | 95.27 | 94.63 | 93.76 | 94.66 | 88.63 | 92.33 | 93.49 | 93.94 | 93.69 | 93.1 | 93.42 | SMA America5.2SB6000U [208V]
SMA America | SB6.0-1SP-US-40 [208V] | Y | Y | Y | 6.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter | 5.49 | 208 | 96.5 | [2/21/2017] | [02.03.00.R] | 2018-10-15 | Y | N |  | 5.06 |  |  | 220 | 365 | 480 | 0.55 | 1.1 | 1.65 | 2.75 | 4.12 | 5.49 | 94.8 | 96.3 | 96.6 | 96.6 | 96.4 | 96 | 96.4 | 94.8 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 97 | 91.7 | 96.2 | 96.7 | 96.8 | 97 | 96.8 | 96.6 | SMA America5.49SB6.0-1SP-US-40 [208V] | 2018-08-01 | 2018-10-15
SMA America | SB6.0-1TP-US-40 [208V] | Y | Y | Y | 6.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 5.49 | 208 | 96.5 | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | Y | N |  | 5.06 |  |  | 220 | 365 | 480 | 0.55 | 1.1 | 1.65 | 2.75 | 4.12 | 5.49 | 94.8 | 96.3 | 96.6 | 96.6 | 96.4 | 96 | 96.4 | 94.8 | 96.7 | 97.1 | 97.2 | 97.1 | 96.8 | 97 | 91.7 | 96.2 | 96.7 | 96.8 | 97 | 96.8 | 96.6 | SMA America5.49SB6.0-1TP-US-40 [208V] | 2018-08-01 | 2018-10-15
SMA America | SB6000TL-US [208V] | Y | N | N | 6 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter | 6 | 208 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 97.6 | 98.4 | 98.6 | 98.5 | 98.4 | 97.9 | 98.4 | 97.4 | 98.2 | 98.4 | 98.3 | 98.1 | 97.7 | 98.1 | 96.5 | 97.6 | 97.9 | 98 | 97.9 | 97.6 | 97.8 | SMA America6SB6000TL-US [208V]
SMA America | SB6000TL-US [240V] | Y | N | N | 6 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter | 6 | 240 | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 97.4 | 98.4 | 98.7 | 98.6 | 98.5 | 98.3 | 98.5 | 97.4 | 98.3 | 98.5 | 98.6 | 98.5 | 98.1 | 98.4 | 96.5 | 97.6 | 98.1 | 98.3 | 98.3 | 98.1 | 98.2 | SMA America6SB6000TL-US [240V]
SMA America | SB6000TL-US-12 [208V] | Y | N | N | 6 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 6 | 208 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 97.6 | 98.4 | 98.6 | 98.5 | 98.4 | 97.9 | 98.4 | 97.4 | 98.2 | 98.4 | 98.3 | 98.1 | 97.7 | 98.1 | 96.5 | 97.6 | 97.9 | 98 | 97.9 | 97.6 | 97.8 | SMA America6SB6000TL-US-12 [208V]
SMA America | SB6000TL-US-12 [240V] | Y | N | N | 6 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 6 | 240 | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 97.4 | 98.4 | 98.7 | 98.6 | 98.5 | 98.3 | 98.5 | 97.4 | 98.3 | 98.5 | 98.6 | 98.5 | 98.1 | 98.4 | 96.5 | 97.6 | 98.1 | 98.3 | 98.3 | 98.1 | 98.2 | SMA America6SB6000TL-US-12 [240V]
SMA America | SB6000TL-US-22 [240V] | Y | N | N | 6 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter | 6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 95 | 96.3 | 96.4 | 96.4 | 96.1 | 95.7 | 96.1 | 95.6 | 97.1 | 97.3 | 97.4 | 97.3 | 96.9 | 97.2 | 94.5 | 96.5 | 96.9 | 97.1 | 97.1 | 96.9 | 96.9 | SMA America6SB6000TL-US-22 [240V]
SMA America | SB6000U [240V] | Y | N | N | 6 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2042 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.17 | 95.47 | 95.76 | 95.48 | 94.86 | 94.2 | 95.03 | 92.3 | 94.88 | 95.22 | 95.23 | 94.58 | 93.82 | 94.68 | 90.1 | 93.3 | 94.14 | 94.25 | 93.93 | 93.17 | 93.8 | SMA America6SB6000U [240V]
SMA America | SB6000U [277V] | Y | N | N | 6 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 277 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.23 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 93.09 | 95.21 | 95.88 | 95.62 | 95.15 | 94.53 | 95.22 | 91.88 | 94.75 | 95.4 | 95.23 | 94.84 | 94.22 | 94.83 | 89.79 | 93.18 | 94.13 | 94.4 | 94.02 | 93.42 | 93.87 | SMA America6SB6000U [277V]
SMA America | SB6000US [208V] | Y | N | N | 6 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.8 | 96.5 | 96.9 | 96.5 | 95.9 | 96.3 | 91.2 | 95.6 | 95.9 | 96.3 | 96.1 | 95.6 | 95.9 | 88 | 93.5 | 94.8 | 94.6 | 94.9 | 94.6 | 94.5 | SMA America6SB6000US [208V]
SMA America | SB6000US [240V] | Y | N | N | 6 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 96.1 | 96.5 | 96.8 | 96.7 | 96 | 96.4 | 91.3 | 95.6 | 96 | 96.3 | 96.3 | 95.9 | 96 | 87.9 | 93.6 | 94.8 | 95.1 | 95 | 94.8 | 94.7 | SMA America6SB6000US [240V]
SMA America | SB6000US [277V] | Y | N | N | 6 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.3 | 96 | 96.7 | 97 | 96.7 | 96.5 | 96.5 | 91.3 | 95.6 | 96.2 | 96.4 | 96.4 | 96 | 96.1 | 87.8 | 93.6 | 94.9 | 95.2 | 95.1 | 94.9 | 94.7 | SMA America6SB6000US [277V]
SMA America | SB6000US-11 [208V] | Y | N | N | 6 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.8 | 96.5 | 96.9 | 96.5 | 95.9 | 96.3 | 91.2 | 95.6 | 95.9 | 96.3 | 96.1 | 95.6 | 95.9 | 88 | 93.5 | 94.8 | 94.6 | 94.9 | 94.6 | 94.5 | SMA America6SB6000US-11 [208V]
SMA America | SB6000US-11 [240V] | Y | N | N | 6 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 96.1 | 96.5 | 96.8 | 96.7 | 96 | 96.4 | 91.3 | 95.6 | 96 | 96.3 | 96.3 | 95.9 | 96 | 87.9 | 93.6 | 94.8 | 95.1 | 95 | 94.8 | 94.7 | SMA America6SB6000US-11 [240V]
SMA America | SB6000US-11 [277V] | Y | N | N | 6 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.3 | 96 | 96.7 | 97 | 96.7 | 96.5 | 96.5 | 91.3 | 95.6 | 96.2 | 96.4 | 96.4 | 96 | 96.1 | 87.8 | 93.6 | 94.9 | 95.2 | 95.1 | 94.9 | 94.7 | SMA America6SB6000US-11 [277V]
SMA America | SB6000US-12 [208V] | Y | N | N | 6 kW, 208 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.8 | 96.5 | 96.9 | 96.5 | 95.9 | 96.3 | 91.2 | 95.6 | 95.9 | 96.3 | 96.1 | 95.6 | 95.9 | 88 | 93.5 | 94.8 | 94.6 | 94.9 | 94.6 | 94.5 | SMA America6SB6000US-12 [208V]
SMA America | SB6000US-12 [240V] | Y | N | N | 6 kW, 240 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 6 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 96.1 | 96.5 | 96.8 | 96.7 | 96 | 96.4 | 91.3 | 95.6 | 96 | 96.3 | 96.3 | 95.9 | 96 | 87.9 | 93.6 | 94.8 | 95.1 | 95 | 94.8 | 94.7 | SMA America6SB6000US-12 [240V]
SMA America | SB6000US-12 [277V] | Y | N | N | 6 kW, 277 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.3 | 96 | 96.7 | 97 | 96.7 | 96.5 | 96.5 | 91.3 | 95.6 | 96.2 | 96.4 | 96.4 | 96 | 96.1 | 87.8 | 93.6 | 94.9 | 95.2 | 95.1 | 94.9 | 94.7 | SMA America6SB6000US-12 [277V]
SMA America | SB7000TL-US-22 [208V] | Y | N | N | 7 kW (208 Vac) Utility Interactive Inverter | 6.01 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.395 |  |  | 100 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.51 | 6.01 | 94.2 | 95.9 | 96.2 | 96.2 | 95.9 | 95.5 | 95.9 | 93.1 | 96.2 | 96.6 | 96.8 | 96.7 | 96.5 | 96.5 | 91.7 | 95.8 | 96.3 | 96.7 | 96.6 | 96.4 | 96.4 | SMA America6.01SB7000TL-US-22 [208V]
SMA America | SBS6.0-US-10 [240V] | N | Y | Y | 6.0 kW, 240 Vac, 1-phase, Sunny Boy Storage- Permanently-connected, Transformerless Multimode - Grid Support Utility Interactive and Standalone functionality - Inverter | 6.022 | 240 | 96.5 | [12/14/2017] | [1.00.04.R] | 2018-10-15 | N | N |  | 6.53 |  |  | 220 | 360 | 550 | 0.6022 | 1.2044 | 1.8066 | 3.011 | 4.5165 | 6.022 | 94.4642 | 96.1546 | 96.429 | 96.4004 | 96.1916 | 95.9566 | 96.1812 | 95.8482 | 97.1984 | 97.4014 | 97.4512 | 97.284 | 96.9922 | 97.2569 | 93.2534 | 96.2388 | 96.799 | 97.0266 | 96.9664 | 96.8002 | 96.7657 | SMA America6.02196SBS6.0-US-10 [240V] | 2018-07-02 | 2018-10-15
SMA America | SB6.0-1SP-US-40 [240V] | Y | Y | Y | 6.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter | 6.05 | 240 | 97 | [2/21/2017] | [02.03.00.R] | 2018-10-15 | Y | N |  | 5.21 |  |  | 220 | 365 | 480 | 0.61 | 1.21 | 1.82 | 3.03 | 4.54 | 6.05 | 94.7 | 96.3 | 96.6 | 96.6 | 96.5 | 96.1 | 96.4 | 95.4 | 97.1 | 97.4 | 97.6 | 97.3 | 97 | 97.3 | 93.4 | 96.5 | 97 | 97.3 | 97.3 | 97 | 97.1 | SMA America6.05SB6.0-1SP-US-40 [240V] | 2018-08-01 | 2018-10-15
SMA America | SB6.0-1TP-US-40 [240V] | Y | Y | Y | 6.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 6.05 | 240 | 97 | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | Y | N |  | 5.21 |  |  | 220 | 365 | 480 | 0.61 | 1.21 | 1.82 | 3.03 | 4.54 | 6.05 | 94.7 | 96.3 | 96.6 | 96.6 | 96.5 | 96.1 | 96.4 | 95.4 | 97.1 | 97.4 | 97.6 | 97.3 | 97 | 97.3 | 93.4 | 96.5 | 97 | 97.3 | 97.3 | 97 | 97.1 | SMA America6.05SB6.0-1TP-US-40 [240V] | 2018-08-01 | 2018-10-15
SMA America | SB7700TL-US-22 [208V] | Y | N | N | 7 kW (208 Vac) Utility Interactive Inverter | 6.73 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.395 |  |  | 100 | 400 | 480 | 0.67 | 1.35 | 2.02 | 3.37 | 5.05 | 6.73 | 94.9 | 96.2 | 96.4 | 96.3 | 95.9 | 95.2 | 96 | 94.2 | 96.4 | 96.7 | 96.8 | 96.7 | 96.3 | 96.6 | 94.7 | 96.1 | 96.4 | 96.7 | 96.7 | 96.4 | 96.6 | SMA America6.73SB7700TL-US-22 [208V]
SMA America | SB7.0-1SP-US-40 [208V] | Y | Y | Y | 7.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter | 6.92 | 208 | 96.5 | [2/21/2017] | [02.03.00.R] | 2018-10-15 | Y | N |  | 5.37 |  |  | 245 | 365 | 480 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.4191 | 96.4997 | 96.8805 | 96.3931 | 96.1295 | 95.5922 | 96.2382 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 96.7272 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048 | 96.3696 | SMA America6.92SB7.0-1SP-US-40 [208V] | 2018-08-01 | 2018-10-15
SMA America | SB7.0-1TP-US-40 [208V] | Y | Y | Y | 7.0 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 6.92 | 208 | 96.5 | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | Y | N |  | 5.37 |  |  | 245 | 365 | 480 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.4191 | 96.4997 | 96.8805 | 96.3931 | 96.1295 | 95.5922 | 96.2382 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 96.7272 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048 | 96.3696 | SMA America6.92SB7.0-1TP-US-40 [208V] | 2018-08-01 | 2018-10-15
SMA America | SB7.7-1SP-US-40 [208V] | Y | Y | Y | 7.7 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter | 6.92 | 208 | 96.5 | [2/21/2017] | [02.03.00.R] | 2018-10-15 | Y | N |  | 5.37 |  |  | 270 | 365 | 480 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.6881 | 96.7105 | 96.729 | 96.5396 | 96.0507 | 95.6947 | 96.2354 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 96.7272 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048 | 96.3696 | SMA America6.92SB7.7-1SP-US-40 [208V] | 2018-08-01 | 2018-10-15
SMA America | SB7.7-1TP-US-40 [208V] | Y | Y | Y | 7.7 kW, 208 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 6.92 | 208 | 96.5 | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | Y | N |  | 5.37 |  |  | 270 | 365 | 480 | 0.69229 | 1.3846 | 2.0769 | 3.4615 | 5.1922 | 6.9229 | 95.6881 | 96.7105 | 96.729 | 96.5396 | 96.0507 | 95.6947 | 96.2354 | 95.3532 | 96.6628 | 97.1412 | 97.0424 | 96.6648 | 96.2346 | 96.7272 | 94.1363 | 96.3475 | 96.6764 | 96.6839 | 96.3523 | 96.3048 | 96.3696 | SMA America6.92SB7.7-1TP-US-40 [208V] | 2018-08-01 | 2018-10-15
SMA America | SB7000TL-US [208V] | Y | N | N | 7 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter | 7 | 208 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 97.8 | 98.6 | 98.6 | 98.4 | 98.2 | 97.6 | 98.3 | 97.7 | 98.3 | 98.4 | 98.3 | 97.9 | 97.5 | 98.1 | 96.9 | 97.8 | 98 | 98 | 97.8 | 97.4 | 97.8 | SMA America7SB7000TL-US [208V]
SMA America | SB7000TL-US [240V] | Y | N | N | 7 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter | 7 | 240 | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 97.7 | 98.5 | 98.7 | 98.6 | 98.4 | 98 | 98.4 | 97.8 | 98.4 | 98.5 | 98.2 | 98.3 | 97.8 | 98.3 | 96.8 | 97.8 | 98.2 | 98.3 | 98.2 | 97.9 | 98.1 | SMA America7SB7000TL-US [240V]
SMA America | SB7000TL-US-12 [208V] | Y | N | N | 7 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 7 | 208 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 97.8 | 98.6 | 98.6 | 98.4 | 98.2 | 97.6 | 98.3 | 97.7 | 98.3 | 98.4 | 98.3 | 97.9 | 97.5 | 98.1 | 96.9 | 97.8 | 98 | 98 | 97.8 | 97.4 | 97.8 | SMA America7SB7000TL-US-12 [208V]
SMA America | SB7000TL-US-12 [240V] | Y | N | N | 6 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 7 | 240 | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 97.7 | 98.5 | 98.7 | 98.6 | 98.4 | 98 | 98.4 | 97.8 | 98.4 | 98.5 | 98.2 | 98.3 | 97.8 | 98.3 | 96.8 | 97.8 | 98.2 | 98.3 | 98.2 | 97.9 | 98.1 | SMA America7SB7000TL-US-12 [240V]
SMA America | SB7000US [208V] | Y | N | N | 7 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 94 | 96.3 | 97.1 | 96.7 | 96.2 | 95.4 | 96.3 | 92.7 | 96.1 | 96.1 | 96.2 | 95.9 | 95.3 | 95.9 | 89.7 | 94.2 | 95 | 94.9 | 94.8 | 94.1 | 94.6 | SMA America7SB7000US [208V]
SMA America | SB7000US [240V] | Y | N | N | 7 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.2 | 96.8 | 96.9 | 96.5 | 95.8 | 96.5 | 92.3 | 96.1 | 96.1 | 96.4 | 96.1 | 95.6 | 96 | 89.3 | 94.3 | 95.1 | 95.6 | 95 | 94.7 | 94.8 | SMA America7SB7000US [240V]
SMA America | SB7000US [277V] | Y | N | N | 7 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.3 | 96.8 | 97 | 96.5 | 95.9 | 96.5 | 92.5 | 96.1 | 96.3 | 96.5 | 96.2 | 95.6 | 96.1 | 89.3 | 94.2 | 95.2 | 95 | 95.1 | 94.6 | 94.8 | SMA America7SB7000US [277V]
SMA America | SB7000US-11 [208V] | Y | N | N | 7 kW, 208 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 94 | 96.3 | 97.1 | 96.7 | 96.2 | 95.4 | 96.3 | 92.7 | 96.1 | 96.1 | 96.2 | 95.9 | 95.3 | 95.9 | 89.7 | 94.2 | 95 | 94.9 | 94.8 | 94.1 | 94.6 | SMA America7SB7000US-11 [208V]
SMA America | SB7000US-11 [240V] | Y | N | N | 7 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.2 | 96.8 | 96.9 | 96.5 | 95.8 | 96.5 | 92.3 | 96.1 | 96.1 | 96.4 | 96.1 | 95.6 | 96 | 89.3 | 94.3 | 95.1 | 95.6 | 95 | 94.7 | 94.8 | SMA America7SB7000US-11 [240V]
SMA America | SB7000US-11 [277V] | Y | N | N | 7 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 7 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.3 | 96.8 | 97 | 96.5 | 95.9 | 96.5 | 92.5 | 96.1 | 96.3 | 96.5 | 96.2 | 95.6 | 96.1 | 89.3 | 94.2 | 95.2 | 95 | 95.1 | 94.6 | 94.8 | SMA America7SB7000US-11 [277V]
SMA America | SB7000US-12 [208V] | Y | N | N | 7 kW, 208 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 7 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 94 | 96.3 | 97.1 | 96.7 | 96.2 | 95.4 | 96.3 | 92.7 | 96.1 | 96.1 | 96.2 | 95.9 | 95.3 | 95.9 | 89.7 | 94.2 | 95 | 94.9 | 94.8 | 94.1 | 94.6 | SMA America7SB7000US-12 [208V]
SMA America | SB7000US-12 [240V] | Y | N | N | 7 kW, 240 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 7 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.2 | 96.8 | 96.9 | 96.5 | 95.8 | 96.5 | 92.3 | 96.1 | 96.1 | 96.4 | 96.1 | 95.6 | 96 | 89.3 | 94.3 | 95.1 | 95.6 | 95 | 94.7 | 94.8 | SMA America7SB7000US-12 [240V]
SMA America | SB7000US-12 [277V] | Y | N | N | 7 kW, 277 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 7 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.3 | 96.8 | 97 | 96.5 | 95.9 | 96.5 | 92.5 | 96.1 | 96.3 | 96.5 | 96.2 | 95.6 | 96.1 | 89.3 | 94.2 | 95.2 | 95 | 95.1 | 94.6 | 94.8 | SMA America7SB7000US-12 [277V]
SMA America | SB7000TL-US-22 [240V] | Y | N | N | 7 kW, 240 Vac Utility Interactive Inverter | 7.01 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 400 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.26 | 7.01 | 94.9 | 96.2 | 96.4 | 96.3 | 95.9 | 95.2 | 96 | 94.2 | 96.4 | 96.7 | 96.8 | 96.7 | 96.3 | 96.6 | 94.7 | 96.1 | 96.4 | 96.7 | 96.7 | 96.4 | 96.6 | SMA America7.01SB7000TL-US-22 [240V]
SMA America | SB7.0-1SP-US-40 [240V] | Y | Y | Y | 7.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter | 7.1 | 240 | 97 | [2/21/2017] | [02.03.00.R] | 2018-10-15 | Y | N |  | 5.1 |  |  | 245 | 365 | 480 | 0.70973 | 1.4195 | 2.1292 | 3.5486 | 5.323 | 7.0973 | 95.1025 | 96.5289 | 96.6286 | 96.7453 | 96.5202 | 96.0676 | 96.5016 | 95.7207 | 97.4129 | 97.4943 | 97.3994 | 96.9791 | 96.5173 | 97.0775 | 93.7611 | 96.5495 | 96.9096 | 97.1923 | 96.9996 | 96.6677 | 96.8607 | SMA America7.1SB7.0-1SP-US-40 [240V] | 2018-08-01 | 2018-10-15
SMA America | SB7.0-1TP-US-40 [240V] | Y | Y | Y | 7.0 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 7.1 | 240 | 97 | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | Y | N |  | 5.1 |  |  | 245 | 365 | 480 | 0.70973 | 1.4195 | 2.1292 | 3.5486 | 5.323 | 7.0973 | 95.1025 | 96.5289 | 96.6286 | 96.7453 | 96.5202 | 96.0676 | 96.5016 | 95.7207 | 97.4129 | 97.4943 | 97.3994 | 96.9791 | 96.5173 | 97.0775 | 93.7611 | 96.5495 | 96.9096 | 97.1923 | 96.9996 | 96.6677 | 96.8607 | SMA America7.1SB7.0-1TP-US-40 [240V] | 2018-08-01 | 2018-10-15
SMA America | SB8000US [240V] | Y | N | N | 8 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 7.6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.17 |  |  | 100 | 345 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.04 | 96.48 | 96.84 | 96.82 | 96.5 | 96.01 | 96.53 | 94.59 | 96.19 | 96.61 | 96.63 | 96.3 | 96.29 | 96.33 | 93.13 | 95.28 | 95.83 | 95.98 | 95.72 | 95.94 | 95.67 | SMA America7.6SB8000US [240V]
SMA America | SB8000US-11 [240V] | Y | N | N | 8 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 7.6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.17 |  |  | 100 | 345 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.04 | 96.48 | 96.84 | 96.82 | 96.5 | 96.01 | 96.53 | 94.59 | 96.19 | 96.61 | 96.63 | 96.3 | 96.29 | 96.33 | 93.13 | 95.28 | 95.83 | 95.98 | 95.72 | 95.94 | 95.67 | SMA America7.6SB8000US-11 [240V]
SMA America | SB8000US-12 [240V] | Y | N | N | 8 kW, 240 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 7.6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.17 |  |  | 100 | 345 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.04 | 96.48 | 96.84 | 96.82 | 96.5 | 96.01 | 96.53 | 94.59 | 96.19 | 96.61 | 96.63 | 96.3 | 96.29 | 96.33 | 93.13 | 95.28 | 95.83 | 95.98 | 95.72 | 95.94 | 95.67 | SMA America7.6SB8000US-12 [240V]
SMA America | SB7700TL-US-22 [240V] | Y | N | N | 7 kW, 240 Vac Utility Interactive Inverter | 7.7 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.464 |  |  | 100 | 400 | 480 | 0.77 | 1.54 | 2.31 | 3.85 | 5.78 | 7.7 | 94.8 | 96.4 | 96.6 | 96.7 | 96.4 | 96 | 96.4 | 94.4 | 97 | 97.3 | 97.3 | 97.1 | 96.8 | 97 | 92.7 | 96.5 | 96.9 | 97.1 | 97 | 96.7 | 96.8 | SMA America7.7SB7700TL-US-22 [240V]
SMA America | SB7.7-1SP-US-40 [240V] | Y | Y | Y | 7.7 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter | 7.76 | 240 | 97 | [2/21/2017] | [02.03.00.R] | 2018-10-15 | Y | N |  | 5.1 |  |  | 270 | 365 | 480 | 0.7758 | 1.5516 | 2.3274 | 3.879 | 5.8185 | 7.758 | 95.6595 | 96.7574 | 97.0783 | 96.9478 | 96.5357 | 96.0095 | 96.6371 | 96.0321 | 97.523 | 97.4427 | 97.3146 | 96.7877 | 96.3456 | 96.9614 | 94.6825 | 96.8252 | 97.0236 | 97.1923 | 96.8751 | 96.7284 | 96.862 | SMA America7.76SB7.7-1SP-US-40 [240V] | 2018-08-01 | 2018-10-15
SMA America | SB7.7-1TP-US-40 [240V] | Y | Y | Y | 7.7 kW, 240 Vac transformerless Grid Support Utility Interactive Inverter with revenue grade energy meter | 7.76 | 240 | 97 | [06/28/2018] | [V02.03.00.R] | 2018-10-15 | Y | N |  | 5.1 |  |  | 270 | 365 | 480 | 0.7758 | 1.5516 | 2.3274 | 3.879 | 5.8185 | 7.758 | 95.6595 | 96.7574 | 97.0783 | 96.9478 | 96.5357 | 96.0095 | 96.6371 | 96.0321 | 97.523 | 97.4427 | 97.3146 | 96.7877 | 96.3456 | 96.9614 | 94.6825 | 96.8252 | 97.0236 | 97.1923 | 96.8751 | 96.7284 | 96.862 | SMA America7.76SB7.7-1TP-US-40 [240V] | 2018-08-01 | 2018-10-15
SMA America | SB8000TL-US [240V] | Y | N | N | 8 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter | 8 | 240 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 345 | 379 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 97.9 | 98.5 | 98.6 | 98.6 | 98.3 | 97.8 | 98.4 | 98 | 98.5 | 98.5 | 98.6 | 98.2 | 97.5 | 98.3 | 97 | 98 | 98.3 | 98.3 | 98.1 | 97.7 | 98.1 | SMA America8SB8000TL-US [240V]
SMA America | SB8000TL-US-12 [208V] | Y | N | N | 8 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 8 | 208 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 98 | 98.6 | 98.6 | 98.4 | 98 | 97.2 | 98.1 | 97.9 | 98.4 | 98.4 | 98.2 | 97.8 | 97.2 | 97.9 | 97.1 | 97.9 | 97.9 | 98 | 97.7 | 97.2 | 97.7 | SMA America8SB8000TL-US-12 [208V]
SMA America | SB8000TL-US-12 [240V] | Y | N | N | 8 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 8 | 240 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 97.9 | 98.5 | 98.6 | 98.6 | 98.3 | 97.8 | 98.4 | 98 | 98.5 | 98.5 | 98.6 | 98.2 | 97.5 | 98.3 | 97 | 98 | 98.3 | 98.3 | 98.1 | 97.7 | 98.1 | SMA America8SB8000TL-US-12 [240V]
SMA America | SB8000US [277V] | Y | N | N | 8 kW, 277 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 |  |  | 100 | 345 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.12 | 96.22 | 96.48 | 96.46 | 96.17 | 95.56 | 96.2 | 94.85 | 95.86 | 96.28 | 96.25 | 95.89 | 95.28 | 95.93 | 93.45 | 95.01 | 95.41 | 95.51 | 95.24 | 94.7 | 95.21 | SMA America8SB8000US [277V]
SMA America | SB8000US-11 [277V] | Y | N | N | 8 kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 |  |  | 100 | 345 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.12 | 96.22 | 96.48 | 96.46 | 96.17 | 95.56 | 96.2 | 94.85 | 95.86 | 96.28 | 96.25 | 95.89 | 95.28 | 95.93 | 93.45 | 95.01 | 95.41 | 95.51 | 95.24 | 94.7 | 95.21 | SMA America8SB8000US-11 [277V]
SMA America | SB8000US-12 [277V] | Y | N | N | 8 kW, 277 Vac Sunny Boy Utility Interactive Inverter with arc detector with display | 8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 |  |  | 100 | 345 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.12 | 96.22 | 96.48 | 96.46 | 96.17 | 95.56 | 96.2 | 94.85 | 95.86 | 96.28 | 96.25 | 95.89 | 95.28 | 95.93 | 93.45 | 95.01 | 95.41 | 95.51 | 95.24 | 94.7 | 95.21 | SMA America8SB8000US-12 [277V]
SMA America | SB9000TL-US [208V] | Y | N | N | 9 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter | 9 | 208 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 98.2 | 98.6 | 98.5 | 98.3 | 97.7 | 96.9 | 97.9 | 98 | 98.4 | 98.4 | 98.2 | 97.6 | 96.9 | 97.8 | 97.4 | 97.9 | 98 | 97.9 | 97.5 | 96.9 | 97.6 | SMA America9SB9000TL-US [208V]
SMA America | SB9000TL-US [240V] | Y | N | N | 9 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter | 9 | 240 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 98 | 98.7 | 98.7 | 98.5 | 98.1 | 97.6 | 98.3 | 98.1 | 98.6 | 98.6 | 98.5 | 97.9 | 97.4 | 98.1 | 97.2 | 98.1 | 98.3 | 98.3 | 98 | 97.6 | 98 | SMA America9SB9000TL-US [240V]
SMA America | SB9000TL-US-12 [208V] | Y | N | N | 9 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 9 | 208 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 98.2 | 98.6 | 98.5 | 98.3 | 97.7 | 96.9 | 97.9 | 98 | 98.4 | 98.4 | 98.2 | 97.6 | 96.9 | 97.8 | 97.4 | 97.9 | 98 | 97.9 | 97.5 | 96.9 | 97.6 | SMA America9SB9000TL-US-12 [208V]
SMA America | SB9000TL-US-12 [240V] | Y | N | N | 9 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 9 | 240 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 0.9 | 1.8 | 2.7 | 4.5 | 6.75 | 9 | 98 | 98.7 | 98.7 | 98.5 | 98.1 | 97.6 | 98.3 | 98.1 | 98.6 | 98.6 | 98.5 | 97.9 | 97.4 | 98.1 | 97.2 | 98.1 | 98.3 | 98.3 | 98 | 97.6 | 98 | SMA America9SB9000TL-US-12 [240V]
SMA America | SB10000TL-US [240V] | Y | N | N | 10 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter | 10 | 240 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 98.3 | 98.7 | 98.6 | 98.5 | 97.9 | 97.3 | 98.2 | 98.2 | 98.5 | 98.6 | 98.4 | 97.7 | 97.1 | 98 | 97.4 | 98.2 | 98.3 | 98.3 | 97.8 | 97.3 | 97.9 | SMA America10SB10000TL-US [240V]
SMA America | SB10000TL-US-12 [240V] | Y | N | N | 10 kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 10 | 240 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 379 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 98.3 | 98.7 | 98.6 | 98.5 | 97.9 | 97.3 | 98.2 | 98.2 | 98.5 | 98.6 | 98.4 | 97.7 | 97.1 | 98 | 97.4 | 98.2 | 98.3 | 98.3 | 97.8 | 97.3 | 97.9 | SMA America10SB10000TL-US-12 [240V]
SMA America | SB10000TL-US [208V] | Y | N | N | 10 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter | 10.1 | 208 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 1.01 | 2.02 | 3.03 | 5.05 | 7.58 | 10.1 | 98.3 | 98.6 | 98.5 | 98.3 | 97.5 | 96.5 | 97.8 | 98.1 | 98.4 | 98.3 | 98 | 97.4 | 96.6 | 97.7 | 97.5 | 98 | 98 | 97.9 | 97.3 | 96.7 | 97.5 | SMA America10.1SB10000TL-US [208V]
SMA America | SB10000TL-US-12 [208V] | Y | N | N | 10 kW, 208 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 10.1 | 208 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.34 |  |  | 100 | 345 | 480 | 1.01 | 2.02 | 3.03 | 5.05 | 7.58 | 10.1 | 98.3 | 98.6 | 98.5 | 98.3 | 97.5 | 96.5 | 97.8 | 98.1 | 98.4 | 98.3 | 98 | 97.4 | 96.6 | 97.7 | 97.5 | 98 | 98 | 97.9 | 97.3 | 96.7 | 97.5 | SMA America10.1SB10000TL-US-12 [208V]
SMA America | SB11000TL-US [240V] | Y | N | N | 11kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter | 11.1 | 240 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 345 | 379 | 480 | 1.11 | 2.22 | 3.33 | 5.55 | 8.33 | 11.1 | 98.4 | 98.7 | 98.6 | 98.4 | 97.8 | 97 | 98 | 98.3 | 98.5 | 98.3 | 98.3 | 97.5 | 96.8 | 97.8 | 97.6 | 98.2 | 98.3 | 98.2 | 97.7 | 97.1 | 97.9 | SMA America11.1SB11000TL-US [240V]
SMA America | SB11000TL-US-12 [240V] | Y | N | N | 11kW, 240 Vac Sunny Boy transformerless Utility Interactive Inverter with arc detector | 11.1 | 240 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 345 | 379 | 480 | 1.11 | 2.22 | 3.33 | 5.55 | 8.33 | 11.1 | 98.4 | 98.7 | 98.6 | 98.4 | 97.8 | 97 | 98 | 98.3 | 98.5 | 98.3 | 98.3 | 97.5 | 96.8 | 97.8 | 97.6 | 98.2 | 98.3 | 98.2 | 97.7 | 97.1 | 97.9 | SMA America11.1SB11000TL-US-12 [240V]
SMA America | STP12000TL-US-10 [480V] | Y | Y | Y | Sunny Tripower TL-US 12 kW, 480Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter | 12 | 480 | 97.5 | [7/13/2017] | [2.03.04.R] | 2018-10-15 | Y | N |  | 1.79 |  |  | 300 | 675 | 800 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.8947 | 95.8254 | 96.4946 | 96.6907 | 96.6273 | 96.507 | 96.4293 | 94.8857 | 96.883 | 97.4944 | 97.777 | 97.8321 | 97.8114 | 97.6137 | 94.1548 | 97.204 | 97.7008 | 98.014 | 98.1838 | 98.1898 | 97.8803 | SMA America12STP12000TL-US-10 [480V] | 2018-08-01 | 2018-10-15
SMA America | STP15000TL-US-10 [480V] | Y | Y | Y | Sunny Tripower TL-US 15 kW, 480Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter | 15 | 480 | 97.5 | [7/13/2017] | [2.03.04.R] | 2018-10-15 | Y | N |  | 1.79 |  |  | 300 | 675 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.8557 | 96.2201 | 96.7314 | 96.6627 | 96.5254 | 96.3471 | 96.448 | 95.4959 | 97.1929 | 97.7963 | 97.8029 | 97.833 | 97.7774 | 97.694 | 95.5529 | 97.5151 | 97.9236 | 98.173 | 98.2148 | 98.1572 | 98.0267 | SMA America15STP15000TL-US-10 [480V] | 2018-08-01 | 2018-10-15
SMA America | STP20000TL-US-10 [480V] | Y | Y | Y | Sunny Tripower TL-US 20 kW, 480Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter | 20 | 480 | 97.5 | [7/13/2017] | [2.03.04.R] | 2018-10-15 | Y | N |  | 1.79 |  |  | 380 | 695 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 95.166 | 96.9605 | 97.2062 | 97.0835 | 96.9341 | 96.7051 | 96.9173 | 97.2288 | 98.2895 | 98.5099 | 98.5485 | 97.8368 | 97.7051 | 98.0588 | 96.4929 | 97.8688 | 98.1306 | 98.2198 | 98.1746 | 98.0422 | 98.0897 | SMA America20STP20000TL-US-10 [480V] | 2018-08-01 | 2018-10-15
SMA America | STP24000TL-US-10 [480V] | Y | Y | Y | Sunny Tripower TL-US 24 kW, 480Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter | 24.06 | 480 | 98 | [7/13/2017] | [2.03.04.R] | 2018-10-15 | Y | N |  | 1.79 |  |  | 450 | 712 | 800 | 2.406 | 4.812 | 7.218 | 12.03 | 18.045 | 24.06 | 96.0825 | 97.4242 | 97.4447 | 97.3151 | 97.1222 | 96.8659 | 97.1621 | 97.4599 | 98.348 | 98.5031 | 98.5314 | 98.4351 | 98.2665 | 98.4117 | 96.9099 | 98.0049 | 98.1886 | 98.2041 | 98.0766 | 97.8823 | 98.0569 | SMA America24.06STP24000TL-US-10 [480V] | 2018-08-01 | 2018-10-15
SMA America | STP30000TL-US-10 [480V] | Y | Y | Y | Sunny Tripower TL-US 30 kW, 480Vac, 3-phase, Transformerless Grid Support Utility Interactive Inverter | 30.01 | 480 | 98 | [7/6/2017] | [2.03.04.R] | 2018-10-15 | Y | N |  | 1.22 |  |  | 500 | 720 | 800 | 3.001 | 6.002 | 9.003 | 15.005 | 22.5075 | 30.01 | 96.588 | 97.716 | 97.926 | 97.98 | 97.838 | 97.622 | 97.8115 | 97.588 | 98.448 | 98.69 | 98.602 | 98.538 | 98.328 | 98.5167 | 97.026 | 98.06 | 98.452 | 98.386 | 98.282 | 98.08 | 98.2528 | SMA America30.01STP30000TL-US-10 [480V] | 2018-08-01 | 2018-10-15
SMA America | ST36 [208V] | Y | N | N | 36 kW, 208 Vac Sunny Tower Utility Interactive Inverter with display | 36 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.76 |  |  | 250 | 310 | 480 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 92.5 | 95.8 | 96.5 | 96.9 | 96.5 | 95.9 | 96.3 | 91.2 | 95.6 | 95.9 | 96.3 | 96.1 | 95.6 | 95.9 | 88 | 93.5 | 94.8 | 94.6 | 94.9 | 94.6 | 94.5 | SMA America36ST36 [208V]
SMA America | ST36 [240V] | Y | N | N | 36 kW, 240 Vac Sunny Tower Utility Interactive Inverter with display | 36 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.6 |  |  | 250 | 310 | 480 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 92.6 | 96.1 | 96.5 | 96.8 | 96.7 | 96 | 96.4 | 91.3 | 95.6 | 96 | 96.3 | 96.3 | 95.9 | 96 | 87.9 | 93.6 | 94.8 | 95.1 | 95 | 94.8 | 94.7 | SMA America36ST36 [240V]
SMA America | ST36 [277V] | Y | N | N | 36 kW, 277 Vac Sunny Tower Utility Interactive Inverter with display | 36 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 8.46 |  |  | 250 | 310 | 480 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 92.3 | 96 | 96.7 | 97 | 96.7 | 96.5 | 96.5 | 91.3 | 95.6 | 96.2 | 96.4 | 96.4 | 96 | 96.1 | 87.8 | 93.6 | 94.9 | 95.2 | 95.1 | 94.9 | 94.7 | SMA America36ST36 [277V]
SMA America | ST42 [208V] | Y | N | N | 42 kW, 208 Vac Sunny Tower Utility Interactive Inverter with display | 42 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 250 | 310 | 480 | 4.2 | 8.4 | 12.6 | 21 | 31.5 | 42 | 94 | 96.3 | 97.1 | 96.7 | 96.2 | 95.4 | 96.3 | 92.7 | 96.1 | 96.1 | 96.2 | 95.9 | 95.3 | 95.9 | 89.7 | 94.2 | 95 | 94.9 | 94.8 | 94.1 | 94.6 | SMA America42ST42 [208V]
SMA America | ST42 [240V] | Y | N | N | 42 kW, 240 Vac Sunny Tower Utility Interactive Inverter with display | 42 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.6 |  |  | 250 | 310 | 480 | 4.2 | 8.4 | 12.6 | 21 | 31.5 | 42 | 93.7 | 96.2 | 96.8 | 96.9 | 96.5 | 95.8 | 96.5 | 92.3 | 96.1 | 96.1 | 96.4 | 96.1 | 95.6 | 96 | 89.3 | 94.3 | 95.1 | 95.6 | 95 | 94.7 | 94.8 | SMA America42ST42 [240V]
SMA America | ST42 [277V] | Y | N | N | 42 kW, 277 Vac Sunny Tower Utility Interactive Inverter with display | 42 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 250 | 310 | 480 | 4.2 | 8.4 | 12.6 | 21 | 31.5 | 42 | 93.7 | 96.3 | 96.8 | 97 | 96.5 | 95.9 | 96.5 | 92.5 | 96.1 | 96.3 | 96.5 | 96.2 | 95.6 | 96.1 | 89.3 | 94.2 | 95.2 | 95 | 95.1 | 94.6 | 94.8 | SMA America42ST42 [277V]
SMA America | ST48 [240V] | Y | N | N | 45.6 kW, 240 Vac Sunny Tower Utility Interactive Inverter with display | 45.6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.01 |  |  | 300 | 345 | 480 | 4.56 | 9.12 | 13.68 | 22.8 | 34.2 | 45.6 | 95 | 96.5 | 96.8 | 96.8 | 96.5 | 96 | 96.5 | 94.6 | 96.2 | 96.6 | 96.6 | 96.3 | 96.3 | 96.3 | 93.1 | 95.3 | 95.8 | 96 | 95.7 | 95.9 | 95.7 | SMA America45.6ST48 [240V]
SMA America | ST48 [277V] | Y | N | N | 48kW, 277 Vac Sunny Tower Utility Interactive Inverter with display | 48 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 300 | 345 | 480 | 4.8 | 9.6 | 14.4 | 24 | 36 | 48 | 95.1 | 96.2 | 96.5 | 96.5 | 96.2 | 95.6 | 96.2 | 94.9 | 95.9 | 96.3 | 96.2 | 95.9 | 95.3 | 95.9 | 93.5 | 95 | 95.4 | 95.5 | 95.2 | 94.7 | 95.2 | SMA America48ST48 [277V]
SMA America | STP50-US-40 [480V] | Y | Y | Y | Sunny Tripower CORE1 50 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter | 50.072 | 480 | 98 | [8/14/2017] | [V1.01.19.R] | 2018-10-15 | N | N |  | 5.1 |  |  | 500 | 725 | 800 | 5.0072 | 10.0144 | 15.0216 | 25.036 | 37.554 | 50.072 | 94.9771 | 97.1941 | 97.7158 | 97.8318 | 97.5793 | 97.2902 | 97.5109 | 96.4618 | 97.7508 | 98.1301 | 98.2175 | 98.0757 | 97.8645 | 98.0206 | 97.214 | 97.859 | 98.0248 | 97.7868 | 98.1846 | 97.8628 | 98.0107 | SMA America50.072STP50-US-40 [480V] | 2017-09-01 | 2018-10-15
SMA America | STP 60-US-10 [400V] | Y | N | N | 60 kW, 400 Vac Utility Interactive Inverter | 59.86 | 400 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 7.1 |  |  | 570 | 630 | 800 | 5.99 | 11.97 | 17.96 | 29.93 | 44.89 | 59.86 | 97.9 | 98.6 | 98.7 | 98.6 | 98.4 | 98.1 | 98.4 | 97.5 | 98.3 | 98.4 | 98.3 | 98.1 | 97.9 | 98.2 | 96.5 | 97.7 | 98 | 98 | 97.7 | 97.5 | 97.8 | SMA America59.86STP 60-US-10 [400V]
SMA America | STP 60-US-10 [480V] | Y | N | N | 60 kW, 480 Vac Utility Interactive Inverter | 60 | 480 | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 8.16 |  |  | 685 | 710 | 800 | 6 | 12 | 18 | 30 | 45 | 60 | 97.7 | 98.5 | 98.7 | 98.8 | 98.6 | 98.5 | 98.6 | 97.5 | 98.4 | 98.7 | 98.7 | 98.6 | 98.4 | 98.6 | 96.9 | 98.1 | 98.4 | 98.4 | 98.3 | 98.1 | 98.3 | SMA America60STP 60-US-10 [480V]
SMA America | SC125U [208V] | Y | N | N | 125 kW, 208 Vac, 3-phase, 275-600 Vdc, Utility Interactive Inverter | 125 | 208 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 26.46 |  |  | 275 | 330 | 480 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 92.39 | 94.58 | 94.61 | 95.03 | 93.7 | 93.51 | 94.07 | 91.15 | 93.15 | 93.89 | 94.15 | 93.31 | 93.02 | 93.45 | 88.83 | 91.92 | 93.69 | 93.77 | 93.46 | 92.82 | 93.26 | SMA America125SC125U [208V]
SMA America | SC125U [480V] | Y | N | N | 126 kW, 480 Vac, 3-phase, 275-600 Vdc, Utility Interactive Inverter | 125 | 480 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 23.92 |  |  | 275 | 330 | 480 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 91.65 | 94.17 | 94.58 | 95.13 | 93.96 | 94.07 | 94.2 | 91.52 | 93.69 | 94.02 | 94.54 | 93.7 | 93.49 | 93.82 | 88.88 | 92.99 | 93.31 | 94.32 | 93.36 | 93.23 | 93.35 | SMA America125SC125U [480V]
SMA America | SC250U [480V] | Y | N | N | 250 kW, 480 Vac, 3-phase Utility Interactive Inverter | 250 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Discontinued | 50 |  |  | 330 | 370 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 93.7 | 95.8 | 96.5 | 97.5 | 97.4 | 96.4 | 97 | 95 | 95.6 | 96.3 | 97.4 | 97.3 | 96.5 | 97 | 92.2 | 95 | 95.9 | 97.2 | 97 | 96.4 | 96.6 | SMA America250SC250U [480V] |  | 2018-04-16
SMA America | SC500HE-US-MV (with Cooper transformer) | Y | N | N | 500 kW, 3-phase, Utility Interactive Inverter with Medium Voltage Cooper transformer | 500 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 110 |  |  | 330 | 370 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 96.03 | 97.64 | 97.93 | 97.88 | 97.43 | 96.82 | 97.51 | 95.31 | 97.24 | 97.65 | 97.73 | 97.28 | 96.69 | 97.31 | 93.33 | 96.28 | 96.95 | 97.23 | 96.95 | 96.36 | 96.8 | SMA America500SC500HE-US-MV (with Cooper transformer)
SMA America | SC500HE-US-MV (with NEMA TP-1 transformer) | Y | N | N | 500 kW, 3-phase, Utility Interactive Inverter with Medium Voltage NEMA NEMA TP1 transformer | 500 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 110 |  |  | 330 | 370 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 94.09 | 96.56 | 97.1 | 97.18 | 96.73 | 96.04 | 96.72 | 93.38 | 96.16 | 96.83 | 97.03 | 96.58 | 95.91 | 96.52 | 91.44 | 95.21 | 96.13 | 96.53 | 96.24 | 95.58 | 96.01 | SMA America500SC500HE-US-MV (with NEMA TP-1 transformer)
SMA America | SC500U [480V] | Y | N | N | 500 kW, 480 Vac, 3-phase Utility Interactive Inverter | 506.7 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Discontinued | 79.3 |  |  | 330 | 370 | 480 | 50.67 | 101.3 | 152 | 253.4 | 380 | 506.7 | 0.949 | 0.9678 | 0.9725 | 0.9737 | 0.9722 | 0.9667 | 0.9711 | 0.946 | 0.9652 | 0.9707 | 0.9725 | 0.9711 | 0.9659 | 0.9698 | 0.938 | 0.9601 | 0.9669 | 0.9694 | 0.9686 | 0.9642 | 0.9667 | SMA America506.7SC500U [480V] |  | 2018-04-16
SMA America | SC500CP-US (with ABB EcoDry Ultra transformer) | Y | N | N | 500 kW, 3-phase, Utility Interactive Inverter with Medium Voltage ABB transformer | 514 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 307.9 |  |  | 430 | 530 | 820 | 51.4 | 102.8 | 154.2 | 257 | 385.5 | 514 | 96.1 | 97.4 | 97.8 | 97.8 | 97.6 | 97.2 | 97.6 | 95.3 | 97 | 97.4 | 97.6 | 97.4 | 97 | 97.3 | 93.2 | 95.7 | 96.5 | 97 | 96.8 | 96.6 | 96.6 | SMA America514SC500CP-US (with ABB EcoDry Ultra transformer)
SMA America | SC500CP-US 600V (with ABB transformer) | Y | N | N | 500 kW, 3-phase, Utility Interactive Inverter with Medium Voltage ABB transformer | 516.2 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 185.5 |  |  | 360 | 391 | 480 | 51.62 | 103.2 | 154.9 | 258.1 | 387.1 | 516.2 | 94.8 | 96.8 | 97.5 | 97.6 | 97.1 | 96.6 | 97.1 | 94.3 | 96.5 | 97.3 | 97.5 | 96.9 | 96.5 | 96.9 | 93.1 | 95.8 | 96.7 | 97.1 | 96.6 | 96.2 | 96.5 | SMA America516.2SC500CP-US 600V (with ABB transformer)
SMA America | SC630CP-US (with ABB EcoDry Ultra transformer) | Y | N | N | 630 kW, 3-phase, Utility Interactive Inverter with Medium Voltage ABB transformer | 653 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 371.9 |  |  | 500 | 580 | 820 | 65.3 | 130.6 | 195.9 | 326.5 | 489.8 | 653 | 96.2 | 97.5 | 97.8 | 97.9 | 97.7 | 97.4 | 97.7 | 95.6 | 97.2 | 97.6 | 97.8 | 97.5 | 97.2 | 97.5 | 94.1 | 96.3 | 96.9 | 97.3 | 97.1 | 96.8 | 97 | SMA America653SC630CP-US (with ABB EcoDry Ultra transformer)
SMA America | SC720CP-US (with ABB EcoDry Ultra transformer) | Y | N | N | 720 kW, 3-phase, Utility Interactive Inverter with Medium Voltage ABB transformer | 742 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 363.8 |  |  | 515 | 592 | 820 | 74.2 | 148.4 | 222.6 | 371 | 556.5 | 742 | 96.3 | 97.6 | 97.9 | 97.9 | 97.6 | 97.3 | 97.7 | 95.9 | 97.3 | 97.7 | 97.8 | 97.6 | 97.2 | 97.5 | 94.5 | 96.5 | 97.1 | 97.4 | 97.2 | 96.8 | 97.1 | SMA America742SC720CP-US (with ABB EcoDry Ultra transformer)
SMA America | SC750CP-US (with ABB EcoDry Ultra transformer) | Y | N | N | 750 kW, 3-phase, Utility Interactive Inverter with Medium Voltage ABB transformer | 770 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 364.7 |  |  | 545 | 614 | 820 | 76.98 | 154 | 230.9 | 384.9 | 577.4 | 769.8 | 96.4 | 97.6 | 97.9 | 98 | 97.7 | 97.3 | 97.7 | 95.9 | 97.3 | 97.7 | 97.9 | 97.7 | 97.3 | 97.6 | 94.7 | 96.6 | 97.2 | 97.5 | 97.3 | 97 | 97.2 | SMA America770SC750CP-US (with ABB EcoDry Ultra transformer)
SMA America | SC800CP-US (with ABB EcoDry Ultra transformer) | Y | N | N | 800 kW, 3-phase, Utility Interactive Inverter with Medium Voltage ABB transformer | 823 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 362.9 |  |  | 570 | 633 | 820 | 82.3 | 164.6 | 246.9 | 411.5 | 617.3 | 823 | 96.4 | 97.6 | 98 | 98.1 | 97.8 | 97.4 | 97.8 | 96 | 97.4 | 97.8 | 98 | 97.7 | 97.3 | 97.7 | 94.9 | 96.8 | 97.4 | 97.6 | 97.4 | 97 | 97.3 | SMA America823SC800CP-US (with ABB EcoDry Ultra transformer)
SMA America | SC850CP-US (with ABB EcoDry Ultra transformer) | Y | N | N | 850 kW, 1000 Vdc, 3-phase, Utility Interactive Inverter with Medium Voltage ABB transformer | 888 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 202.3 |  |  | 620 | 671 | 820 | 88.8 | 177.6 | 266.4 | 444 | 666 | 888 | 95.6 | 97.2 | 97.9 | 98 | 97.8 | 97.4 | 97.7 | 95.3 | 97.1 | 97.7 | 97.9 | 97.7 | 97.3 | 97.6 | 94.5 | 96.6 | 97.4 | 97.6 | 97.5 | 97.1 | 97.3 | SMA America888SC850CP-US (with ABB EcoDry Ultra transformer)
SMA America | SC900CP-US (with ABB EcoDry Ultra transformer) | Y | N | N | 900 kW, 1000 Vdc, 3-phase, Utility Interactive Inverter with Medium Voltage ABB transformer | 942 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 198.2 |  |  | 655 | 697 | 820 | 94.2 | 188.4 | 282.6 | 471 | 706.5 | 942 | 95.6 | 97.2 | 97.9 | 98 | 97.8 | 97.5 | 97.7 | 95.3 | 97 | 97.8 | 97.9 | 97.8 | 97.4 | 97.6 | 94.7 | 96.7 | 97.5 | 97.7 | 97.6 | 97.2 | 97.4 | SMA America942SC900CP-US (with ABB EcoDry Ultra transformer)
SMA America | SC-1850-US [385V] | Y | Y | Y | Sunny Central 1850 kW, 385 Vac Grid Support Utility Interactive Inverter | 1661 | 385 | 97 | [10/16/2017] | [04.00.25.R] | 2018-10-15 | Y | N | Weighted efficiency includes transformer efficiency of Eaton 34.5kV. | 294 |  |  | 570 | 665 | 950 | 166.1 | 332.2 | 498.3 | 830.5 | 1245.75 | 1661 | 96.09 | 97.54 | 97.81 | 97.79 | 97.59 | 97.25 | 97.58 | 95.5 | 97.22 | 97.55 | 97.62 | 97.45 | 97.13 | 97.39 | 93.24 | 96.22 | 96.74 | 97.07 | 96.98 | 96.67 | 96.77 | SMA America1661SC-1850-US [385V] | 2018-04-16 | 2018-10-15
SMA America | SC-2200-US [385V] | Y | Y | Y | Sunny Central 2200 kW, 385 Vac Grid Support Utility Interactive Inverter | 2079 | 385 | 97 | [10/16/2017] | [04.00.25.R] | 2018-10-15 | Y | N | Weighted efficiency includes transformer efficiency of Eaton 34.5kV. | 297 |  |  | 570 | 665 | 950 | 207.9 | 415.8 | 623.7 | 1039.5 | 1559.25 | 2079 | 96.63 | 97.68 | 97.8 | 97.69 | 97.33 | 96.68 | 97.42 | 96.07 | 97.38 | 97.58 | 97.53 | 97.21 | 96.57 | 97.25 | 94.45 | 96.53 | 96.96 | 97.05 | 96.73 | 96.18 | 96.69 | SMA America2079SC-2200-US [385V] | 2018-04-16 | 2018-10-15
SMA America | SC 2500-EV-US [550V] | N | Y | Y | Sunny Central 2500 kW, 550 Vac Grid Support Utility Interactive Inverter | 2353.87 | 550 | 97 | [08/30/2017] | [04.00.25.R] | 2018-10-15 | Y | N | Weighted efficiency includes transformer efficiency of Eaton 34.5 kV. | 370 |  |  | 850 | 994 | 1425 | 235.39 | 470.77 | 706.16 | 1176.94 | 1765.4 | 2353.87 | 96.42 | 97.63 | 97.83 | 97.79 | 97.42 | 96.82 | 97.49 | 95.86 | 97.35 | 97.63 | 97.65 | 97.28 | 96.74 | 97.32 | 94.25 | 96.58 | 97.07 | 97.2 | 96.81 | 96.42 | 96.79 | SMA America2353.87SC 2500-EV-US [550V] | 2018-05-01 | 2018-10-15
SMA America | SC 2750-EV-US [600V] | N | Y | Y | Sunny Central 2750 kW, 600Vac, multi-mode, 3-phase Grid Support Utility Interactive Inverter | 2600 | 600 | 97.5 | [08/30/2017] | [04.00.25.R] | 2018-10-15 | Y | N | Weighted efficiency includes transformer efficiency of Eaton 34.5kV. | 379.32 |  |  | 875 | 957 | 1200 | 260 | 520 | 780 | 1300 | 1950 | 2600 | 95.6543 | 97.2785 | 97.676 | 97.8338 | 97.6424 | 97.2188 | 97.5677 | 95.3931 | 97.1422 | 97.5611 | 97.7454 | 97.5481 | 97.0711 | 97.4608 | 94.4709 | 96.7352 | 97.0588 | 97.4894 | 97.3596 | 96.8887 | 97.1805 | SMA America2600SC 2750-EV-US [600V] | 2018-08-15 | 2018-10-15
Solar Liberty | SLX 3000 [208V] | Y | N | N | 2.8 kW, 208 Vac Utility Interactive Inverter | 2.81 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.35 |  |  | 100 | 275 | 400 | 0.28 | 0.56 | 0.84 | 1.41 | 2.11 | 2.81 | 89.4 | 94.4 | 95.5 | 96.2 | 96.2 | 95.9 | 95.8 | 88.7 | 93.8 | 95.2 | 95.9 | 96 | 95.7 | 95.5 | 86.5 | 92.1 | 94 | 95.1 | 95.3 | 95.2 | 94.6 | Solar Liberty2.81SLX 3000 [208V]
Solar Liberty | SLX 3000 [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 90.6 | 95 | 96 | 96.6 | 96.6 | 96.2 | 96.2 | 89.8 | 94.4 | 95.6 | 96.4 | 96.4 | 96 | 95.9 | 87.7 | 92.9 | 94.5 | 95.6 | 95.8 | 95.5 | 95.1 | Solar Liberty3.01SLX 3000 [240V]
Solar Liberty | SLX 4000 [208V] | Y | N | N | 3.5 kW, 208 Vac Utility Interactive Inverter | 3.51 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.35 |  |  | 100 | 275 | 400 | 0.35 | 0.7 | 1.05 | 1.76 | 2.63 | 3.51 | 91.3 | 95.1 | 96 | 96.3 | 96.1 | 95.4 | 95.9 | 90.4 | 94.7 | 95.7 | 96 | 95.9 | 95.3 | 95.6 | 88.4 | 93.3 | 94.7 | 95.3 | 95.3 | 94.7 | 94.8 | Solar Liberty3.51SLX 4000 [208V]
Solar Liberty | SLX 4000 [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 4.02 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.4 | 0.8 | 1.21 | 2.01 | 3.02 | 4.02 | 92.6 | 95.7 | 96.4 | 96.5 | 96.3 | 95.5 | 96.1 | 91.8 | 95.3 | 96.1 | 96.3 | 96.1 | 95.4 | 95.9 | 90 | 94.1 | 95.2 | 95.7 | 95.5 | 94.9 | 95.2 | Solar Liberty4.02SLX 4000 [240V]
Solar Liberty | SLX 5000 [208V] | Y | N | N | 4.4 kW, 208 Vac Utility Interactive Inverter | 4.4 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 92.9 | 95.8 | 96.5 | 96.8 | 96.6 | 95.9 | 96.4 | 92.2 | 95.3 | 96.2 | 96.4 | 96.2 | 95.5 | 96 | 90.1 | 93.9 | 95 | 95.7 | 95.6 | 95.2 | 95.2 | Solar Liberty4.4SLX 5000 [208V]
Solar Liberty | SLX 5000 [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter | 4.6 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 13.95 |  |  | 100 | 275 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.5 | 95.6 | 96.2 | 96.1 | 95.9 | 95.3 | 95.9 | 93 | 95.3 | 96 | 95.9 | 95.9 | 95.2 | 95.7 | 91.7 | 94.4 | 95.2 | 95.7 | 95.5 | 95 | 95.3 | Solar Liberty4.6SLX 5000 [240V]
Solar Liberty | SLX 5300 [208V] | Y | N | N | 4.6 kW, 208 Vac Utility Interactive Inverter | 5.01 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.47 |  |  | 100 | 275 | 400 | 0.5 | 1 | 1.5 | 2.51 | 3.76 | 5.01 | 93.9 | 96.1 | 96.6 | 96.7 | 96.4 | 95.7 | 96.3 | 92.7 | 95.8 | 96.4 | 96.5 | 96.2 | 95.6 | 96.1 | 91.2 | 94.7 | 95.7 | 96.1 | 95.9 | 95.4 | 95.7 | Solar Liberty5.01SLX 5300 [208V]
Solar Liberty | SLX 5300 [240V] | Y | N | N | 5.3 kW, 240 Vac Utility Interactive Inverter | 5.3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 14 |  |  | 100 | 275 | 400 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 94.3 | 96.1 | 96.3 | 96.4 | 96 | 95.2 | 96 | 93.8 | 95.9 | 96.1 | 96.3 | 95.8 | 95.2 | 95.8 | 92.5 | 95 | 95.7 | 96 | 95.5 | 94.9 | 95.4 | Solar Liberty5.3SLX 5300 [240V]
Solar Liberty | SLX 6500 [208V] | Y | N | N | 6.43 kW, 208 Vac Utility Interactive Inverter | 6.43 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.64 | 1.29 | 1.93 | 3.22 | 4.82 | 6.43 | 93.3 | 95.6 | 96 | 96 | 95.6 | 94.8 | 95.6 | 92.9 | 95.4 | 95.9 | 95.9 | 95.5 | 94.8 | 95.5 | 91.6 | 94.8 | 95.4 | 95.6 | 95.2 | 94.6 | 95.1 | Solar Liberty6.43SLX 6500 [208V]
Solar Liberty | SLX 6500 [240V] | Y | N | N | 6.45 kW, 240 Vac Utility Interactive Inverter | 6.45 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.65 |  |  | 100 | 275 | 400 | 0.65 | 1.29 | 1.94 | 3.23 | 4.84 | 6.45 | 93.5 | 95.9 | 96.3 | 96.3 | 96 | 95.4 | 96 | 93.1 | 95.7 | 96.2 | 96.3 | 96 | 95.3 | 95.9 | 91.8 | 95 | 95.6 | 95.9 | 95.7 | 95.2 | 95.5 | Solar Liberty6.45SLX 6500 [240V]
Solar Liberty | SLX 6500 [277V] | Y | N | N | 6.45 kW, 277 Vac Utility Interactive Inverter | 6.45 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 100 | 275 | 400 | 0.645 | 1.29 | 1.935 | 3.225 | 4.838 | 6.45 | 93.82 | 96.14 | 96.54 | 96.67 | 96.41 | 95.82 | 96.33 | 93.37 | 95.93 | 96.36 | 96.54 | 96.31 | 95.75 | 96.2 | 92.05 | 95.29 | 95.88 | 96.19 | 96.04 | 95.56 | 95.83 | Solar Liberty6.45SLX 6500 [277V]
Solar Liberty | SLX 7500 [208V] | Y | N | N | 7.43 kW, 208 Vac Utility Interactive Inverter | 7.43 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.52 |  |  | 100 | 275 | 400 | 0.74 | 1.49 | 2.23 | 3.72 | 5.57 | 7.43 | 94.1 | 96 | 96.2 | 96.1 | 95.4 | 94.6 | 95.6 | 93.7 | 95.7 | 96 | 96 | 95.3 | 94.5 | 95.5 | 92.5 | 95.1 | 95.6 | 95.6 | 95.1 | 94.3 | 95.1 | Solar Liberty7.43SLX 7500 [208V]
Solar Liberty | SLX 7500 [240V] | Y | N | N | 7.45 kW, 240 Vac Utility Interactive Inverter | 7.45 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.68 |  |  | 100 | 275 | 400 | 0.745 | 1.49 | 2.235 | 3.725 | 5.588 | 7.45 | 94.32 | 96.24 | 96.54 | 96.47 | 95.87 | 95.16 | 96 | 93.91 | 96.02 | 96.34 | 96.34 | 95.81 | 95.1 | 95.89 | 92.69 | 95.39 | 95.93 | 95.99 | 95.52 | 94.9 | 95.52 | Solar Liberty7.45SLX 7500 [240V]
Solar Liberty | SLX 7500 [277V] | Y | N | N | 7.46 kW, 277 Vac Utility Interactive Inverter | 7.46 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 100 | 275 | 400 | 0.746 | 1.492 | 2.238 | 3.73 | 5.595 | 7.46 | 94.44 | 96.42 | 96.66 | 96.61 | 96.24 | 95.52 | 96.27 | 94.04 | 96.11 | 96.5 | 96.56 | 96.17 | 95.46 | 96.17 | 92.87 | 95.53 | 96.08 | 96.19 | 95.89 | 95.3 | 95.81 | Solar Liberty7.46SLX 7500 [277V]
Solar Power | YS-1500TL [208V] | Y | N | N | 1500 W, 208 Vac Utility Interactive Inverter | 1.5 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 330 | 360 | 0.15 | 0.3 | 0.45 | 0.75 | 1.12 | 1.5 | 91.1 | 94.9 | 96 | 96.4 | 96.2 | 96 | 95.9 | 91.7 | 95.5 | 96.5 | 96.8 | 96.7 | 96.5 | 96.4 | 91.5 | 95.2 | 96.2 | 96.7 | 96.7 | 96.5 | 96.3 | Solar Power1.5YS-1500TL [208V]
Solar Power | YS-1500TL [240V] | Y | N | N | 1500 W, 240 Vac Utility Interactive Inverter | 1.62 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.11 |  |  | 100 | 330 | 360 | 0.16 | 0.32 | 0.49 | 0.81 | 1.21 | 1.62 | 89.5 | 94.2 | 95.5 | 96.3 | 96.3 | 96 | 95.8 | 90.2 | 94.7 | 95.9 | 96.6 | 96.6 | 96.5 | 96.2 | 91.3 | 95.4 | 96.5 | 97 | 97 | 96.8 | 96.6 | Solar Power1.62YS-1500TL [240V]
Solar Power | YS-1500TL [277V] | Y | N | N | 1500 W, 277 Vac Utility Interactive Inverter | 1.62 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.13 |  |  | 100 | 330 | 360 | 0.16 | 0.32 | 0.48 | 0.81 | 1.21 | 1.62 | 89.2 | 93.5 | 95 | 96.1 | 96.2 | 96.1 | 95.6 | 89.3 | 94 | 95.6 | 96.4 | 96.6 | 96.7 | 96 | 89.3 | 94.3 | 95.7 | 96.6 | 96.8 | 96.8 | 96.2 | Solar Power1.62YS-1500TL [277V]
Solar Power | YS-2000TL [208V] | Y | N | N | 2000 W, 208 Vac Utility Interactive Inverter | 1.81 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.09 |  |  | 100 | 360 | 400 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.81 | 92.3 | 95.4 | 96 | 96.4 | 96.3 | 96 | 96.1 | 92.8 | 96 | 96.6 | 96.8 | 96.6 | 96.4 | 96.5 | 92.7 | 95.7 | 96.3 | 96.6 | 96.5 | 96.3 | 96.3 | Solar Power1.81YS-2000TL [208V]
Solar Power | YS-2000TL [277V] | Y | N | N | 2000 W, 277 Vac Utility Interactive Inverter | 2 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 360 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89.3 | 93.7 | 95.1 | 96 | 96.3 | 96.1 | 95.7 | 91.1 | 94.8 | 95.9 | 96.5 | 96.8 | 96.8 | 96.3 | 92.9 | 96.1 | 96.9 | 97.3 | 97.4 | 97.3 | 97.1 | Solar Power2YS-2000TL [277V]
Solar Power | YS-2000TL [240V] | Y | N | N | 2000 W, 240 Vac Utility Interactive Inverter | 2.01 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 100 | 360 | 400 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2.01 | 91.4 | 94.6 | 95.7 | 96.3 | 96.4 | 96.1 | 96 | 92.9 | 96.1 | 96.8 | 97.1 | 97.1 | 96.9 | 96.9 | 92.3 | 95.8 | 96.6 | 96.9 | 97 | 96.8 | 96.7 | Solar Power2.01YS-2000TL [240V]
Solar Power | YS-3000TL [208V] | Y | N | N | 3000 W, 208 Vac Utility Interactive Inverter | 2.5 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.1 |  |  | 100 | 360 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 92.3 | 95.4 | 96.2 | 96.5 | 96.2 | 95.8 | 96 | 93.9 | 96.2 | 96.8 | 97 | 96.8 | 96.4 | 96.7 | 92.7 | 95.8 | 96.5 | 96.8 | 96.6 | 96.3 | 96.4 | Solar Power2.5YS-3000TL [208V]
Solar Power | YS-3000TL [240V] | Y | N | N | 3000 W, 240 Vac Utility Interactive Inverter | 2.8 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 |  |  | 100 | 360 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 91 | 94.4 | 95.6 | 96.4 | 96.4 | 96.1 | 96 | 94 | 96.6 | 97.1 | 97.5 | 97.4 | 97 | 97.2 | 93.3 | 96.1 | 96.8 | 97.4 | 97.3 | 97 | 97 | Solar Power2.8YS-3000TL [240V]
Solar Power | YS-3000TL [277V] | Y | N | N | 3000 W, 277 Vac Utility Interactive Inverter | 2.8 | 277 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.19 |  |  | 100 | 360 | 400 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.4 | 93.4 | 94.8 | 95.9 | 96.2 | 96 | 95.5 | 91.6 | 95.2 | 96.3 | 96.9 | 97 | 96.8 | 96.6 | 94.1 | 96.6 | 97.3 | 97.7 | 97.6 | 97.4 | 97.4 | Solar Power2.8YS-3000TL [277V]
Solar Power | YS-3600MTL [208V] | Y | N | N | 3600 W, 208 Vac Utility Interactive Inverter | 3.6 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.23 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 91.9 | 94.6 | 95.5 | 96.4 | 96.5 | 96.3 | 96.1 | 94.5 | 96.7 | 97.3 | 97.6 | 97.4 | 97.2 | 97.3 | 93 | 96 | 96.9 | 97.3 | 97.3 | 97.1 | 97 | Solar Power3.6YS-3600MTL [208V]
Solar Power | YS-3600MTL [240V] | Y | N | N | 3600 W, 240 Vac Utility Interactive Inverter | 3.6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.31 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 92.4 | 94.6 | 95.5 | 96.5 | 96.7 | 96.7 | 96.2 | 95.3 | 97.1 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | 94.2 | 96.5 | 97.1 | 97.5 | 97.6 | 97.4 | 97.3 | Solar Power3.6YS-3600MTL [240V]
Solar Power | YS-3600MTL [277V] | Y | N | N | 3600 W, 277 Vac Utility Interactive Inverter | 3.61 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.61 | 91.2 | 93.9 | 94.7 | 96.1 | 96.6 | 96.6 | 95.9 | 93.4 | 96 | 96.6 | 97.4 | 97.5 | 97.5 | 97.2 | 94.5 | 96.8 | 97.4 | 97.9 | 98 | 97.9 | 97.7 | Solar Power3.61YS-3600MTL [277V]
Solar Power | YS-4200MTL [208V] | Y | N | N | 4200 W, 208 Vac Utility Interactive Inverter | 4.2 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.6 | 94.4 | 95.5 | 96.6 | 96.8 | 96.7 | 96.3 | 94.1 | 96.5 | 97.1 | 97.3 | 97.1 | 96.7 | 97 | 93.6 | 96.2 | 96.8 | 97.2 | 97.5 | 97.1 | 97.1 | Solar Power4.2YS-4200MTL [208V]
Solar Power | YS-4200MTL [240V] | Y | N | N | 4200 W, 240 Vac Utility Interactive Inverter | 4.2 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.4 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.2 | 91.4 | 94.4 | 96 | 96.6 | 96.8 | 96.6 | 96.3 | 92.1 | 95.2 | 96.3 | 97.3 | 97.6 | 97.1 | 97 | 93.6 | 96.3 | 97.2 | 97.6 | 97.6 | 97.6 | 97.4 | Solar Power4.2YS-4200MTL [240V]
Solar Power | YS-4200MTL [277V] | Y | N | N | 4200 W, 277 Vac Utility Interactive Inverter | 4.21 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.33 |  |  | 100 | 375 | 450 | 0.42 | 0.84 | 1.26 | 2.1 | 3.15 | 4.21 | 92.4 | 94.6 | 95.5 | 96.5 | 96.7 | 96.7 | 96.2 | 95.3 | 97.1 | 97.5 | 97.8 | 97.7 | 97.5 | 97.6 | 94.2 | 96.5 | 97.1 | 97.5 | 97.6 | 97.4 | 97.3 | Solar Power4.21YS-4200MTL [277V]
Solar Power | YS-5000MTL [208V] | Y | N | N | 5000 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.26 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 94.7 | 96.5 | 96.8 | 96.9 | 96.5 | 96 | 96.5 | 95.4 | 97 | 97.3 | 97.4 | 97 | 96.5 | 97 | 94.3 | 96.4 | 96.9 | 97.1 | 97 | 96.5 | 96.8 | Solar Power4.6YS-5000MTL [208V]
Solar Power | YS-5000MTL [240V] | Y | N | N | 5000 W, 240 Vac Utility Interactive Inverter | 4.6 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.8 | 95.2 | 96 | 96.7 | 96.6 | 96.4 | 96.3 | 95.8 | 97.3 | 97.7 | 97.8 | 97.5 | 97.1 | 97.5 | 96.7 | 96.7 | 97.2 | 97.5 | 97.4 | 97.1 | 97.3 | Solar Power4.6YS-5000MTL [240V]
Solar Power | YS-5000MTL [277V] | Y | N | N | 5000 W, 277 Vac Utility Interactive Inverter | 4.6 | 277 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.43 |  |  | 100 | 375 | 450 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 92.2 | 94.9 | 95.6 | 96.6 | 96.8 | 96.8 | 96.4 | 94.6 | 96.7 | 97.2 | 97.6 | 97.6 | 97.4 | 97.4 | 95.4 | 97.1 | 97.6 | 97.9 | 97.8 | 97.7 | 97.7 | Solar Power4.6YS-5000MTL [277V]
Solar Power | YS-8000TL [208V] | Y | N | N | 8000 W, 208 Vac Utility Interactive Inverter | 8.07 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.053 |  |  | 100 | 345 | 480 | 0.81 | 1.61 | 2.42 | 4.03 | 6.05 | 8.07 | 95.6 | 96.7 | 97.1 | 97.2 | 97.1 | 96.9 | 97.1 | 94.9 | 96.3 | 96.8 | 97 | 96.9 | 96.8 | 96.8 | 92.6 | 95 | 95.8 | 96.4 | 96.4 | 96.2 | 96.1 | Solar Power8.07YS-8000TL [208V]
Solar Power | YS-8000TL [240V] | Y | N | N | 8000 W, 240 Vac Utility Interactive Inverter | 8.08 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.075 |  |  | 100 | 380 | 480 | 0.81 | 1.62 | 2.42 | 4.04 | 6.06 | 8.08 | 95.4 | 96.7 | 97.1 | 97.4 | 97.4 | 97.2 | 97.2 | 95.1 | 96.6 | 97 | 97.3 | 97.3 | 97.2 | 97.1 | 93.2 | 95.5 | 96.2 | 96.8 | 96.4 | 96.9 | 96.3 | Solar Power8.08YS-8000TL [240V]
Solar Power | YS-9000TL [208V] | Y | N | N | 9000 W, 208 Vac Utility Interactive Inverter | 9.08 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.053 |  |  | 100 | 345 | 480 | 0.91 | 1.82 | 2.72 | 4.54 | 6.81 | 9.08 | 95.9 | 96.8 | 97.1 | 97.2 | 97 | 96.8 | 97 | 95.3 | 96.5 | 96.9 | 97 | 97 | 96.7 | 96.9 | 93.1 | 95.3 | 96 | 96.4 | 96.4 | 96.2 | 96.2 | Solar Power9.08YS-9000TL [208V]
Solar Power | YS-9000TL [240V] | Y | N | N | 9000 W, 240 Vac Utility Interactive Inverter | 9.08 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.075 |  |  | 100 | 380 | 480 | 0.91 | 1.82 | 2.72 | 4.54 | 6.81 | 9.08 | 95.8 | 96.9 | 97.2 | 97.4 | 97.4 | 97.2 | 97.2 | 95.5 | 96.8 | 97.1 | 97.3 | 97.3 | 97.1 | 97.2 | 93.8 | 95.8 | 96.4 | 96.7 | 96.9 | 96.8 | 96.6 | Solar Power9.08YS-9000TL [240V]
Solar Power | YS-10000TL [208V] | Y | N | N | 10000 W, 208 Vac Utility Interactive Inverter | 10.09 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.053 |  |  | 100 | 345 | 480 | 1.01 | 2.02 | 3.03 | 5.04 | 7.57 | 10.09 | 95.8 | 96.9 | 97.1 | 97.2 | 97 | 96.6 | 97 | 95.5 | 96.6 | 96.9 | 97 | 96.9 | 96.5 | 96.8 | 93.1 | 95.4 | 96.1 | 96.4 | 96.3 | 96 | 96.1 | Solar Power10.09YS-10000TL [208V]
Solar Power | YS-10000TL [240V] | Y | N | N | 10000 W, 240 Vac Utility Interactive Inverter | 10.09 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.075 |  |  | 100 | 380 | 480 | 1.01 | 2.02 | 3.03 | 5.04 | 7.56 | 10.09 | 96 | 97 | 97.3 | 97.4 | 97.3 | 97.1 | 97.2 | 95.8 | 96.9 | 97.2 | 97.4 | 97.3 | 97 | 97.2 | 94.3 | 96 | 96.5 | 96.9 | 96.8 | 96.7 | 96.7 | Solar Power10.09YS-10000TL [240V]
Solar Power | YS-11000TL [240V] | Y | N | N | 11000 W, 240 Vac Utility Interactive Inverter | 11.7 | 240 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.075 |  |  | 356 | 380 | 480 | 1.17 | 2.34 | 3.51 | 5.85 | 8.775 | 11.7 | 96 | 97 | 97.3 | 97.3 | 97.2 | 97 | 97.2 | 95.8 | 96.9 | 97.2 | 97.3 | 97.2 | 96.9 | 97.1 | 94.3 | 96 | 96.5 | 97 | 96.8 | 96.5 | 96.6 | Solar Power11.7YS-11000TL [240V]
Solarbine | S6T AC [120V] | Y | N | N | 212 W, 120 Vac Inverter | 0.21 | 120 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0 |  |  | 36 | 50 | 55 | 0.021 | 0.04 | 0.06 | 0.11 | 0.16 | 0.21 | 87.9 | 94.4 | 95.8 | 95.7 | 94.8 | 93.5 | 94.8 | 85.2 | 92.5 | 94.6 | 95.3 | 95.1 | 94.2 | 94.5 | 83.6 | 92 | 94.3 | 94.9 | 94.9 | 93.9 | 94.2 | Solarbine0.21S6T AC [120V]
SolarBridge Technologies | P235HV-240 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 | 0.225 | 0.03 | 30 | 43 | 50 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 86.6 | 91.6 | 93.3 | 94.6 | 94.7 | 94.5 | 94 | 85.9 | 91.3 | 93.2 | 94.9 | 95.3 | 95.3 | 94.4 | 87.3 | 90.7 | 93.3 | 95 | 95.5 | 95.4 | 94.5 | SolarBridge Technologies0.225P235HV-240 [240V]
SolarBridge Technologies | P235LV-240 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.02 |  |  | 21 | 31.5 | 35 | 0.0225 | 0.045 | 0.0675 | 0.1125 | 0.1688 | 0.225 | 86.98 | 91.98 | 93.37 | 94.53 | 94.52 | 94.11 | 93.93 | 85.82 | 91.51 | 93.51 | 95.05 | 96.08 | 95.32 | 94.88 | 85.39 | 91.3 | 93.34 | 94.9 | 95.33 | 95.5 | 94.41 | SolarBridge Technologies0.225P235LV-240 [240V]
SolarBridge Technologies | SBT250-NA240-A111 [240V] | Y | N | N | 225 W, 240 Vac Inverter, 1-phase ACPV | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | SolarBridge Technologies0.225SBT250-NA240-A111 [240V]
SolarBridge Technologies | SBT250-NA240-A311 [240V] | Y | N | N | 225 W, 240 Vac Inverter, 1-phase ACPV | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | SolarBridge Technologies0.225SBT250-NA240-A311 [240V]
SolarBridge Technologies | P250HV-208/240-xxx | Y | N | N | 240 W, 208 or 240 Vac Inverter, where xxx may be up to 20 characters | 0.24 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | SolarBridge Technologies0.24P250HV-208/240-xxx
SolarBridge Technologies | P250HV-240-xxx [240V] | Y | N | N | 240 W, 240 Vac Inverter, "xxx" may be up to 20 characters | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.21 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 89.1 | 93.6 | 94.7 | 95 | 95.1 | 94.8 | 94.7 | 88.6 | 93.5 | 94.7 | 95.3 | 95.6 | 94.8 | 95 | 88.1 | 93.3 | 94.7 | 95.3 | 95.7 | 95.7 | 95 | SolarBridge Technologies0.24P250HV-240-xxx [240V]
SolarBridge Technologies | P250LV-208/240-xxx | Y | N | N | 240 W, 208 or 240 Vac Inverter, where xxx may be up to 20 characters | 0.24 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | SolarBridge Technologies0.24P250LV-208/240-xxx
SolarBridge Technologies | P250LV-240-xxx [240V] | Y | N | N | 240 W, 240 Vac Inverter, "xxx" may be up to 20 characters | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.22 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 88.7 | 93.7 | 94 | 94.9 | 95 | 94.7 | 94.5 | 87.7 | 93.5 | 94.8 | 95.1 | 95.5 | 95.5 | 94.9 | 86.9 | 93.2 | 94.6 | 95.1 | 95.7 | 95.7 | 94.9 | SolarBridge Technologies0.24P250LV-240-xxx [240V]
SolarBridge Technologies | SBT250-NA208/240-A121 | Y | N | N | 240 W, 208 Vac or 240 Vac 1-phase ACPV | 0.24 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | SolarBridge Technologies0.24SBT250-NA208/240-A121
SolarBridge Technologies | SBT250-NA208/240-A321 | Y | N | N | 240 W, 208 Vac or 240 Vac 1-phase ACPV | 0.24 |  | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | SolarBridge Technologies0.24SBT250-NA208/240-A321
SolarCity | H6 | Y | N | N | 6 kW Utility Interactive Solar and Storage Inverter | 6 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 6 |  |  | 200 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.638 | 95.448 | 96.164 | 96.652 | 96.53 | 96.134 | 96.2821 | 93.212 | 95.944 | 96.742 | 97.264 | 97.286 | 97.094 | 96.9764 | 93.212 | 95.944 | 96.742 | 97.264 | 97.286 | 97.094 | 96.9764 | SolarCity6H6
SolarCity | H6L | Y | N | N | 6 kW Utility Interactive Solar and Storage Inverter | 6 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 6 |  |  | 200 | 400 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.638 | 95.448 | 96.164 | 96.652 | 96.53 | 96.134 | 96.2821 | 93.212 | 95.944 | 96.742 | 97.264 | 97.286 | 97.094 | 96.9764 | 93.548 | 96.14 | 96.932 | 97.426 | 97.436 | 97.238 | 97.1432 | SolarCity6H6L
SolarEdge Technologies Ltd. | SE3000H-US [240V] | Y | Y | Y | 3.0 kW, 240 Vac HD-Wave technology Grid Support Utility Interactive Inverter | 2.962 | 240 | 99 | [6/26/2017] | [2.0.121] | 2018-10-15 | Y | N |  | 0 |  |  | 360 | 395 | 480 | 0.3 | 0.6 | 0.9 | 1.6 | 2.1 | 2.8 | 95.67 | 98.01 | 98.63 | 99.01 | 99.19 | 99.19 | 98.89 | 95.39 | 97.88 | 98.54 | 98.96 | 99.16 | 99.16 | 98.83 | 95.93 | 98.04 | 98.57 | 99 | 99.08 | 99.17 | 98.83 | SolarEdge Technologies Ltd.2.962SE3000H-US [240V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE3000 [240V] | Y | N | N | 3 kW, 240 Vac, Utility Interactive Inverter | 3.01 | 240 | 97.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 3.39 |  |  | 100 | 388 | 480 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 95.1 | 97.1 | 97.5 | 97.8 | 97.8 | 97.7 | 97.6 | 94.8 | 96.8 | 97.4 | 97.7 | 97.7 | 97.6 | 97.5 | 93.4 | 96.4 | 97 | 97.4 | 97.5 | 97.5 | 97.2 | SolarEdge Technologies Ltd.3.01SE3000 [240V]
SolarEdge Technologies Ltd. | SE3000x [240V] | N | Y | Y | 3 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 3.01 | 240 | 97.5 | [6/7/2017] | [2.52.326] | 2018-10-15 | Y | N |  | 3.39 |  |  | 100 | 388 | 480 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 95.1 | 97.1 | 97.5 | 97.8 | 97.8 | 97.7 | 97.6 | 94.8 | 96.8 | 97.4 | 97.7 | 97.7 | 97.6 | 97.5 | 93.4 | 96.4 | 97 | 97.4 | 97.5 | 97.5 | 97.2 | SolarEdge Technologies Ltd.3.01SE3000x [240V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE3000 [208V] | Y | N | N | 3 kW, 208 Vac, Utility Interactive Inverter | 3.02 | 208 | 97.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 3.71 |  |  | 305 | 350 | 480 | 0.3 | 0.6 | 0.91 | 1.51 | 2.27 | 3.02 | 96 | 97.4 | 97.6 | 97.7 | 97.6 | 97.4 | 97.5 | 95.6 | 97.1 | 97.5 | 97.6 | 97.5 | 97.3 | 97.4 | 93.6 | 96.3 | 96.9 | 97.2 | 97.2 | 97.1 | 97 | SolarEdge Technologies Ltd.3.02SE3000 [208V]
SolarEdge Technologies Ltd. | SE3000x [208V] | N | Y | Y | 3 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 3.02 | 208 | 97.5 | [6/7/2017] | [2.52.326] | 2018-10-15 | Y | N |  | 3.71 |  |  | 305 | 350 | 480 | 0.3 | 0.6 | 0.91 | 1.51 | 2.27 | 3.02 | 96 | 97.4 | 97.6 | 97.7 | 97.6 | 97.4 | 97.5 | 95.6 | 97.1 | 97.5 | 97.6 | 97.5 | 97.3 | 97.4 | 93.6 | 96.3 | 96.9 | 97.2 | 97.2 | 97.1 | 97 | SolarEdge Technologies Ltd.3.02SE3000x [208V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE3300 [240V] | Y | N | N | 3.3 kW, 240 Vac, Utility Interactive Inverter | 3.251 | 240 | 97.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 5.46 |  |  | 370 | 435 | 500 | 0.33 | 0.65 | 0.98 | 1.63 | 2.44 | 3.25 | 95.3 | 97.1 | 97.5 | 97.6 | 97.6 | 97.5 | 97.5 | 94.9 | 96.8 | 97.3 | 97.5 | 97.5 | 97.3 | 97.3 | 94.2 | 96.5 | 96.9 | 97.3 | 97.4 | 97.2 | 97.1 | SolarEdge Technologies Ltd.3.251SE3300 [240V]
SolarEdge Technologies Ltd. | SE3300x [240V] | N | Y | Y | 3.3 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 3.251 | 240 | 97.5 | [6/7/2017] | [2.52.326] | 2018-10-15 | Y | N |  | 5.46 |  |  | 370 | 435 | 500 | 0.33 | 0.65 | 0.98 | 1.63 | 2.44 | 3.25 | 95.3 | 97.1 | 97.5 | 97.6 | 97.6 | 97.5 | 97.5 | 94.9 | 96.8 | 97.3 | 97.5 | 97.5 | 97.3 | 97.3 | 94.2 | 96.5 | 96.9 | 97.3 | 97.4 | 97.2 | 97.1 | SolarEdge Technologies Ltd.3.251SE3300x [240V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE3800H-US [208V] | Y | Y | Y | 3.3 kW, 208 Vac HD-Wave technology Grid Support Utility Interactive Inverter | 3.255 | 208 | 99 | [01/17/2018] | [2.0.140] | 2018-10-15 | N | N |  | 4.12 |  |  | 360 | 395 | 480 | 0.3255 | 0.651 | 0.9765 | 1.6275 | 2.4413 | 3.255 | 89.795 | 99.3907 | 99.3812 | 99.2769 | 99.0026 | 98.7791 | 98.7455 | 92.1061 | 99.3518 | 99.377 | 99.2454 | 98.986 | 98.7542 | 98.8189 | 95.5802 | 99.4287 | 99.3924 | 99.2524 | 98.9976 | 98.7297 | 98.9699 | SolarEdge Technologies Ltd.3.255SE3800H-US [208V] | 2018-06-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE3300 [208V] | Y | N | N | 3.3 kW, 208 Vac, Utility Interactive Inverter | 3.288 | 208 | 97 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 5.55 |  |  | 320 | 410 | 500 | 0.33 | 0.66 | 0.99 | 1.64 | 2.47 | 3.29 | 95.5 | 97.2 | 97.3 | 97.4 | 97.2 | 97.4 | 97.2 | 94.8 | 96.7 | 97 | 97.2 | 97 | 96.8 | 96.9 | 93.5 | 96.3 | 96.6 | 96.9 | 96.9 | 96.8 | 96.7 | SolarEdge Technologies Ltd.3.288SE3300 [208V]
SolarEdge Technologies Ltd. | SE3300x [208V] | N | Y | Y | 3.3 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 3.288 | 208 | 97 | [6/7/2017] | [2.52.326] | 2018-10-15 | Y | N |  | 5.55 |  |  | 320 | 410 | 500 | 0.33 | 0.66 | 0.99 | 1.64 | 2.47 | 3.29 | 95.5 | 97.2 | 97.3 | 97.4 | 97.2 | 97.4 | 97.2 | 94.8 | 96.7 | 97 | 97.2 | 97 | 96.8 | 96.9 | 93.5 | 96.3 | 96.6 | 96.9 | 96.9 | 96.8 | 96.7 | SolarEdge Technologies Ltd.3.288SE3300x [208V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE3800H-US [240V] | Y | Y | Y | 3.8 kW, 240 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter | 3.747 | 240 | 99 | [6/26/2017] | [2.0.121] | 2018-10-15 | Y | N |  | 0 |  |  | 360 | 395 | 480 | 0.3 | 0.8 | 1.2 | 2 | 2.8 | 3.6 | 96.56 | 98.4 | 98.82 | 99.18 | 99.19 | 99.2 | 99 | 96.34 | 98.3 | 98.75 | 99.14 | 99.16 | 99.12 | 98.95 | 96.72 | 98.57 | 98.82 | 99.07 | 99.17 | 99.08 | 98.97 | SolarEdge Technologies Ltd.3.747SE3800H-US [240V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE3800 [240V] | Y | N | N | 3.8 kW, 240 Vac Utility Interactive Inverter | 3.79 | 240 | 98 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 2.24 |  |  | 360 | 400 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.84 | 3.79 | 96.1 | 97.6 | 98 | 98.1 | 98.1 | 98.2 | 98 | 95.7 | 97.3 | 97.8 | 98.1 | 98 | 98.2 | 97.9 | 94.6 | 96.8 | 97.5 | 97.9 | 97.9 | 97.8 | 97.6 | SolarEdge Technologies Ltd.3.79SE3800 [240V]
SolarEdge Technologies Ltd. | SE3800x [240V] | N | Y | Y | 3.8 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 3.79 | 240 | 98 | [6/7/2017] | [2.52.326] | 2018-10-15 | Y | N |  | 2.24 |  |  | 360 | 400 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.84 | 3.79 | 96.1 | 97.6 | 98 | 98.1 | 98.1 | 98.2 | 98 | 95.7 | 97.3 | 97.8 | 98.1 | 98 | 98.2 | 97.9 | 94.6 | 96.8 | 97.5 | 97.9 | 97.9 | 97.8 | 97.6 | SolarEdge Technologies Ltd.3.79SE3800x [240V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE4000 [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 3.97 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 5.92 |  |  | 370 | 435 | 500 | 0.4 | 0.79 | 1.19 | 1.99 | 2.98 | 3.97 | 95.3 | 97.2 | 97.6 | 97.7 | 97.4 | 97.7 | 97.4 | 94.9 | 96.9 | 97.4 | 97.5 | 97.3 | 97.2 | 97.3 | 94.2 | 96.5 | 97.1 | 97.3 | 97.2 | 97.1 | 97.1 | SolarEdge Technologies Ltd.3.97SE4000 [240V]
SolarEdge Technologies Ltd. | SE3800 [208V] | Y | N | N | 3.8 kW, 208 Vac Utility Interactive Inverter | 3.99 | 208 | 97 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 5.1 |  |  | 320 | 410 | 500 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 95.5 | 97.2 | 97.3 | 97.3 | 97.4 | 97.1 | 97.3 | 94.8 | 96.7 | 97.1 | 97.2 | 96.8 | 97 | 96.9 | 93.5 | 96.3 | 96.8 | 96.9 | 96.8 | 96.4 | 96.6 | SolarEdge Technologies Ltd.3.99SE3800 [208V]
SolarEdge Technologies Ltd. | SE3800x [208V] | N | Y | Y | 3.8 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 3.99 | 208 | 97 | [6/7/2017] | [2.52.326] | 2018-10-15 | Y | N |  | 5.1 |  |  | 320 | 410 | 500 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 95.5 | 97.2 | 97.3 | 97.3 | 97.4 | 97.1 | 97.3 | 94.8 | 96.7 | 97.1 | 97.2 | 96.8 | 97 | 96.9 | 93.5 | 96.3 | 96.8 | 96.9 | 96.8 | 96.4 | 96.6 | SolarEdge Technologies Ltd.3.99SE3800x [208V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE4000 [208V] | Y | N | N | 4 kW, 208 Vac Utility Interactive Inverter | 3.99 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 5.1 |  |  | 320 | 410 | 500 | 0.4 | 0.8 | 1.2 | 2 | 2.99 | 3.99 | 95.5 | 97.2 | 97.3 | 97.3 | 97.4 | 97.1 | 97.3 | 94.8 | 96.7 | 97.1 | 97.2 | 96.8 | 97 | 96.9 | 93.5 | 96.3 | 96.8 | 96.9 | 96.8 | 96.4 | 96.6 | SolarEdge Technologies Ltd.3.99SE4000 [208V]
SolarEdge Technologies Ltd. | SE5000H-US [208V] | Y | Y | Y | 5 kW, 208 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter | 4.979 | 208 | 98.5 | [6/26/2017] | [2.0.121] | 2018-10-15 | Y | N |  | 4.51 |  |  | 360 | 395 | 480 | 0.4 | 1 | 1.6 | 2.7 | 3.6 | 4.9 | 96.58 | 98.34 | 98.72 | 98.82 | 98.82 | 98.91 | 98.7 | 96.34 | 98.22 | 98.64 | 98.76 | 98.77 | 98.64 | 98.62 | 95.89 | 97.99 | 98.46 | 98.68 | 98.7 | 98.57 | 98.51 | SolarEdge Technologies Ltd.4.979SE5000H-US [208V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE5000 [208V] | Y | N | N | 5 kW, 208 Vac Utility Interactive Inverter | 4.98 | 208 | 97 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 5.46 |  |  | 320 | 410 | 500 | 0.5 | 1 | 1.49 | 2.49 | 3.73 | 4.98 | 96.6 | 97.3 | 97.4 | 97.2 | 97.1 | 96.6 | 97.1 | 95.9 | 97 | 97.2 | 97 | 97 | 96.6 | 97 | 96.2 | 96.6 | 96.9 | 96.9 | 96.4 | 96.5 | 96.5 | SolarEdge Technologies Ltd.4.98SE5000 [208V]
SolarEdge Technologies Ltd. | SE5000x [208V] | N | Y | Y | 5 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 4.98 | 208 | 97 | [6/7/2017] | [2.52.326] | 2018-10-15 | Y | N |  | 5.46 |  |  | 320 | 410 | 500 | 0.5 | 1 | 1.49 | 2.49 | 3.73 | 4.98 | 96.6 | 97.3 | 97.4 | 97.2 | 97.1 | 96.6 | 97.1 | 95.9 | 97 | 97.2 | 97 | 97 | 96.6 | 97 | 96.2 | 96.6 | 96.9 | 96.9 | 96.4 | 96.5 | 96.5 | SolarEdge Technologies Ltd.4.98SE5000x [208V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE5000 [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter | 4.99 | 240 | 98 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 2.24 |  |  | 370 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 96.7 | 97.9 | 98.1 | 98.1 | 98.3 | 98.1 | 98.1 | 96.4 | 97.7 | 98 | 98 | 98.2 | 98 | 98 | 95.7 | 97.4 | 97.7 | 97.8 | 97.8 | 97.9 | 97.7 | SolarEdge Technologies Ltd.4.99SE5000 [240V]
SolarEdge Technologies Ltd. | SE5000x [240V] | N | Y | Y | 5 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 4.99 | 240 | 98 | [6/7/2017] | [2.52.326] | 2018-10-15 | Y | N |  | 2.24 |  |  | 370 | 400 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.74 | 4.99 | 96.7 | 97.9 | 98.1 | 98.1 | 98.3 | 98.1 | 98.1 | 96.4 | 97.7 | 98 | 98 | 98.2 | 98 | 98 | 95.7 | 97.4 | 97.7 | 97.8 | 97.8 | 97.9 | 97.7 | SolarEdge Technologies Ltd.4.99SE5000x [240V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE5000 [277V] | Y | N | N | 5 kW, 277 Vac Utility Interactive Inverter | 5.01 | 277 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.24 |  |  | 405 | 425 | 480 | 0.5 | 1 | 1.5 | 2.51 | 3.76 | 5.01 | 97.1 | 98 | 98.2 | 98.3 | 98.1 | 98 | 98.1 | 97 | 98 | 98.2 | 98.2 | 98.1 | 97.9 | 98.1 | 96.5 | 97.7 | 98 | 98.1 | 98 | 97.8 | 97.9 | SolarEdge Technologies Ltd.5.01SE5000 [277V]
SolarEdge Technologies Ltd. | SE5000H-US [240V] | Y | Y | Y | 5 kW, 240 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter | 5.052 | 240 | 99 | [6/26/2017] | [2.0.121] | 2018-10-15 | Y | N |  | 4.52 |  |  | 360 | 395 | 480 | 0.4 | 1 | 1.6 | 2.7 | 3.6 | 4.9 | 96.65 | 98.42 | 98.79 | 99 | 98.97 | 99.11 | 98.84 | 96.38 | 98.28 | 98.7 | 98.94 | 98.92 | 98.86 | 98.76 | 96.03 | 98.07 | 98.57 | 98.87 | 98.87 | 98.81 | 98.68 | SolarEdge Technologies Ltd.5.052SE5000H-US [240V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE6000H-US [208V] | Y | Y | Y | 5 kW, 208 Vac HD-Wave technology Grid Support Utility Interactive Inverter | 5.054 | 208 | 99 | [01/17/2018] | [2.0.140] | 2018-10-15 | N | N |  | 4.52 |  |  | 360 | 395 | 480 | 0.5054 | 1.0108 | 1.5162 | 2.527 | 3.7905 | 5.054 | 96.6546 | 98.421 | 98.7873 | 99.0003 | 98.9676 | 99.1108 | 98.8401 | 96.3757 | 98.2834 | 98.7004 | 98.9384 | 98.9206 | 98.8604 | 98.7612 | 96.0285 | 98.0689 | 98.5658 | 98.8689 | 98.8702 | 98.8054 | 98.6764 | SolarEdge Technologies Ltd.5.054SE6000H-US [208V] | 2018-06-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE6000 [208V] | Y | N | N | 5.3 kW, 208 Vac, Utility Interactive Inverter | 5.33 | 208 | 97 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 5.22 |  |  | 320 | 410 | 500 | 0.53 | 1.07 | 1.6 | 2.66 | 3.99 | 5.33 | 96.6 | 97.3 | 97.4 | 97.2 | 97.1 | 96.4 | 97.1 | 95.9 | 97 | 97.2 | 97 | 97 | 96.4 | 97 | 96.2 | 96.6 | 96.9 | 96.9 | 96.4 | 96.3 | 96.5 | SolarEdge Technologies Ltd.5.33SE6000 [208V]
SolarEdge Technologies Ltd. | SE6000x [208V] | N | Y | Y | 6 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 5.33 | 208 | 97 | [6/7/2017] | [2.52.326] | 2018-10-15 | Y | N |  | 5.22 |  |  | 320 | 410 | 500 | 0.53 | 1.07 | 1.6 | 2.66 | 3.99 | 5.33 | 96.6 | 97.3 | 97.4 | 97.2 | 97.1 | 96.4 | 97.1 | 95.9 | 97 | 97.2 | 97 | 97 | 96.4 | 97 | 96.2 | 96.6 | 96.9 | 96.9 | 96.4 | 96.3 | 96.5 | SolarEdge Technologies Ltd.5.33SE6000x [208V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE6000 [240V] | Y | N | N | 6 kW, 240 Vac, Utility Interactive Inverter | 5.99 | 240 | 97.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 3.52 |  |  | 370 | 435 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 5.99 | 96.5 | 97.6 | 97.7 | 97.5 | 97.3 | 97 | 97.4 | 96 | 97.4 | 97.5 | 97.3 | 97.3 | 97 | 97.3 | 95.7 | 97.1 | 97.3 | 97.2 | 97.3 | 96.9 | 97.2 | SolarEdge Technologies Ltd.5.99SE6000 [240V]
SolarEdge Technologies Ltd. | SE6000x [240V] | N | Y | Y | 6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter, where x = (blank), A, or A-US. | 5.99 | 240 | 97.5 | [6/7/2017] | [2.52.326] | 2018-10-15 | Y | N |  | 3.52 |  |  | 370 | 435 | 500 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 5.99 | 96.5 | 97.6 | 97.7 | 97.5 | 97.3 | 97 | 97.4 | 96 | 97.4 | 97.5 | 97.3 | 97.3 | 97 | 97.3 | 95.7 | 97.1 | 97.3 | 97.2 | 97.3 | 96.9 | 97.2 | SolarEdge Technologies Ltd.5.99SE6000x [240V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE6000 [277V] | Y | N | N | 6 kW, 277 Vac, Utility Interactive Inverter | 6.04 | 277 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.74 |  |  | 405 | 425 | 480 | 0.6 | 1.21 | 1.81 | 3.02 | 4.53 | 6.04 | 97.5 | 98.2 | 98.3 | 98.2 | 98 | 97.9 | 98.1 | 97.3 | 98.1 | 98.2 | 98.2 | 98 | 97.8 | 98 | 96.9 | 97.8 | 98.1 | 98.1 | 97.9 | 97.7 | 97.9 | SolarEdge Technologies Ltd.6.04SE6000 [277V]
SolarEdge Technologies Ltd. | SE6000H-US [240V] | Y | Y | Y | 6 kW, 240 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter | 6.046 | 240 | 99 | [6/26/2017] | [2.0.121] | 2018-10-15 | Y | N |  | 4.52 |  |  | 360 | 395 | 480 | 0.5 | 1.3 | 1.9 | 3 | 4.3 | 5.8 | 97.17 | 98.61 | 98.9 | 98.95 | 98.95 | 98.98 | 98.96 | 96.95 | 98.51 | 98.82 | 98.89 | 98.9 | 98.95 | 98.79 | 96.65 | 98.32 | 98.7 | 98.83 | 98.85 | 98.71 | 98.7 | SolarEdge Technologies Ltd.6.046SE6000H-US [240V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE7000 [277V] | Y | N | N | 7 kW, 277 Vac Utility Interactive Inverter | 7.02 | 277 | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.24 |  |  | 100 | 425 | 480 | 0.7 | 1.4 | 2.1 | 3.51 | 5.26 | 7.02 | 97.7 | 98.2 | 98.3 | 98.2 | 97.9 | 97.6 | 98 | 97.6 | 98.2 | 98.2 | 98.1 | 97.9 | 97.6 | 98 | 97.2 | 98 | 98.1 | 98 | 97.8 | 97.5 | 97.8 | SolarEdge Technologies Ltd.7.02SE7000 [277V]
SolarEdge Technologies Ltd. | SE7600A-US [208V] | Y | Y | Y | 7.6 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter | 7.56 | 208 | 97.5 | [6/7/2017] | [2.52.326] | 2018-10-15 | Y | N |  | 5.75 |  |  | 325 | 375 | 480 | 0.756 | 1.512 | 2.268 | 3.78 | 5.67 | 7.56 | 96.3 | 97.4 | 97.6 | 97.6 | 97.5 | 97.3 | 97.5 | 96 | 97.2 | 97.5 | 97.5 | 97.4 | 97.2 | 97.3 | 95.2 | 96.8 | 97.1 | 97.2 | 97.1 | 96.8 | 97 | SolarEdge Technologies Ltd.7.56SE7600A-US [208V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE7600A-US [277V] | Y | N | N | 7.6 kW, 277 Vac, 1-phase Utility Interactive Inverter | 7.6 | 277 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 6.03 |  |  | 100 | 435 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.8 | 97.3 | 97.6 | 97.8 | 97.8 | 97.8 | 97.7 | 95.7 | 97.3 | 97.6 | 97.8 | 97.7 | 97.7 | 97.6 | 95.6 | 97.1 | 97.4 | 97.7 | 97.7 | 97.6 | 97.6 | SolarEdge Technologies Ltd.7.6SE7600A-US [277V]
SolarEdge Technologies Ltd. | SE7600H-US [240V] | Y | Y | Y | 7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 7.616 | 240 | 99 | [6/26/2017] | [2.0.121] | 2018-10-15 | Y | N |  | 4.52 |  |  | 360 | 395 | 480 | 0.7 | 1.6 | 2.4 | 3.6 | 5.5 | 7.3 | 97.72 | 98.8 | 98.97 | 98.97 | 99.04 | 98.73 | 98.94 | 97.52 | 98.7 | 98.91 | 98.93 | 99.02 | 98.69 | 98.89 | 97.24 | 98.57 | 98.83 | 98.87 | 98.75 | 98.71 | 98.71 | SolarEdge Technologies Ltd.7.616SE7600H-US [240V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE7600 [240V] | Y | N | N | 7.6 kW, 240 Vac, 1-phase Utility Interactive Inverter | 7.625 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.16 |  |  | 360 | 400 | 480 | 0.7625 | 1.525 | 2.288 | 3.813 | 5.719 | 7.625 | 97 | 97.9 | 98 | 97.9 | 97.7 | 97.3 | 97.7 | 96.6 | 97.8 | 97.9 | 97.9 | 97.6 | 97.3 | 97.7 | 95.7 | 97.4 | 97.6 | 97.6 | 97.5 | 97.1 | 97.5 | SolarEdge Technologies Ltd.7.625SE7600 [240V]
SolarEdge Technologies Ltd. | SE7600A-US [240V] | Y | Y | Y | 7.6 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 7.625 | 240 | 97.5 | [6/7/2017] | [2.52.326] | 2018-10-15 | Y | N |  | 2.16 |  |  | 360 | 400 | 480 | 0.7625 | 1.525 | 2.288 | 3.813 | 5.719 | 7.625 | 97 | 97.9 | 98 | 97.9 | 97.7 | 97.3 | 97.7 | 96.6 | 97.8 | 97.9 | 97.9 | 97.6 | 97.3 | 97.7 | 95.7 | 97.4 | 97.6 | 97.6 | 97.5 | 97.1 | 97.5 | SolarEdge Technologies Ltd.7.625SE7600A-US [240V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE9K [208V] | Y | N | N | 9 kW, 208 Vac, 3-phase Utility Interactive Inverter | 8.963 | 208 | 96.5 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 3.08 |  |  | 384 | 424 | 504 | 0.9 | 1.79 | 2.69 | 4.48 | 6.72 | 8.96 | 95.2 | 96.5 | 96.8 | 96.6 | 96.3 | 96.1 | 96.4 | 94.9 | 96.3 | 96.7 | 96.5 | 96.3 | 96 | 96.3 | 94.3 | 96 | 96.4 | 96.4 | 96.1 | 95.8 | 96.1 | SolarEdge Technologies Ltd.8.963SE9K [208V]
SolarEdge Technologies Ltd. | SE9KUS [208V] | N | Y | Y | 9 kW, 208 Vac, 3-phase Grid Support Utility Interactive Inverter | 8.963 | 208 | 96.5 | [6/8/2017] | [2.19.759] | 2018-10-15 | Y | N |  | 3.08 |  |  | 384 | 424 | 504 | 0.9 | 1.79 | 2.69 | 4.48 | 6.72 | 8.96 | 95.2 | 96.5 | 96.8 | 96.6 | 96.3 | 96.1 | 96.4 | 94.9 | 96.3 | 96.7 | 96.5 | 96.3 | 96 | 96.3 | 94.3 | 96 | 96.4 | 96.4 | 96.1 | 95.8 | 96.1 | SolarEdge Technologies Ltd.8.963SE9KUS [208V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE10K [480V] | Y | N | N | 10 kW, 480 Vac, 3-phase Utility Interactive Inverter | 9.85 | 480 | 98 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 3.13 |  |  | 100 | 882 | 962 | 0.98 | 1.97 | 2.95 | 4.92 | 7.38 | 9.85 | 95.5 | 97.4 | 97.8 | 98.1 | 98.1 | 98 | 97.9 | 95.1 | 97.3 | 97.7 | 98 | 98 | 97.9 | 97.8 | 94.2 | 97 | 97.5 | 97.9 | 98 | 97.9 | 97.7 | SolarEdge Technologies Ltd.9.85SE10K [480V]
SolarEdge Technologies Ltd. | SE10KUS [480V] | N | Y | Y | 10 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 9.85 | 480 | 98 | [6/8/2017] | [2.19.759] | 2018-10-15 | Y | N |  | 3.13 |  |  | 100 | 882 | 962 | 0.98 | 1.97 | 2.95 | 4.92 | 7.38 | 9.85 | 95.5 | 97.4 | 97.8 | 98.1 | 98.1 | 98 | 97.9 | 95.1 | 97.3 | 97.7 | 98 | 98 | 97.9 | 97.8 | 94.2 | 97 | 97.5 | 97.9 | 98 | 97.9 | 97.7 | SolarEdge Technologies Ltd.9.85SE10KUS [480V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE10000A-US [208V] | Y | Y | Y | 10 kW, 208 Vac, 1-phase Grid Support Utility Interactive Inverter | 9.93 | 208 | 97 | [6/7/2017] | [2.52.326] | 2018-10-15 | Y | N |  | 5.75 |  |  | 325 | 375 | 480 | 0.993 | 1.986 | 2.979 | 4.965 | 7.448 | 9.93 | 96.8 | 97.6 | 97.7 | 97.5 | 97.4 | 97.1 | 97.4 | 96.5 | 97.4 | 97.5 | 97.4 | 97.2 | 96.9 | 97.3 | 96.2 | 97 | 97.2 | 97.1 | 96.9 | 96.7 | 96.9 | SolarEdge Technologies Ltd.9.93SE10000A-US [208V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE10000A-US [240V] | Y | Y | Y | 10 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 9.94 | 240 | 97.5 | [6/7/2017] | [2.52.326] | 2018-10-15 | Y | N |  | 5.95 |  |  | 360 | 400 | 480 | 0.99 | 1.99 | 2.98 | 4.97 | 7.46 | 9.94 | 96.8 | 97.6 | 97.8 | 97.8 | 97.7 | 97.5 | 97.7 | 96.6 | 97.5 | 97.7 | 97.6 | 97.6 | 97.4 | 97.6 | 96.4 | 97.3 | 97.5 | 97.4 | 97.4 | 97.2 | 97.3 | SolarEdge Technologies Ltd.9.94SE10000A-US [240V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE10000A-US [277V] | Y | N | N | 10 kW, 277 Vac, 1-phase Utility Interactive Inverter | 9.95 | 277 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 6.03 |  |  | 415 | 435 | 480 | 0.995 | 1.99 | 2.985 | 4.975 | 7.463 | 9.95 | 96.5 | 97.5 | 97.8 | 97.8 | 97.8 | 97.7 | 97.7 | 96.4 | 97.5 | 97.8 | 97.8 | 97.7 | 97.6 | 97.7 | 96.3 | 97.4 | 97.6 | 97.7 | 97.6 | 97.5 | 97.5 | SolarEdge Technologies Ltd.9.95SE10000A-US [277V]
SolarEdge Technologies Ltd. | SE10000H-US [240V] | Y | Y | Y | 10 kW, 240 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter | 9.994 | 240 | 99 | [01/17/2018] | [2.0.350] | 2018-10-15 | N | N |  | 6 |  |  | 360 | 395 | 480 | 0.999 | 1.999 | 2.998 | 4.997 | 7.496 | 9.994 | 97.86 | 98.83 | 98.94 | 99.23 | 98.95 | 98.63 | 98.94 | 97.69 | 98.74 | 98.88 | 99.18 | 98.91 | 98.55 | 98.89 | 97.44 | 98.54 | 98.68 | 98.7 | 98.62 | 98.1 | 98.57 | SolarEdge Technologies Ltd.9.994SE10000H-US [240V] [SI1] | 2018-04-02 | 2018-10-15
SolarEdge Technologies Ltd. | SE10000H-US [208V] | Y | Y | Y | 10 kW, 208 Vac, 1-phase, HD-Wave technology Grid Support Utility Interactive Inverter | 10.001 | 208 | 98.5 | [01/17/2018] | [2.0.350] | 2018-10-15 | N | N |  | 5.71 |  |  | 360 | 395 | 480 | 1 | 2 | 3 | 5.001 | 7.501 | 10.001 | 97.77 | 98.73 | 98.83 | 99.07 | 98.67 | 98.17 | 98.71 | 97.65 | 98.66 | 98.77 | 98.97 | 98.58 | 98.09 | 98.62 | 97.44 | 98.54 | 98.7 | 98.7 | 98.62 | 98.1 | 98.57 | SolarEdge Technologies Ltd.10.001SE10000H-US [208V] [SI1] | 2018-04-02 | 2018-10-15
SolarEdge Technologies Ltd. | SE11400A-US [277V] | Y | N | N | 11.4 kW, 277 Vac, 1-phase Utility Interactive Inverter | 11.34 | 277 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 6.03 |  |  | 415 | 435 | 480 | 1.134 | 2.268 | 3.402 | 5.67 | 8.505 | 11.34 | 96.8 | 97.6 | 97.9 | 97.8 | 97.7 | 97.6 | 97.7 | 96.7 | 97.6 | 97.8 | 97.7 | 97.7 | 97.5 | 97.7 | 96.5 | 97.4 | 97.7 | 97.7 | 97.6 | 97.5 | 97.6 | SolarEdge Technologies Ltd.11.34SE11400A-US [277V]
SolarEdge Technologies Ltd. | SE11400A-US [240V] | Y | Y | Y | 11.4 kW, 240 Vac, 1-phase Grid Support Utility Interactive Inverter | 11.39 | 240 | 97.5 | [6/7/2017] | [2.52.326] | 2018-10-15 | Y | N |  | 5.95 |  |  | 360 | 400 | 480 | 1.139 | 2.278 | 3.417 | 5.695 | 8.543 | 11.39 | 96.9 | 97.7 | 97.8 | 97.8 | 97.6 | 97.4 | 97.7 | 96.8 | 97.6 | 97.7 | 97.6 | 97.5 | 97.3 | 97.5 | 96.5 | 97.4 | 97.5 | 97.5 | 97.3 | 97.1 | 97.3 | SolarEdge Technologies Ltd.11.39SE11400A-US [240V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE11400H-US [240V] | Y | Y | Y | 11.4 kW, 240 Vac, HD-Wave technology Grid Support Utility Interactive Inverter | 11.393 | 240 | 99 | [01/17/2018] | [2.0.350] | 2018-10-15 | N | N |  | 6 |  |  | 360 | 395 | 480 | 1.139 | 2.279 | 3.418 | 5.697 | 8.545 | 11.393 | 97.88 | 98.84 | 98.95 | 99.16 | 98.82 | 98.41 | 98.85 | 97.91 | 98.83 | 98.93 | 99.17 | 98.83 | 98.4 | 98.85 | 97.42 | 98.63 | 98.79 | 98.82 | 98.8 | 98.39 | 98.72 | SolarEdge Technologies Ltd.11.393SE11400H-US [240] [SI1] | 2018-04-02 | 2018-10-15
SolarEdge Technologies Ltd. | SE14.4KUS [208V] | Y | Y | Y | 14.4 kW, 208 Vac, 3-phase Grid Support Utility Interactive Inverter | 14.51 | 208 | 97 | [6/8/2017] | [2.19.759] | 2018-10-15 | Y | N |  | 4.16 |  |  | 400 | 460 | 600 | 1.45 | 2.9 | 4.35 | 7.26 | 10.88 | 14.51 | 95.9 | 97.3 | 97.5 | 97.5 | 97 | 96.6 | 97.1 | 95.2 | 97.1 | 97.2 | 97.3 | 97.2 | 96.8 | 97.1 | 94.7 | 96.3 | 96.7 | 96.9 | 96.4 | 96.2 | 96.4 | SolarEdge Technologies Ltd.14.51SE14.4KUS [208V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE43.2KUS [208V] | Y | Y | Y | 43.2 kW, 208 Vac, 3-phase Grid Support Utility Interactive Inverter. (Made up of three SE14.4KUS installed together rated max output power = 43.2kW) | 14.51 | 208 | 97 | [11/02/2017] | [2.19.759] | 2018-10-15 | Y | N | Performance data is the same as SE14.4KUS. | 4.16 |  |  | 400 | 460 | 600 | 1.451 | 2.902 | 4.353 | 7.255 | 10.8825 | 14.51 | 95.8927 | 97.2782 | 97.4837 | 97.462 | 97.0093 | 96.6434 | 97.1118 | 95.2252 | 97.0865 | 97.1922 | 97.3046 | 97.1963 | 96.8019 | 97.1145 | 94.6669 | 96.2868 | 96.6724 | 96.8566 | 96.3889 | 96.1759 | 96.4365 | SolarEdge Technologies Ltd.14.51SE43.2KUS [208V] [SI1] | 2018-02-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE20K [480V] | Y | N | N | 20 kW, 480 Vac, 3-phase Utility Interactive Inverter | 20.05 | 480 | 98 | Not Applicable | Not Applicable | Not Applicable | Y | N |  | 3.48 |  |  | 842 | 882 | 962 | 2.01 | 4.01 | 6.02 | 10.03 | 15.04 | 20.05 | 96.6 | 97.6 | 97.9 | 98 | 98 | 97.9 | 97.9 | 96.6 | 97.5 | 97.9 | 98 | 98 | 97.9 | 97.9 | 96 | 97.3 | 97.7 | 97.9 | 97.8 | 97.8 | 97.7 | SolarEdge Technologies Ltd.20.05SE20K [480V]
SolarEdge Technologies Ltd. | SE20KUS [480V] | N | Y | Y | 20 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 20.05 | 480 | 98 | [6/8/2017] | [2.19.759] | 2018-10-15 | Y | N |  | 3.48 |  |  | 842 | 882 | 962 | 2.01 | 4.01 | 6.02 | 10.03 | 15.04 | 20.05 | 96.6 | 97.6 | 97.9 | 98 | 98 | 97.9 | 97.9 | 96.6 | 97.5 | 97.9 | 98 | 98 | 97.9 | 97.9 | 96 | 97.3 | 97.7 | 97.9 | 97.8 | 97.8 | 97.7 | SolarEdge Technologies Ltd.20.05SE20KUS [480V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE30KUS [480V] | Y | Y | Y | 30 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 30.159 | 480 | 98.5 | [9/20/2017] | [2.19.759] | 2018-10-15 | N | N |  | 7.06 |  |  | 790 | 850 | 950 | 3 | 6 | 9 | 15 | 22.5 | 30 | 97.4085 | 98.3647 | 98.5506 | 98.5075 | 98.4804 | 98.3856 | 98.4411 | 97.0794 | 98.2049 | 98.429 | 98.4194 | 98.4029 | 98.314 | 98.3422 | 96.4164 | 97.9007 | 98.2089 | 98.2953 | 98.2622 | 98.2 | 98.1677 | SolarEdge Technologies Ltd.30.159SE30KUS [480V] | 2018-01-02 | 2018-10-15
SolarEdge Technologies Ltd. | SE100KUS [480V] | Y | Y | Y | 100 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter. (Made up of three SE33.3KUS installed together rated max output power = 100kW). | 33.3 | 480 | 98.5 | [11/02/2017] | [2.19.759] | 2018-10-15 | Y | N | Performance data is the same as SE33.3KUS. | 5.05 |  |  | 790 | 850 | 950 | 3.34 | 6.68 | 10.02 | 16.7 | 25.05 | 33.4 | 97.1892 | 98.2429 | 98.8889 | 98.5098 | 98.6777 | 98.4615 | 98.5757 | 96.664 | 98.0844 | 98.1132 | 98.5059 | 98.3704 | 98.1595 | 98.2749 | 96.3383 | 97.844 | 97.8428 | 98.4706 | 98.3128 | 98.1595 | 98.1794 | SolarEdge Technologies Ltd.33.3SE100KUS [480V] [SI1] | 2018-02-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE33.3KUS [480V] | Y | Y | Y | 33.3 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter | 33.3 | 480 | 98.5 | [6/8/2017] | [2.19.759] | 2018-10-15 | Y | N |  | 5.05 |  |  | 790 | 850 | 950 | 3.34 | 6.68 | 10.02 | 16.7 | 25.05 | 33.4 | 97.2 | 98.2 | 98.9 | 98.5 | 98.7 | 98.5 | 98.6 | 96.7 | 98.1 | 98.1 | 98.5 | 98.4 | 98.2 | 98.3 | 96.3 | 97.8 | 97.8 | 98.5 | 98.3 | 98.2 | 98.2 | SolarEdge Technologies Ltd.33.3SE33.3KUS [480V] | 2017-07-01 | 2018-10-15
SolarEdge Technologies Ltd. | SE66.6KUS [480V] | Y | Y | Y | 66.6 kW, 480 Vac, 3-phase Grid Support Utility Interactive Inverter. (Made up of two SE33.3KUS installed together rated max output power = 66.6kW). | 33.3 | 480 | 98.5 | [11/02/2017] | [2.19.759] | 2018-10-15 | Y | N | Performance data is the same as SE33.3KUS. | 5.05 |  |  | 790 | 850 | 950 | 3.34 | 6.68 | 10.02 | 16.7 | 25.05 | 33.4 | 97.1892 | 98.2429 | 98.8889 | 98.5098 | 98.6777 | 98.4615 | 98.5757 | 96.664 | 98.0844 | 98.1132 | 98.5059 | 98.3704 | 98.1595 | 98.2749 | 96.3383 | 97.844 | 97.8428 | 98.4706 | 98.3128 | 98.1595 | 98.1794 | SolarEdge Technologies Ltd.33.3SE66.6KUS [480V] [SI1] | 2018-02-01 | 2018-10-15
Solargate | SG-4000 [240V] | Y | N | N | 4000 W 240 Vac Utility Interactive Inverter | 4.03 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.19 |  |  | 100 | 310 | 440 | 0.4 | 0.81 | 1.21 | 2.02 | 3.02 | 4.03 | 91.6 | 94.5 | 95.2 | 95.3 | 95 | 93.9 | 94.9 | 90.2 | 94.5 | 95.5 | 95.8 | 95.6 | 95 | 95.3 | 87.4 | 92.8 | 94 | 95 | 95.2 | 94.6 | 94.5 | Solargate4.03SG-4000 [240V]
Solaria Corporation | Solaria PowerXT-345R-AC [240V] | Y | Y | Y | 345 W Monocrystalline ACPV Module. DC Module: Solaria PowerXT-345R-PD. Microinverter IQ7PLUS-72-ACM-US [240V] [SI1]. | 0.29 | 240 | 97 | [05/03/2018] | [V02.10.00];[V02.12.00] | 2018-10-15 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 36 | 45 | 0.03 | 0.06 | 0.09 | 0.15 | 0.22 | 0.29 | 95 | 96.2 | 97.1 | 97.4 | 97.2 | 96.6 | 97.1 | 94.2 | 95.6 | 96.8 | 97.5 | 97.4 | 97.2 | 97.1 | 93.3 | 94.8 | 96.4 | 97.3 | 97.3 | 97.1 | 96.9 | Solaria Corporation0.29Solaria PowerXT-345R-AC [240V] | 2018-06-01 | 2018-10-15
Solaria Corporation | Solaria PowerXT-350R-AC [240V] | Y | Y | Y | 350 W Monocrystalline ACPV Module. DC Module: Solaria PowerXT-350R-PD. Microinverter IQ7PLUS-72-ACM-US [240V] [SI1]. | 0.29 | 240 | 97 | [05/03/2018] | [V02.10.00];[V02.12.00] | 2018-10-15 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 36 | 45 | 0.03 | 0.06 | 0.09 | 0.15 | 0.22 | 0.29 | 95 | 96.2 | 97.1 | 97.4 | 97.2 | 96.6 | 97.1 | 94.2 | 95.6 | 96.8 | 97.5 | 97.4 | 97.2 | 97.1 | 93.3 | 94.8 | 96.4 | 97.3 | 97.3 | 97.1 | 96.9 | Solaria Corporation0.29Solaria PowerXT-350R-AC [240V] | 2018-06-01 | 2018-10-15
Solaria Corporation | Solaria PowerXT-355R-AC [240V] | Y | Y | Y | 355 W Monocrystalline ACPV Module. DC Module: Solaria PowerXT-355R-PD. Microinverter IQ7PLUS-72-ACM-US [240V] [SI1]. | 0.29 | 240 | 97 | [05/03/2018] | [V02.10.00];[V02.12.00] | 2018-10-15 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 36 | 45 | 0.03 | 0.06 | 0.09 | 0.15 | 0.22 | 0.29 | 95 | 96.2 | 97.1 | 97.4 | 97.2 | 96.6 | 97.1 | 94.2 | 95.6 | 96.8 | 97.5 | 97.4 | 97.2 | 97.1 | 93.3 | 94.8 | 96.4 | 97.3 | 97.3 | 97.1 | 96.9 | Solaria Corporation0.29Solaria PowerXT-355R-AC [240V] | 2018-06-01 | 2018-10-15
Solaria Corporation | Solaria PowerXT-360R-AC [240V] | Y | Y | Y | 360 W Monocrystalline ACPV Module. DC Module: Solaria PowerXT-360R-PD. Microinverter IQ7PLUS-72-ACM-US [240V] [SI1]. | 0.29 | 240 | 97 | [05/03/2018] | [V02.10.00];[V02.12.00] | 2018-10-15 | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.025 |  |  | 27 | 36 | 45 | 0.03 | 0.06 | 0.09 | 0.15 | 0.22 | 0.29 | 95 | 96.2 | 97.1 | 97.4 | 97.2 | 96.6 | 97.1 | 94.2 | 95.6 | 96.8 | 97.5 | 97.4 | 97.2 | 97.1 | 93.3 | 94.8 | 96.4 | 97.3 | 97.3 | 97.1 | 96.9 | Solaria Corporation0.29Solaria PowerXT-360R-AC [240V] | 2018-06-01 | 2018-10-15
Sol-Ark | Sol-Ark-8k-48-ST [208V] | Y | N | N | 8000 W, 208 Vac, 1-phase, Hybrid Utility Interactive PV and Battery Inverter | 7.839 | 208 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 13.4 |  |  | 240 | 370 | 425 | 0.784 | 1.568 | 2.352 | 3.92 | 5.88 | 7.84 | 91.4863 | 94.7602 | 95.3527 | 97.2963 | 97.1851 | 96.8599 | 96.6231 | 91.7 | 94.9639 | 95.4957 | 97.4288 | 97.2316 | 96.9297 | 96.715 | 91.9073 | 94.929 | 95.3698 | 97.3187 | 96.9256 | 97.0631 | 96.5278 | Sol-Ark7.839Sol-Ark-8k-48-ST [208V] | 2018-11-01
Sol-Ark | Sol-Ark-8k-48-ST [240V] | Y | N | N | 8000 W, 240V, 1-phase, Hybrid Utility Interactive PV and Battery Inverter | 7.976 | 240 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 13.4 |  |  | 240 | 370 | 425 | 0.798 | 1.596 | 2.394 | 3.99 | 5.985 | 7.98 | 91.8196 | 94.911 | 95.5205 | 97.0796 | 96.988 | 97.1305 | 96.5277 | 91.6709 | 95.0008 | 95.7077 | 97.5465 | 97.4459 | 97.0835 | 96.8871 | 91.5513 | 95.0717 | 95.8584 | 97.6006 | 97.274 | 97.0868 | 96.8243 | Sol-Ark7.976Sol-Ark-8k-48-ST [240V] | 2018-11-01
Solarmax | SM 12MT2A | Y | N | N | Photovoltaic Inverter | 11.7 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.45 |  |  | 340 | 500 | 850 | 1.17 | 2.33 | 3.5 | 5.83 | 8.75 | 11.67 | 95.2 | 96.6 | 96.6 | 97 | 96.7 | 96.5 | 96.7 | 95.8 | 97.1 | 97.6 | 97.5 | 97.5 | 97.2 | 97.4 | 97.4 | 97.8 | 98.1 | 98.2 | 97.9 | 97.7 | 97.9 | Solarmax11.7SM 12MT2A
Solarmax | SM 15MT3A | Y | N | N | Photovoltaic Inverter | 14.7 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 325 | 400 | 500 | 1.47 | 2.94 | 4.41 | 7.35 | 11.03 | 14.71 | 94.6 | 96.1 | 96.7 | 96.7 | 96.5 | 96.1 | 96.4 | 95 | 96.6 | 96.8 | 97 | 97 | 96.7 | 96.9 | 95 | 96.7 | 96.9 | 97.3 | 97.2 | 96.9 | 97.1 | Solarmax14.7SM 15MT3A
Solarmax | SM 18MT3A | Y | N | N | Photovoltaic Inverter | 17.7 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 400 | 595 | 850 | 1.77 | 3.54 | 5.31 | 8.84 | 13.27 | 17.69 | 95.4 | 96.4 | 96.9 | 97.1 | 96.7 | 96.4 | 96.7 | 96.2 | 97.5 | 97.5 | 97.4 | 97.4 | 97 | 97.4 | 96.5 | 97.6 | 97.7 | 97.7 | 97.5 | 97.4 | 97.5 | Solarmax17.7SM 18MT3A
Solarmax | 75TS-A | Y | N | N | Photovoltaic Inverter | 75.13 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 11.24 |  |  | 325 | 450 | 600 | 7.51 | 15.03 | 22.54 | 37.57 | 56.35 | 75.13 | 93.9 | 95.8 | 95.9 | 95.6 | 95 | 94.3 | 95.2 | 93.5 | 95.7 | 95.7 | 95.5 | 94.8 | 93.8 | 95 | 92.2 | 94.2 | 94.8 | 94.8 | 94.3 | 93.6 | 94.3 | Solarmax75.1375TS-A
Sonnetek | Sonnetek 2000 [120V] | Y | N | N | 2000 W, 120 Vac Utility Interactive Inverter | 2 | 120 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 14.18 |  |  | 100 | 240 | 360 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89 | 92.2 | 92.8 | 92.6 | 91.7 | 90.8 | 91.9 | 88.6 | 91.9 | 92.8 | 92.6 | 91.6 | 90.5 | 91.8 | 87.1 | 90.8 | 91.8 | 92.2 | 91.3 | 90.1 | 91.3 | Sonnetek2Sonnetek 2000 [120V]
Sonnetek | Sonnetek 4000 [240V] | Y | N | N | 4000 W, 240 Vac Utility Interactive Inverter | 4.03 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.19 |  |  | 100 | 310 | 440 | 0.4 | 0.81 | 1.21 | 2.02 | 3.02 | 4.03 | 91.6 | 94.5 | 95.2 | 95.3 | 95 | 93.9 | 94.9 | 90.2 | 94.5 | 95.5 | 95.8 | 95.6 | 95 | 95.3 | 87.4 | 92.8 | 94 | 95 | 95.2 | 94.6 | 94.5 | Sonnetek4.03Sonnetek 4000 [240V]
Sparq Systems | S215NA2240 [240V] | Y | N | N | 207 W, 240 Vac Microinverter | 0.21 | 240 | 93 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.03 |  |  | 22 | 27 | 40 | 0.02 | 0.04 | 0.06 | 0.1 | 0.16 | 0.21 | 84 | 91.2 | 92.8 | 94.3 | 94.7 | 94 | 93.7 | 83.8 | 91 | 91.5 | 93.9 | 94.1 | 93.8 | 93.2 | 81.5 | 89.3 | 92.1 | 93.3 | 93.6 | 93.4 | 92.6 | Sparq Systems0.21S215NA2240 [240V]
Sparq Systems | Q1000-4101 [240V] | Y | N | N | 960 W, 240 Vac Microinverter | 0.96 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.1 |  |  | 28 | 29 | 31 | 0.1 | 0.19 | 0.29 | 0.48 | 0.72 | 0.96 | 91.5 | 95 | 95.5 | 96.1 | 96.6 | 96.7 | 96.1 | 91.4 | 94.9 | 95.4 | 95.8 | 96.4 | 96.5 | 95.9 | 91.3 | 94.9 | 95.1 | 95.8 | 96.3 | 96.4 | 95.8 | Sparq Systems0.96Q1000-4101 [240V]
Sparq Systems | Q1200-4101 [240V] | Y | Y | Y | 1200 W, 240 Vac, 60Hz Grid Support Utility Interactive Inverter | 1.165 | 240 | 96.5 | [06/29/2018] | [1.20.62] | 2018-10-15 | N | Y |  | 0.04 |  |  | 28 | 29 | 31 | 0.12 | 0.24 | 0.36 | 0.6 | 0.9 | 1.2 | 91.2693 | 95.4412 | 96.5736 | 97.1364 | 97.0548 | 96.7999 | 96.6893 | 90.983 | 95.514 | 96.5823 | 97.0419 | 96.9805 | 96.7573 | 96.6212 | 89.75 | 95.2351 | 96.4213 | 97.0117 | 96.9939 | 96.8163 | 96.5424 | Sparq Systems1.165Q1200-4101 [240V] | 2018-08-01 | 2018-10-15
Sputnik Engineering | SM 12MT2A | Y | N | N | Photovoltaic Inverter | 11.7 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.45 |  |  | 340 | 500 | 850 | 1.17 | 2.33 | 3.5 | 5.83 | 8.75 | 11.67 | 95.2 | 96.6 | 96.6 | 97 | 96.7 | 96.5 | 96.7 | 95.8 | 97.1 | 97.6 | 97.5 | 97.5 | 97.2 | 97.4 | 97.4 | 97.8 | 98.1 | 98.2 | 97.9 | 97.7 | 97.9 | Sputnik Engineering11.7SM 12MT2A
Sputnik Engineering | SM 15MT3A | Y | N | N | Photovoltaic Inverter | 14.7 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 325 | 400 | 500 | 1.47 | 2.94 | 4.41 | 7.35 | 11.03 | 14.71 | 94.6 | 96.1 | 96.7 | 96.7 | 96.5 | 96.1 | 96.4 | 95 | 96.6 | 96.8 | 97 | 97 | 96.7 | 96.9 | 95 | 96.7 | 96.9 | 97.3 | 97.2 | 96.9 | 97.1 | Sputnik Engineering14.7SM 15MT3A
Sputnik Engineering | SM 18MT3A | Y | N | N | Photovoltaic Inverter | 17.7 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 400 | 595 | 850 | 1.77 | 3.54 | 5.31 | 8.84 | 13.27 | 17.69 | 95.4 | 96.4 | 96.9 | 97.1 | 96.7 | 96.4 | 96.7 | 96.2 | 97.5 | 97.5 | 97.4 | 97.4 | 97 | 97.4 | 96.5 | 97.6 | 97.7 | 97.7 | 97.5 | 97.4 | 97.5 | Sputnik Engineering17.7SM 18MT3A
Sputnik Engineering | 75TS | Y | N | N | Photovoltaic Inverter | 75.13 |  | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 11.24 |  |  | 325 | 450 | 600 | 7.51 | 15.03 | 22.54 | 37.57 | 56.35 | 75.13 | 93.9 | 95.8 | 95.9 | 95.6 | 95 | 94.3 | 95.2 | 93.5 | 95.7 | 95.7 | 95.5 | 94.8 | 93.8 | 95 | 92.2 | 94.2 | 94.8 | 94.8 | 94.3 | 93.6 | 94.3 | Sputnik Engineering75.1375TS
Sungrow Power Supply | SG30KU | Y | N | N | 30 kW, 3-phase, Utility Interactive Inverter | 30 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.52 |  |  | 480 | 705 | 800 | 3 | 6 | 9 | 15 | 22.5 | 30 | 95.5 | 97 | 97.5 | 97.5 | 97.3 | 96.8 | 97.3 | 97.3 | 98.2 | 98.5 | 98.5 | 98.3 | 98.1 | 98.3 | 96.3 | 97.9 | 98.2 | 98.3 | 98.2 | 98 | 98.1 | Sungrow Power Supply30SG30KU
Sungrow Power Supply | SG36KU | Y | N | N | 36 kW, 3-phase Utility Interactive Inverter | 36 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.51 |  |  | 580 | 700 | 800 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 96.6 | 97.7 | 97.8 | 97.8 | 97.5 | 97 | 97.5 | 97.6 | 98.2 | 98.5 | 98.4 | 98.2 | 97.9 | 98.2 | 97.1 | 98.1 | 98.3 | 98.3 | 98.1 | 97.8 | 98.1 | Sungrow Power Supply36SG36KU
Sungrow Power Supply | SG60KU | Y | N | N | 60 kW, transformerless Utility Interactive Inverter | 60 |  | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.84 |  |  | 550 | 700 | 850 | 6 | 12 | 18 | 30 | 45 | 60 | 97.8 | 98.5 | 98.6 | 98.5 | 98.4 | 98.5 | 98.5 | 97.8 | 98.6 | 98.8 | 99 | 98.8 | 98.6 | 98.8 | 97.2 | 98.3 | 98.6 | 98.7 | 98.4 | 98.3 | 98.4 | Sungrow Power Supply60SG60KU
Sungrow Power Supply | SG60KU-M | Y | N | N | 60 kW, transformerless Utility Interactive Inverter | 60 |  | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.88 |  |  | 550 | 700 | 850 | 6 | 12 | 18 | 30 | 45 | 60 | 97.8 | 98.2 | 98.2 | 98.4 | 98.4 | 98 | 98.3 | 97.8 | 98.6 | 98.8 | 98.9 | 98.7 | 98.5 | 98.7 | 97.5 | 98.6 | 98.5 | 98.8 | 98.5 | 98.4 | 98.5 | Sungrow Power Supply60SG60KU-M
Sungrow Power Supply | SG100KU-outdoor [480V] | Y | N | N | 100 kW, 480 Vac Utility Interactive Inverter | 100 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 159.8 |  |  | 300 | 350 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 94.9 | 96.5 | 96.8 | 96.8 | 96.6 | 96 | 96.6 | 93.8 | 96.3 | 96.5 | 96.7 | 96.3 | 95.6 | 96.3 | 94.5 | 96.2 | 96.6 | 96.5 | 96 | 95.2 | 96.1 | Sungrow Power Supply100SG100KU-outdoor [480V]
Sungrow Power Supply | SG100KU [480V] | Y | N | N | 100 kW, 480 Vac Utility Interactive Inverter | 101 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 41.78 |  |  | 300 | 380 | 480 | 10.1 | 20.2 | 30.3 | 50.5 | 75.75 | 101 | 94.75 | 96.01 | 96.27 | 97.32 | 96.84 | 96.01 | 96.71 | 94.29 | 95.59 | 96.07 | 96.96 | 96.59 | 95.88 | 96.43 | 93.54 | 95.36 | 95.54 | 96.82 | 96.31 | 95.64 | 96.13 | Sungrow Power Supply101SG100KU [480V]
Sungrow Power Supply | SG250KC [600V] | Y | N | N | 250 kW, 600 Vac Utility Interactive Inverter (Canada) | 250 | 600 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 71 | 250 | 71 | 320 | 360 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 95.8 | 97.4 | 97.1 | 97.2 | 96.8 | 96.2 | 96.9 | 95.3 | 96.9 | 97.1 | 97.1 | 96.7 | 96.1 | 96.7 | 94.5 | 95.9 | 96.7 | 96.6 | 96.4 | 95.9 | 96.4 | Sungrow Power Supply250SG250KC [600V]
Sungrow Power Supply | SG250KU [480V] | Y | N | N | 250 kW, 480 Vac Utility Interactive Inverter (United States) | 250 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 50 | 250 | 50 | 320 | 360 | 480 | 25 | 50 | 75 | 125 | 187.5 | 250 | 95 | 96.6 | 97.1 | 97.1 | 96.5 | 96 | 96.6 | 95.3 | 96.8 | 97.4 | 96.9 | 96.3 | 95.8 | 96.5 | 93.7 | 95.8 | 96.6 | 96.5 | 96.3 | 95.8 | 96.3 | Sungrow Power Supply250SG250KU [480V]
Sungrow Power Supply | SG500LV | Y | N | N | 500 kW Utility Interactive Inverter to connect with medium voltage transformer | 500 |  | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 90 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 94.5 | 96.6 | 97 | 97 | 96.7 | 95.4 | 96.6 | 94.2 | 96.5 | 97 | 97 | 96.5 | 95.5 | 96.5 | 93.6 | 96.3 | 96.9 | 96.2 | 95.9 | 95.4 | 96 | Sungrow Power Supply500SG500LV
Sungrow Power Supply | SG750MX | Y | N | N | 750 kW, 3-phase, Utility Interactive Inverter with medium voltage NEMA NEMA TP1 transformer | 750 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 87 |  |  | 500 | 580 | 800 | 75 | 150 | 225 | 375 | 562.5 | 750 | 95 | 97 | 97.5 | 97.5 | 97.2 | 96.6 | 97.2 | 94.4 | 96.9 | 97.5 | 97.5 | 97.2 | 96.5 | 97.1 | 93 | 96.1 | 96.9 | 97.1 | 96.7 | 96.1 | 96.6 | Sungrow Power Supply750SG750MX
Sungrow Power Supply | SG800MX | Y | N | N | 800 kW, 3-phase, Utility Interactive Inverter with medium voltage NEMA NEMA TP1 transformer | 800 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 97 |  |  | 545 | 615 | 800 | 80 | 160 | 240 | 400 | 600 | 800 | 94 | 96.7 | 97.4 | 97.6 | 97.3 | 96.7 | 97.2 | 93.7 | 96.3 | 97.1 | 97.5 | 97.2 | 96.5 | 97.1 | 93.5 | 96.1 | 96.9 | 97.2 | 97 | 96.2 | 96.8 | Sungrow Power Supply800SG800MX
Sungrow Power Supply | SG1000MX | Y | N | N | 1000 kW, 3-phase, Utility Interactive Inverter with medium voltage NEMA NEMA TP1 transformer | 1000 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 17 |  |  | 570 | 630 | 800 | 100 | 200 | 300 | 500 | 750 | 1000 | 94.3 | 96.9 | 97.5 | 97.8 | 97.5 | 96.9 | 97.4 | 93.9 | 96.6 | 97.4 | 97.8 | 97.5 | 96.8 | 97.3 | 93.6 | 96.3 | 97.2 | 97.5 | 97.4 | 96.4 | 97.2 | Sungrow Power Supply1000SG1000MX
Sungrow Power Supply Co., Ltd. | SG 60KU-M [480V] | N | Y | Y | SG 60KU-M is 60kW, 480Vac transformerless Grid Support Utility Interactive Inverter. | 60 | 480 | 98.5 | [9/7/2017] | [DSP_SG60KU-M_V14_A] | 2018-10-15 | Y | N |  | 0.88 |  |  | 550 | 700 | 850 | 6 | 12 | 18 | 30 | 45 | 60 | 97.8 | 98.2 | 98.2 | 98.4 | 98.4 | 98 | 98.3 | 97.8 | 98.6 | 98.8 | 98.9 | 98.7 | 98.5 | 98.7 | 97.5 | 98.6 | 98.5 | 98.8 | 98.5 | 98.4 | 98.5 | SUNGROW Power Supply Co., Ltd60SG 60KU-M (480) [SI1] | 2017-11-15 | 2018-10-15
Sungrow Power Supply Co., Ltd. | SG125HV [600V] | Y | Y | Y | 125kW, 600Vac transformerless Grid Support Utility Interactive Inverter. | 125.178 | 600 | 98.5 | [7/7/2017] | [DSP_SG125KHV_V11_A LCD_SG125KHV_V03_A_M ] | 2018-10-15 | Y | N |  | 5.59 |  |  | 860 | 945 | 1200 | 12.5 | 25 | 37.5 | 62.5 | 93.75 | 125 | 98.5862 | 98.8265 | 98.8829 | 98.6821 | 98.4462 | 98.2555 | 98.5632 | 98.2896 | 98.5839 | 98.589 | 98.4937 | 98.3596 | 98.1057 | 98.411 | 98.0848 | 98.4261 | 98.4778 | 98.3839 | 98.0971 | 97.6269 | 98.1955 | Sungrow Power Supply Co., Ltd.125.178SG125HV [SI1] | 2017-11-01 | 2018-10-15
Sungrow Power Supply Co., Ltd. | SG2500U [550V] | Y | Y | Y | 2500kW, 550Vac Grid Support Utility Interactive Inverter connect to grid via a 2500kVA medium voltage transformer. | 2500 | 550 | 98 | [5/16/2017] | [DSP_SG2500U_V11_V1_A, LCD_SG2500U_V1_A_M] | 2018-10-15 | N | N | Weighted Efficiency includes efficiency of ABB ZGSB-H-2500/35. | 651.36 |  |  | 800 | 900 | 1200 | 250 | 500 | 750 | 1250 | 1875 | 2500 | 98 | 98.6 | 98.8 | 98.8 | 98.6 | 98.4 | 97.9 | 97.8 | 98.5 | 98.6 | 98.6 | 98.5 | 98.3 | 97.7 | 97.4 | 98.2 | 98.4 | 98.5 | 98.3 | 98.2 | 97.7 | Sungrow Power Supply Co., Ltd.2500 SG2500U [550V] [SI1] | 2018-02-01 | 2018-10-15
Sunna Tech | SUNNA 2000TL-US-240 [240V] | Y | N | N | 2110 W, 240 Vac Utility Interactive Inverter | 2.11 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.21 | 0.42 | 0.63 | 1.06 | 1.58 | 2.11 | 85.3 | 91.6 | 92.9 | 94.3 | 94.6 | 94.5 | 93.8 | 82.1 | 91.9 | 94.2 | 95.6 | 96.1 | 96.4 | 95 | 82.2 | 91.5 | 93.8 | 95.6 | 96.1 | 96.3 | 95 | Sunna Tech2.11SUNNA 2000TL-US-240 [240V]
Sunna Tech | SUNNA 3000TL-US-240 [240V] | Y | N | N | 3180 W, 240 Vac Utility Interactive Inverter | 3.18 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.32 | 0.64 | 0.95 | 1.59 | 2.39 | 3.18 | 88.8 | 92.9 | 94.1 | 94.6 | 94.3 | 94 | 94 | 88.8 | 94.4 | 95.3 | 96.2 | 96.3 | 95.9 | 95.7 | 89.5 | 93.7 | 95.3 | 96.2 | 96.3 | 96.1 | 95.7 | Sunna Tech3.18SUNNA 3000TL-US-240 [240V]
Sunna Tech | SUNNA 4200TL-US-240 [240V] | Y | N | N | 4100 W, 240 Vac Utility Interactive Inverter | 4.16 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.42 | 0.83 | 1.25 | 2.08 | 3.12 | 4.16 | 90.6 | 93.8 | 94.5 | 94.8 | 94.6 | 94.2 | 94.4 | 91.4 | 95 | 95.7 | 96.1 | 96.2 | 95.9 | 95.9 | 90.7 | 94.7 | 95.5 | 96.1 | 96.1 | 95.9 | 95.7 | Sunna Tech4.16SUNNA 4200TL-US-240 [240V]
Sunna Tech | SUNNA 5000TL-US-240 [240V] | Y | N | N | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8 | Sunna Tech5.24SUNNA 5000TL-US-240 [240V]
SunPower | SPR-225E-BLK-U-ACPV [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.225 | 0.03 | 30 | 43 | 50 | 0.02 | 0.05 | 0.07 | 0.11 | 0.2 | 0.2 | 86.6 | 91.6 | 93.3 | 94.6 | 94.7 | 94.5 | 94 | 85.9 | 91.3 | 93.2 | 94.9 | 95.3 | 95.3 | 94.4 | 87.3 | 90.7 | 93.3 | 95 | 95.5 | 95.4 | 94.5 | SunPower0.225SPR-225E-BLK-U-ACPV [240V]
SunPower | SPR-230NE-BLK-U-ACPV [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.225 | 0.03 | 30 | 43 | 50 | 0.02 | 0.05 | 0.07 | 0.11 | 0.2 | 0.2 | 86.6 | 91.6 | 93.3 | 94.6 | 94.7 | 94.5 | 94 | 85.9 | 91.3 | 93.2 | 94.9 | 95.3 | 95.3 | 94.4 | 87.3 | 90.7 | 93.3 | 95 | 95.5 | 95.4 | 94.5 | SunPower0.225SPR-230NE-BLK-U-ACPV [240V]
SunPower | SPR-240E-WHT-U-ACPV [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.225 | 0.03 | 30 | 43 | 50 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 86.6 | 91.6 | 93.3 | 94.6 | 94.7 | 94.5 | 94 | 85.9 | 91.3 | 93.2 | 94.9 | 95.3 | 95.3 | 94.4 | 87.3 | 90.7 | 93.3 | 95 | 95.5 | 95.4 | 94.5 | SunPower0.225SPR-240E-WHT-U-ACPV [240V]
SunPower | SPR-245NE-WHT-U-240 ACPV [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.225 | 0.03 | 30 | 43 | 50 | 0.02 | 0.05 | 0.07 | 0.11 | 0.2 | 0.2 | 86.6 | 91.6 | 93.3 | 94.6 | 94.7 | 94.5 | 94 | 85.9 | 91.3 | 93.2 | 94.9 | 95.3 | 95.3 | 94.4 | 87.3 | 90.7 | 93.3 | 95 | 95.5 | 95.4 | 94.5 | SunPower0.225SPR-245NE-WHT-U-240 ACPV [240V]
SunPower | SPR-245NE-WHT-U-ACPV [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.225 | 0.03 | 30 | 43 | 50 | 0.02 | 0.05 | 0.07 | 0.11 | 0.2 | 0.2 | 86.6 | 91.6 | 93.3 | 94.6 | 94.7 | 94.5 | 94 | 85.9 | 91.3 | 93.2 | 94.9 | 95.3 | 95.3 | 94.4 | 87.3 | 90.7 | 93.3 | 95 | 95.5 | 95.4 | 94.5 | SunPower0.225SPR-245NE-WHT-U-ACPV [240V]
SunPower | SPR-E20-245-A-AC [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.225 | 0.03 | 30 | 43 | 50 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 86.6 | 91.6 | 93.3 | 94.6 | 94.7 | 94.5 | 94 | 85.9 | 91.3 | 93.2 | 94.9 | 95.3 | 95.3 | 94.4 | 87.3 | 90.7 | 93.3 | 95 | 95.5 | 95.4 | 94.5 | SunPower0.225SPR-E20-245-A-AC [240V]
SunPower | SPR-X20-250-BLK-A-AC [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.225 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.225 | 0.03 | 30 | 43 | 50 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 86.6 | 91.6 | 93.3 | 94.6 | 94.7 | 94.5 | 94 | 85.9 | 91.3 | 93.2 | 94.9 | 95.3 | 95.3 | 94.4 | 87.3 | 90.7 | 93.3 | 95 | 95.5 | 95.4 | 94.5 | SunPower0.225SPR-X20-250-BLK-A-AC [240V]
SunPower | SPR-E20-245-B-AC [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | SunPower0.24SPR-E20-245-B-AC [208V]
SunPower | SPR-E20-245-B-AC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | SunPower0.24SPR-E20-245-B-AC [240V]
SunPower | SPR-X19-240-BLK-B-AC [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | SunPower0.24SPR-X19-240-BLK-B-AC [208V]
SunPower | SPR-X19-240-BLK-B-AC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | SunPower0.24SPR-X19-240-BLK-B-AC [240V]
SunPower | SPR-X20-250-BLK-B-AC [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | SunPower0.24SPR-X20-250-BLK-B-AC [208V]
SunPower | SPR-X20-250-BLK-B-AC [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.7 | 94.6 | 95.7 | 95 | 95 | 94.7 | 94.9 | 90 | 94.5 | 95.4 | 95.2 | 95.3 | 95.1 | 95 | 89.3 | 93.7 | 95.1 | 95 | 95.3 | 95.2 | 94.9 | SunPower0.24SPR-X20-250-BLK-B-AC [240V] |  | 2018-03-15
SunPower | MI-C-320-US208/240-1X [208V] | Y | Y | Y | 320 W, 208 Vac Grid Support Utility Interactive Microinverter | 0.32 | 208 | 95.5 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. Previously listed as MI-C-320-US208-1X | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | SunPower0.32MI-C-320-US208/240-1X [208V] | 2017-07-01 | 2018-10-15
SunPower | MI-C-320-US208/240-1X [240V] | Y | Y | Y | 320 W, 240 Vac Grid Support Utility Interactive Microinverter | 0.32 | 240 | 96 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. Previously listed as MI-C-320-US240-1X | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | SunPower0.32MI-C-320-US208/240-1X [240V] | 2017-07-01 | 2018-10-15
SunPower | MI-C-320-US208-xx [208V] | Y | N | N | 320 W, 208 Vac Utility Interactive Microinverter | 0.32 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.04 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.7 | 95.6 | 96.3 | 96.2 | 96 | 95.4 | 95.9 | 91.4 | 95.1 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 90.6 | 94.8 | 95.7 | 96.1 | 96 | 95.7 | 95.7 | SunPower0.32MI-C-320-US208-xx [208V]
SunPower | MI-C-320-US240-xx [240V] | Y | N | N | 320 W, 240 Vac Utility Interactive Microinverter | 0.32 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | SunPower0.32MI-C-320-US240-xx [240V]
SunPower | SPR-E19-320-C-AC [208V] | Y | N | N | 320 W, 208 Vac Inverter | 0.32 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | SunPower0.32SPR-E19-320-C-AC [208V]
SunPower | SPR-E19-320-C-AC [240V] | Y | N | N | 320 W, 240 Vac Inverter | 0.32 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | SunPower0.32SPR-E19-320-C-AC [240V]
SunPower | SPR-E19-320-D-AC [208V] | Y | Y | Y | 320 W, 208 Vac Grid Support Utility Interactive Microinverter for ACPV Module | 0.32 | 208 | 95.5 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | SunPower0.32SPR-E19-320-D-AC [208V] | 2017-09-01 | 2018-10-15
SunPower | SPR-E19-320-D-AC [240V] | Y | Y | Y | 320 W, 240 Vac Grid Support Utility Interactive Microinverter for ACPV Module | 0.32 | 240 | 96 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | SunPower0.32SPR-E19-320-D-AC [240V] | 2017-09-01 | 2018-10-15
SunPower | SPR-E20-327-C-AC [208V] | Y | N | N | 320 W, 208 Vac Inverter | 0.32 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | SunPower0.32SPR-E20-327-C-AC [208V]
SunPower | SPR-E20-327-C-AC [240V] | Y | N | N | 320 W, 240 Vac Inverter | 0.32 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | SunPower0.32SPR-E20-327-C-AC [240V]
SunPower | SPR-E20-327-D-AC [208V] | Y | Y | Y | 320 W, 208 Vac Grid Support Utility Interactive Microinverter for ACPV Module | 0.32 | 208 | 95.5 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | SunPower0.32SPR-E20-327-D-AC [208V] | 2017-09-01 | 2018-10-15
SunPower | SPR-E20-327-D-AC [240V] | Y | Y | Y | 320 W, 240 Vac Grid Support Utility Interactive Microinverter for ACPV Module | 0.32 | 240 | 96 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | SunPower0.32SPR-E20-327-D-AC [240V] | 2017-09-01 | 2018-10-15
SunPower | SPR-X20-327-BLK-C-AC [208V] | Y | N | N | 320 W, 208 Vac Inverter | 0.32 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | SunPower0.32SPR-X20-327-BLK-C-AC [208V]
SunPower | SPR-X20-327-BLK-C-AC [240V] | Y | N | N | 320 W, 240 Vac Inverter | 0.32 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | SunPower0.32SPR-X20-327-BLK-C-AC [240V]
SunPower | SPR-X20-327-BLK-D-AC [208V] | Y | Y | Y | 320 W, 208 Vac Grid Support Utility Interactive Microinverter for ACPV Module | 0.32 | 208 | 95.5 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | SunPower0.32SPR-X20-327-BLK-D-AC [208V] | 2017-09-01 | 2018-10-15
SunPower | SPR-X20-327-BLK-D-AC [240V] | Y | Y | Y | 320 W, 240 Vac Grid Support Utility Interactive Microinverter for ACPV Module | 0.32 | 240 | 96 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | SunPower0.32SPR-X20-327-BLK-D-AC [240V] | 2017-09-01 | 2018-10-15
SunPower | SPR-X20-327-C-AC [208V] | Y | N | N | 320 W, 208 Vac Inverter | 0.32 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | SunPower0.32SPR-X20-327-C-AC [208V]
SunPower | SPR-X20-327-C-AC [240V] | Y | N | N | 320 W, 240 Vac Inverter | 0.32 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | SunPower0.32SPR-X20-327-C-AC [240V]
SunPower | SPR-X20-327-D-AC [208V] | Y | Y | Y | 320 W, 208 Vac Grid Support Utility Interactive Microinverter for ACPV Module | 0.32 | 208 | 95.5 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | SunPower0.32SPR-X20-327-D-AC [208V] | 2017-09-01 | 2018-10-15
SunPower | SPR-X20-327-D-AC [240V] | Y | Y | Y | 320 W, 240 Vac Grid Support Utility Interactive Microinverter for ACPV Module | 0.32 | 240 | 96 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | SunPower0.32SPR-X20-327-D-AC [240V] | 2017-09-01 | 2018-10-15
SunPower | SPR-X21-335-BLK-C-AC [208V] | Y | N | N | 320 W, 208 Vac Inverter | 0.32 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | SunPower0.32SPR-X21-335-BLK-C-AC [208V]
SunPower | SPR-X21-335-BLK-C-AC [240V] | Y | N | N | 320 W, 240 Vac Inverter | 0.32 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | SunPower0.32SPR-X21-335-BLK-C-AC [240V]
SunPower | SPR-X21-335-BLK-D-AC [208V] | Y | Y | Y | 320 W, 208 Vac Grid Support Utility Interactive Microinverter for ACPV Module | 0.32 | 208 | 95.5 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | SunPower0.32SPR-X21-335-BLK-D-AC [208V] | 2017-09-01 | 2018-10-15
SunPower | SPR-X21-335-BLK-D-AC [240V] | Y | Y | Y | 320 W, 240 Vac Grid Support Utility Interactive Microinverter for ACPV Module | 0.32 | 240 | 96 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | SunPower0.32SPR-X21-335-BLK-D-AC [240V] | 2017-09-01 | 2018-10-15
SunPower | SPR-X21-335-C-AC [208V] | Y | N | N | 320 W, 208 Vac Inverter | 0.32 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | SunPower0.32SPR-X21-335-C-AC [208V]
SunPower | SPR-X21-335-C-AC [240V] | Y | N | N | 320 W, 240 Vac Inverter | 0.32 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | SunPower0.32SPR-X21-335-C-AC [240V]
SunPower | SPR-X21-335-D-AC [208V] | Y | Y | Y | 320 W, 208 Vac Grid Support Utility Interactive Microinverter for ACPV Module | 0.32 | 208 | 95.5 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | SunPower0.32SPR-X21-335-D-AC [208V] | 2017-09-01 | 2018-10-15
SunPower | SPR-X21-335-D-AC [240V] | Y | Y | Y | 320 W, 240 Vac Grid Support Utility Interactive Microinverter for ACPV Module | 0.32 | 240 | 96 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | SunPower0.32SPR-X21-335-D-AC [240V] | 2017-09-01 | 2018-10-15
SunPower | SPR-X21-345-C-AC [208V] | Y | N | N | 320 W, 208 Vac Inverter | 0.32 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | SunPower0.32SPR-X21-345-C-AC [208V]
SunPower | SPR-X21-345-C-AC [240V] | Y | N | N | 320 W, 240 Vac Inverter | 0.32 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.07 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.9 | 95.8 | 96.5 | 96.4 | 96.3 | 95.8 | 96.1 | 92.9 | 95.7 | 96.5 | 96.5 | 96.4 | 96 | 96.2 | 91.7 | 95.4 | 96.2 | 96.5 | 96.5 | 96.2 | 96.2 | SunPower0.32SPR-X21-345-C-AC [240V]
SunPower | SPR-X21-345-D-AC [208V] | Y | Y | Y | 320 W, 208 Vac Grid Support Utility Interactive Microinverter for ACPV Module | 0.32 | 208 | 95.5 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | SunPower0.32SPR-X21-345-D-AC [208V] | 2017-09-01 | 2018-10-15
SunPower | SPR-X21-345-D-AC [240V] | Y | Y | Y | 320 W, 240 Vac Grid Support Utility Interactive Microinverter for ACPV Module | 0.32 | 240 | 96 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | SunPower0.32SPR-X21-345-D-AC [240V] | 2017-09-01 | 2018-10-15
SunPower | SPR-X21-350-BLK-D-AC [208V] | Y | Y | Y | 350 W DC, 208 Vac Grid Support Utility Interactive ACPV Module with SunPower MI-C-320-US208-1X Microinverter | 0.32 | 208 | 95.5 | [10/3/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | SunPower0.32SPR-X21-350-BLK-D-AC (208V) [SI1] | 2018-01-16 | 2018-10-15
SunPower | SPR-X21-350-BLK-D-AC [240V] | Y | Y | Y | 350 W DC, 240 Vac Grid Support Utility Interactive ACPV Module with SunPower MI-C-320-US240-1X Microinverter | 0.32 | 240 | 96 | [10/3/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | SunPower0.32SPR-X21-350-BLK-D-AC (240V) [SI1] | 2018-01-16 | 2018-10-15
SunPower | SPR-X22-360-C-AC [208V] | Y | N | N | 320 W, 208 Vac Inverter | 0.32 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.7 | 95.6 | 96.3 | 96.2 | 96 | 95.4 | 95.9 | 91.4 | 95.1 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 90.6 | 94.8 | 95.7 | 96.1 | 96 | 95.7 | 95.7 | SunPower0.32SPR-X22-360-C-AC [208V]
SunPower | SPR-X22-360-C-AC [240V] | Y | N | N | 320 W, 240 Vac Inverter | 0.32 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 92.7 | 95.6 | 96.3 | 96.2 | 96 | 95.4 | 95.9 | 91.4 | 95.1 | 95.9 | 96.1 | 95.9 | 95.5 | 95.7 | 90.6 | 94.8 | 95.7 | 96.1 | 96 | 95.7 | 95.7 | SunPower0.32SPR-X22-360-C-AC [240V]
SunPower | SPR-X22-360-D-AC [208V] | Y | Y | Y | 320 W, 208 Vac Grid Support Utility Interactive Microinverter for ACPV Module | 0.32 | 208 | 95.5 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | SunPower0.32SPR-X22-360-D-AC [208V] | 2017-09-01 | 2018-10-15
SunPower | SPR-X22-360-D-AC [240V] | Y | Y | Y | 320 W, 240 Vac Grid Support Utility Interactive Microinverter for ACPV Module | 0.32 | 240 | 96 | [7/11/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | SunPower0.32SPR-X22-360-D-AC [240V] | 2017-09-01 | 2018-10-15
SunPower | SPR-X22-370-D-AC [208V] | Y | Y | Y | 370 W DC, 208 Vac Grid Support Utility Interactive ACPV Module with SunPower MI-C-320-US208-1X Microinverter | 0.32 | 208 | 95.5 | [10/3/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 90.8 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 90.2 | 94.5 | 95.5 | 96.2 | 96.1 | 95.9 | 95.7 | 89.4 | 94.1 | 95.3 | 96.2 | 96.2 | 95.9 | 95.7 | SunPower0.32SPR-X22-370-D-AC (208V) [SI1] | 2018-01-16 | 2018-10-15
SunPower | SPR-X22-370-D-AC [240V] | Y | Y | Y | 370 W DC, 240 Vac Grid Support Utility Interactive ACPV Module with SunPower MI-C-320-US240-1X Microinverter | 0.32 | 240 | 96 | [10/3/2017] | [15732] | 2018-10-15 | Y | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.1 |  |  | 53 | 60 | 64 | 0.03 | 0.06 | 0.1 | 0.16 | 0.24 | 0.32 | 89.7 | 94.1 | 95.3 | 96.2 | 96.1 | 95.9 | 95.7 | 90 | 94.3 | 95.4 | 96.3 | 96.3 | 96.2 | 95.8 | 89.6 | 94 | 95.2 | 96.3 | 96.4 | 96.2 | 95.8 | SunPower0.32SPR-X22-370-D-AC (240V) [SI1] | 2018-01-16 | 2018-10-15
SunPower | SPR-2500 [240V] | Y | N | N | 2500 W, 240 Vac Utility Interactive Inverter | 2.5 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.9 |  |  | 100 | 218 | 400 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 87.1 | 93.3 | 94.9 | 95.8 | 95.8 | 95.6 | 95.2 | 85.2 | 92.4 | 93.8 | 95.2 | 95.4 | 95.1 | 94.6 | 80.4 | 90 | 91.7 | 93.7 | 94.5 | 93.8 | 93.2 | SunPower2.5SPR-2500 [240V]
SunPower | SPR-2500x [240V] | Y | N | N | 2.5 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 2.5 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 2.5 | 1 | 100 | 266 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 88.5 | 92.7 | 94.1 | 94.8 | 94.8 | 94.5 | 94.4 | 87.7 | 92.3 | 93.7 | 94.5 | 94.6 | 94.4 | 94.1 | 86.3 | 90.9 | 92.6 | 93.8 | 94 | 93.8 | 93.3 | SunPower2.5SPR-2500x [240V]
SunPower | SPR-2800x [208V] | Y | N | N | 2.7 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 2.7 | 208 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 2.7 | 1 | 100 | 266 | 480 | 0.27 | 0.54 | 0.81 | 1.35 | 2.025 | 2.7 | 88.7 | 93.1 | 94.1 | 94.6 | 94.5 | 94 | 94.1 | 88 | 92.8 | 93.8 | 94.4 | 94.3 | 93.8 | 93.9 | 84.6 | 90.6 | 92.3 | 93.4 | 93.4 | 92.5 | 92.7 | SunPower2.7SPR-2800x [208V]
SunPower | SPR-2800x [240V] | Y | N | N | 2.8 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 2.8 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.3 | 2.8 | 1.3 | 100 | 266 | 480 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.3 | 93.5 | 94.4 | 95 | 94.8 | 94.4 | 94.5 | 88.6 | 93.1 | 94.2 | 94.7 | 94.6 | 94.2 | 94.3 | 85.3 | 91 | 92.7 | 93.8 | 93.7 | 92.7 | 93.1 | SunPower2.8SPR-2800x [240V]
SunPower | SPR-3000m [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter with display | 3 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.08 |  |  | 100 | 250 | 400 | 0.2 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 94 | 95.8 | 96 | 95.8 | 95.1 | 94.3 | 95.3 | 93.1 | 95.9 | 95.7 | 95.6 | 94.9 | 94 | 95.1 | 91.6 | 94.8 | 95.2 | 94.7 | 94.2 | 93.5 | 94.3 | SunPower3SPR-3000m [208V]
SunPower | SPR-3000m [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter with display | 3 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.07 |  |  | 100 | 250 | 400 | 0.2 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 93.4 | 95.9 | 96.3 | 96.5 | 96.1 | 95.6 | 96 | 92.5 | 95.8 | 96 | 96.1 | 95.8 | 95.1 | 95.7 | 90.5 | 94.6 | 95.4 | 95.3 | 95.2 | 94.6 | 95 | SunPower3SPR-3000m [240V]
SunPower | SPR-3300x [208V] | Y | N | N | 3.1 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.1 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.24 | 3.1 | 1.24 | 100 | 250 | 400 | 0.31 | 0.62 | 0.93 | 1.55 | 2.325 | 3.1 | 91.4 | 94.7 | 95.4 | 95.6 | 95.5 | 95.1 | 95.3 | 90.9 | 94.4 | 95.2 | 95.6 | 95.4 | 95.1 | 95.2 | 89.3 | 93.4 | 94.5 | 95.2 | 95.2 | 94.9 | 94.7 | SunPower3.1SPR-3300x [208V]
SunPower | SPR-3300f [208V] | Y | N | N | 3300 W, 208 Vac Utility Interactive Inverter | 3.3 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.62 |  |  | 100 | 366 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 92 | 94.5 | 95.1 | 95.2 | 94.8 | 93.8 | 94.7 | 92 | 94.9 | 95.3 | 95.8 | 95.8 | 95.3 | 95.5 | 91.7 | 94.3 | 94.4 | 95.3 | 95.3 | 95.1 | 95 | SunPower3.3SPR-3300f [208V]
SunPower | SPR-3300f [240V] | Y | N | N | 3300 W, 240 Vac Utility Interactive Inverter | 3.3 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.83 |  |  | 100 | 390 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 91 | 94.5 | 95.3 | 95.6 | 95.5 | 94.8 | 95.3 | 91.9 | 95.1 | 95.3 | 96 | 96.1 | 95.9 | 95.8 | 91.4 | 94.7 | 94.9 | 95.6 | 95.7 | 95.6 | 95.3 | SunPower3.3SPR-3300f [240V]
SunPower | SPR-3300f [277V] | Y | N | N | 3300 W, 277 Vac Utility Interactive Inverter | 3.3 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 |  |  | 100 | 330 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 90.7 | 94.4 | 95.3 | 95.9 | 95.9 | 95.5 | 95.5 | 91 | 94.9 | 95.4 | 96.1 | 96.2 | 96.1 | 95.8 | 90.9 | 94.8 | 95.3 | 95.8 | 96 | 96.1 | 95.6 | SunPower3.3SPR-3300f [277V]
SunPower | SPR-3300x [240V] | Y | N | N | 3.3 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 3.3 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.52 | 3.3 | 1.52 | 100 | 250 | 400 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 91.9 | 95 | 95.7 | 95.9 | 95.9 | 95.5 | 95.6 | 91.4 | 94.7 | 95.5 | 95.9 | 95.7 | 95.4 | 95.5 | 89.8 | 93.6 | 94.8 | 95.4 | 95.3 | 95.2 | 95 | SunPower3.3SPR-3300x [240V]
SunPower | SPR-3301f [208V] | Y | N | N | 3300 W, 208 Vac Utility Interactive Inverter | 3.3 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.53 | 3.3 | 0.53 | 100 | 366 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 92.9 | 94.67 | 95.24 | 95.4 | 95.13 | 94.37 | 95.05 | 93.04 | 95.01 | 95.5 | 95.98 | 95.85 | 95.37 | 95.66 | 92.51 | 93.92 | 94.7 | 95.44 | 95.49 | 95.23 | 95.17 | SunPower3.3SPR-3301f [208V]
SunPower | SPR-3301f [240V] | Y | N | N | 3300 W, 240 Vac Utility Interactive Inverter | 3.3 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.7 | 3.3 | 0.7 | 100 | 390 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 92.11 | 94.81 | 95.53 | 95.93 | 95.77 | 95.28 | 95.55 | 93.02 | 95.3 | 95.52 | 96.23 | 96.3 | 96.07 | 96 | 92.63 | 94.64 | 94.83 | 95.73 | 95.97 | 95.91 | 95.58 | SunPower3.3SPR-3301f [240V]
SunPower | SPR-3301f [277V] | Y | N | N | 3300 W, 277 Vac Utility Interactive Inverter | 3.3 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.94 | 3.3 | 0.94 | 100 | 330 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 91.26 | 94.76 | 95.6 | 96.2 | 96.24 | 95.93 | 95.87 | 91.44 | 95.25 | 95.55 | 96.39 | 96.49 | 96.34 | 96.09 | 92.25 | 94.89 | 95.24 | 95.96 | 96.29 | 96.37 | 95.87 | SunPower3.3SPR-3301f [277V]
SunPower | SPR-3500 [240V] | Y | N | N | 3500 W, 240 Vac Utility Interactive Inverter | 3.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.9 |  |  | 100 | 263 | 400 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 87.2 | 93.1 | 95.4 | 96.5 | 96.7 | 96.6 | 95.9 | 85.7 | 92.2 | 94.9 | 96.2 | 96.4 | 96.3 | 95.5 | 82.1 | 90.2 | 93.6 | 95.4 | 95.7 | 95.6 | 94.5 | SunPower3.5SPR-3500 [240V]
SunPower | SPR-4000m [208V] | Y | N | N | 4 kW, 208 Vac Utility Interactive Inverter with display | 3.5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.14 |  |  | 100 | 310 | 480 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 94.3 | 96.3 | 96.5 | 96.4 | 95.8 | 94.9 | 95.9 | 93.5 | 96.2 | 96.1 | 96.1 | 95.5 | 94.8 | 95.6 | 91.5 | 94.9 | 95.4 | 95.1 | 94.8 | 94 | 94.7 | SunPower3.5SPR-4000m [208V]
SunPower | SPR-3801f [208V] | Y | N | N | 3800 W, 208 Vac Utility Interactive Inverter | 3.8 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.53 | 3.8 | 0.53 | 100 | 366 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.98 | 94.93 | 95.38 | 95.33 | 94.78 | 93.76 | 94.85 | 93.52 | 95.04 | 95.62 | 95.96 | 95.65 | 95.02 | 95.56 | 92.96 | 93.88 | 94.78 | 95.48 | 95.41 | 94.93 | 95.15 | SunPower3.8SPR-3801f [208V]
SunPower | SPR-3801f [240V] | Y | N | N | 3800 W, 240 Vac Utility Interactive Inverter | 3.8 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.7 | 3.8 | 0.7 | 100 | 390 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.7 | 95.04 | 95.67 | 95.88 | 95.57 | 94.87 | 95.47 | 93.31 | 95.3 | 95.74 | 96.28 | 96.2 | 95.81 | 95.98 | 93.05 | 94.61 | 95.08 | 95.85 | 95.93 | 95.71 | 95.62 | SunPower3.8SPR-3801f [240V]
SunPower | SPR-3801f [277V] | Y | N | N | 3800 W, 277 Vac Utility Interactive Inverter | 3.8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.94 | 3.8 | 0.94 | 100 | 330 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.08 | 95.02 | 95.77 | 96.22 | 96.12 | 95.68 | 95.86 | 92.56 | 95.38 | 95.82 | 96.46 | 96.42 | 96.14 | 96.14 | 92.98 | 95.16 | 95.31 | 96.1 | 96.35 | 96.27 | 95.97 | SunPower3.8SPR-3801f [277V]
SunPower | SPR-4000f [208V] | Y | N | N | 4000 W, 208 Vac Utility Interactive Inverter | 3.8 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.62 |  |  | 100 | 366 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93 | 94.9 | 95.3 | 95.1 | 94.4 | 93 | 94.6 | 93.6 | 95.1 | 95.7 | 95.9 | 95.6 | 94.9 | 95.6 | 92.7 | 94.4 | 95 | 95.4 | 95.2 | 94.7 | 95 | SunPower3.8SPR-4000f [208V]
SunPower | SPR-4000x [208V] | Y | N | N | 3.8 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.8 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.99 | 3.8 | 0.99 | 100 | 300 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.7 | 94.8 | 95.5 | 95.7 | 95.4 | 95.1 | 95.3 | 91 | 94.6 | 95.3 | 95.6 | 95.4 | 94.9 | 95.2 | 90.2 | 93.6 | 94.7 | 95.1 | 95.1 | 94.7 | 94.7 | SunPower3.8SPR-4000x [208V]
SunPower | SPR-4000f [240V] | Y | N | N | 4000 W, 240 Vac Utility Interactive Inverter | 4 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.83 |  |  | 100 | 390 | 480 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 92.3 | 94.9 | 95.5 | 95.6 | 95.1 | 94.1 | 95.1 | 93 | 95.2 | 95.7 | 96.1 | 96 | 95.6 | 95.8 | 92.9 | 94.9 | 95.2 | 95.6 | 95.7 | 95.4 | 95.4 | SunPower4SPR-4000f [240V]
SunPower | SPR-4000f [277V] | Y | N | N | 4000 W, 277 Vac Utility Interactive Inverter | 4 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 |  |  | 100 | 330 | 480 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 92.1 | 94.9 | 95.6 | 95.9 | 95.7 | 94.9 | 95.5 | 92 | 95.2 | 95.7 | 96.2 | 96.2 | 95.8 | 95.9 | 92.6 | 95.1 | 95.3 | 95.9 | 96.1 | 96 | 95.7 | SunPower4SPR-4000f [277V]
SunPower | SPR-4000m [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter with display | 4 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.17 |  |  | 100 | 310 | 480 | 0.25 | 0.8 | 1.2 | 2 | 3 | 4 | 92.5 | 96.4 | 96.8 | 96.7 | 96.4 | 96 | 96.3 | 91.9 | 96.2 | 96.3 | 96.5 | 96 | 95.5 | 96 | 89.1 | 94.7 | 95.6 | 95.5 | 95.3 | 94.9 | 95.1 | SunPower4SPR-4000m [240V]
SunPower | SPR-4000x [240V] | Y | N | N | 4.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 4 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 | 4 | 1.1 | 100 | 300 | 480 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 92.2 | 95.1 | 95.8 | 96 | 95.8 | 95.5 | 95.7 | 91.6 | 94.9 | 95.7 | 95.9 | 95.8 | 95.3 | 95.5 | 90.7 | 94.2 | 95 | 95.5 | 95.4 | 95.1 | 95.1 | SunPower4SPR-4000x [240V]
SunPower | SPR-5000x [208V] | Y | N | N | 4.5 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 4.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 4.5 | 1 | 100 | 300 | 480 | 0.45 | 0.9 | 1.35 | 2.25 | 3.375 | 4.5 | 92.1 | 94.9 | 95.5 | 95.5 | 94.9 | 94.3 | 95 | 91.8 | 94.7 | 95.3 | 95.4 | 94.9 | 94.3 | 94.9 | 90.5 | 93.9 | 94.6 | 95 | 94.7 | 94.2 | 94.5 | SunPower4.5SPR-5000x [208V]
SunPower | SPR-4600 [208V] | Y | N | N | 4600 W, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 | 4.6 | 4 | 100 | 254 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 90.3 | 94.8 | 95.9 | 96.5 | 96.5 | 96.2 | 96.1 | 89.2 | 94.3 | 95.6 | 96.3 | 96.4 | 96.1 | 95.9 | 86.5 | 92.9 | 94.7 | 95.6 | 95.7 | 95.4 | 95 | SunPower4.6SPR-4600 [208V]
SunPower | SPR-5000m [208V] | Y | N | N | 5 kW, 208 Vac Utility Interactive Inverter with display | 5 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.7 | 96.2 | 96.7 | 96.7 | 96.3 | 96.4 | 89.9 | 95 | 95.7 | 96.2 | 96.4 | 96 | 95.9 | 86.3 | 92.5 | 94.3 | 95 | 95.1 | 95 | 94.5 | SunPower5SPR-5000m [208V]
SunPower | SPR-5000m [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter with display | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91 | 95.7 | 96.2 | 96.8 | 96.8 | 96.5 | 96.4 | 89.7 | 94.9 | 95.7 | 96.2 | 96.4 | 96.2 | 95.9 | 86.2 | 92.5 | 94.3 | 95.2 | 95.2 | 95.1 | 94.6 | SunPower5SPR-5000m [240V]
SunPower | SPR-5000m [277V] | Y | N | N | 5 kW, 277 Vac Utility Interactive Inverter with display | 5 | 277 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 91.5 | 95.8 | 96.5 | 96.8 | 96.5 | 96.6 | 96.3 | 90 | 95 | 95.8 | 96.2 | 96.5 | 96.2 | 96 | 86.3 | 92.3 | 94.4 | 95.2 | 95.2 | 95.2 | 94.6 | SunPower5SPR-5000m [277V]
SunPower | SPR-5000x [240V] | Y | N | N | 5.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 5 | 1 | 100 | 300 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.2 | 95.5 | 95.9 | 95.9 | 95.5 | 94.8 | 95.5 | 92.7 | 95.3 | 95.8 | 95.8 | 95.4 | 94.8 | 95.4 | 91.5 | 94.6 | 95.3 | 95.4 | 95.1 | 94.5 | 95 | SunPower5SPR-5000x [240V]
SunPower | SPR-5200 [240V] | Y | N | N | 5200 W, 240 Vac Utility Interactive Inverter | 5.2 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 4 | 5.2 | 4 | 100 | 280 | 400 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 89.4 | 94.8 | 96 | 96.8 | 97 | 96.8 | 96.4 | 88.6 | 94.4 | 95.7 | 96.7 | 96.8 | 96.6 | 96.2 | 87.7 | 93.1 | 94.8 | 96.1 | 96.3 | 96.1 | 95.5 | SunPower5.2SPR-5200 [240V]
SunPower | SPR-6000m [208V] | Y | N | N | 6 kW, 208 Vac Utility Interactive Inverter with display | 6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.5 | 95.8 | 96.5 | 96.9 | 96.5 | 95.9 | 96.3 | 91.2 | 95.6 | 95.9 | 96.3 | 96.1 | 95.6 | 95.9 | 88 | 93.5 | 94.8 | 94.6 | 94.9 | 94.6 | 94.5 | SunPower6SPR-6000m [208V]
SunPower | SPR-6000m [240V] | Y | N | N | 6 kW, 240 Vac Utility Interactive Inverter with display | 6 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.6 | 96.1 | 96.5 | 96.8 | 96.7 | 96 | 96.4 | 91.3 | 95.6 | 96 | 96.3 | 96.3 | 95.9 | 96 | 87.9 | 93.6 | 94.8 | 95.1 | 95 | 94.8 | 94.7 | SunPower6SPR-6000m [240V]
SunPower | SPR-6000m [277V] | Y | N | N | 6 kW, 277 Vac Utility Interactive Inverter with display | 6 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.6 | 1.2 | 1.8 | 3 | 4.5 | 6 | 92.3 | 96 | 96.7 | 97 | 96.7 | 96.5 | 96.5 | 91.3 | 95.6 | 96.2 | 96.4 | 96.4 | 96 | 96.1 | 87.8 | 93.6 | 94.9 | 95.2 | 95.1 | 94.9 | 94.7 | SunPower6SPR-6000m [277V]
SunPower | SPR-6500f [208V] | Y | N | N | 6500 W, 208 Vac Utility Interactive Inverter | 6.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.71 |  |  | 100 | 366 | 480 | 0.65 | 1.3 | 1.95 | 3.25 | 4.88 | 6.5 | 92.8 | 94.7 | 94.6 | 95.2 | 94.7 | 93.7 | 94.6 | 93 | 94.9 | 95.2 | 95.7 | 95.6 | 95.2 | 95.4 | 91.8 | 93.8 | 94.6 | 94.9 | 95 | 94.9 | 94.7 | SunPower6.5SPR-6500f [208V]
SunPower | SPR-6500f [240V] | Y | N | N | 6500 W, 240 Vac Utility Interactive Inverter | 6.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.76 |  |  | 100 | 390 | 480 | 0.65 | 1.3 | 1.95 | 3.25 | 4.88 | 6.5 | 92.7 | 95 | 95.1 | 95.6 | 95.4 | 94.8 | 95.3 | 93 | 94.9 | 95.5 | 95.8 | 96 | 95.8 | 95.7 | 91.8 | 94.1 | 94.8 | 95.2 | 95.5 | 95.4 | 95.1 | SunPower6.5SPR-6500f [240V]
SunPower | SPR-6500f [277V] | Y | N | N | 6500 W, 277 Vac Utility Interactive Inverter | 6.5 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.02 |  |  | 100 | 330 | 480 | 0.65 | 1.3 | 1.95 | 3.25 | 4.88 | 6.5 | 93.5 | 95.4 | 95.7 | 96 | 96 | 95.5 | 95.8 | 93.9 | 95.5 | 96 | 96.2 | 96.3 | 96.2 | 96.1 | 93.8 | 95 | 95.6 | 95.8 | 96.1 | 96.1 | 95.8 | SunPower6.5SPR-6500f [277V]
SunPower | SPR-6501f [208V] | Y | N | N | 6500 W, 208 Vac Utility Interactive Inverter | 6.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.6 | 6.5 | 0.6 | 100 | 366 | 480 | 0.65 | 1.3 | 1.95 | 3.25 | 4.875 | 6.5 | 93.55 | 95.01 | 94.97 | 95.27 | 94.94 | 94.12 | 94.92 | 93.97 | 95.36 | 95.54 | 95.84 | 95.71 | 95.26 | 95.61 | 92.88 | 94.56 | 95.06 | 95.27 | 95.35 | 95.11 | 95.15 | SunPower6.5SPR-6501f [208V]
SunPower | SPR-6501f [240V] | Y | N | N | 6500 W, 240 Vac Utility Interactive Inverter | 6.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.8 | 6.5 | 0.8 | 100 | 390 | 480 | 0.65 | 1.3 | 1.95 | 3.25 | 4.875 | 6.5 | 93.66 | 95.4 | 95.56 | 95.81 | 95.62 | 95.09 | 95.53 | 94.19 | 95.48 | 95.86 | 96.09 | 96.16 | 95.91 | 95.98 | 93.3 | 94.9 | 95.53 | 95.56 | 95.81 | 95.74 | 95.57 | SunPower6.5SPR-6501f [240V]
SunPower | SPR-6501f [277V] | Y | N | N | 6500 W, 277 Vac Utility Interactive Inverter | 6.5 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 | 6.5 | 1.1 | 100 | 330 | 480 | 0.65 | 1.3 | 1.95 | 3.25 | 4.875 | 6.5 | 93.95 | 95.72 | 96.02 | 96.18 | 96.13 | 95.81 | 96 | 94.26 | 95.79 | 96.3 | 96.38 | 96.43 | 96.26 | 96.28 | 94.08 | 95.4 | 95.87 | 95.9 | 96.18 | 96.28 | 95.97 | SunPower6.5SPR-6501f [277V]
SunPower | SPR-7000m [208V] | Y | N | N | 7 kW, 208 Vac Utility Interactive Inverter with display | 7 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.46 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 94 | 96.3 | 97.1 | 96.7 | 96.2 | 95.4 | 96.3 | 92.7 | 96.1 | 96.1 | 96.2 | 95.9 | 95.3 | 95.9 | 89.7 | 94.2 | 95 | 94.9 | 94.8 | 94.1 | 94.6 | SunPower7SPR-7000m [208V]
SunPower | SPR-7000m [240V] | Y | N | N | 7 kW, 240 Vac Utility Interactive Inverter with display | 7 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.72 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.2 | 96.8 | 96.9 | 96.5 | 95.8 | 96.5 | 92.3 | 96.1 | 96.1 | 96.4 | 96.1 | 95.6 | 96 | 89.3 | 94.3 | 95.1 | 95.6 | 95 | 94.7 | 94.8 | SunPower7SPR-7000m [240V]
SunPower | SPR-7000m [277V] | Y | N | N | 7 kW, 277 Vac Utility Interactive Inverter with display | 7 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.41 |  |  | 100 | 310 | 480 | 0.7 | 1.4 | 2.1 | 3.5 | 5.25 | 7 | 93.7 | 96.3 | 96.8 | 97 | 96.5 | 95.9 | 96.5 | 92.5 | 96.1 | 96.3 | 96.5 | 96.2 | 95.6 | 96.1 | 89.3 | 94.2 | 95.2 | 95 | 95.1 | 94.6 | 94.8 | SunPower7SPR-7000m [277V]
SunPower | SPR-7501f [208V] | Y | N | N | 7500 W, 208 Vac Utility Interactive Inverter | 7.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.6 | 7.5 | 0.6 | 100 | 366 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.625 | 7.5 | 94.23 | 95.18 | 95 | 95.19 | 94.68 | 93.6 | 94.78 | 94.47 | 95.69 | 95.69 | 95.89 | 95.6 | 94.94 | 95.6 | 93.01 | 95.11 | 95.35 | 95.4 | 95.31 | 94.87 | 95.21 | SunPower7.5SPR-7501f [208V]
SunPower | SPR-7501f [240V] | Y | N | N | 7500 W, 240 Vac Utility Interactive Inverter | 7.5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.8 | 7.5 | 0.8 | 100 | 390 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.625 | 7.5 | 94.37 | 95.6 | 95.61 | 95.78 | 95.46 | 94.73 | 95.47 | 94.49 | 95.9 | 96.06 | 96.22 | 96.16 | 95.73 | 96.06 | 93.98 | 95.29 | 95.68 | 95.83 | 95.86 | 95.61 | 95.71 | SunPower7.5SPR-7501f [240V]
SunPower | SPR-7501f [277V] | Y | N | N | 7500 W, 277 Vac Utility Interactive Inverter | 7.5 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 | 7.5 | 1.1 | 100 | 330 | 480 | 0.75 | 1.5 | 2.25 | 3.75 | 5.625 | 7.5 | 94.05 | 95.73 | 95.93 | 96.15 | 95.95 | 95.45 | 95.88 | 94.27 | 95.84 | 96.09 | 96.36 | 96.26 | 95.96 | 96.14 | 93.86 | 95.28 | 95.81 | 95.97 | 96.16 | 96.11 | 95.94 | SunPower7.5SPR-7501f [277V]
SunPower | SPR-8000f [208V] | Y | N | N | 7600 W 208 Vac Utility Interactive Inverter | 7.6 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.71 |  |  | 100 | 366 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 93.4 | 94.8 | 94.4 | 95 | 94.3 | 92.9 | 94.4 | 93.3 | 95.1 | 95.4 | 95.7 | 95.5 | 94.7 | 95.4 | 92.3 | 94.4 | 94.5 | 95.1 | 95 | 94.5 | 94.8 | SunPower7.6SPR-8000f [208V]
SunPower | SPR-8000m [240V] | Y | N | N | 8 kW, 240 Vac Sunny Boy Utility Interactive Inverter with display | 7.6 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.17 |  |  | 100 | 345 | 480 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95.04 | 96.48 | 96.84 | 96.82 | 96.5 | 96.01 | 96.53 | 94.59 | 96.19 | 96.61 | 96.63 | 96.3 | 96.29 | 96.33 | 93.13 | 95.28 | 95.83 | 95.98 | 95.72 | 95.94 | 95.67 | SunPower7.6SPR-8000m [240V]
SunPower | SPR-8000f [240V] | Y | N | N | 8000 W, 240 Vac Utility Interactive Inverter | 8 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.76 |  |  | 100 | 390 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 94 | 95.3 | 95.2 | 95.6 | 95.1 | 94 | 95.1 | 93.9 | 95.5 | 95.6 | 96 | 96 | 95.5 | 95.8 | 93.4 | 94.9 | 95.4 | 95.5 | 95.5 | 95.3 | 95.4 | SunPower8SPR-8000f [240V]
SunPower | SPR-8000f [277V] | Y | N | N | 8000 W, 277 Vac Utility Interactive Inverter | 8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.02 |  |  | 100 | 330 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 94.3 | 95.8 | 95.7 | 96.1 | 95.7 | 95 | 95.7 | 95 | 96 | 96.2 | 96.4 | 96.3 | 95.8 | 96.2 | 94.8 | 95.8 | 95.6 | 96.1 | 96.2 | 96 | 96 | SunPower8SPR-8000f [277V]
SunPower | SPR-8000m [277V] | Y | N | N | 8kW, 277 Vac Sunny Boy Utility Interactive Inverter with display | 8 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.15 |  |  | 100 | 345 | 480 | 0.8 | 1.6 | 2.4 | 4 | 6 | 8 | 95.12 | 96.22 | 96.48 | 96.46 | 96.17 | 95.56 | 96.2 | 94.85 | 95.86 | 96.28 | 96.25 | 95.89 | 95.28 | 95.93 | 93.45 | 95.01 | 95.41 | 95.51 | 95.24 | 94.7 | 95.21 | SunPower8SPR-8000m [277V]
SunPower | SPR-10001f [208V] | Y | N | N | 10000 W, 208 Vac Utility Interactive Inverter | 9.995 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.77 | 10 | 0.77 | 100 | 366 | 480 | 0.9995 | 1.999 | 2.999 | 4.998 | 7.496 | 9.995 | 93.96 | 94.59 | 95.13 | 95.15 | 94.79 | 93.95 | 94.82 | 93.94 | 95.27 | 95.61 | 95.79 | 95.64 | 95.11 | 95.55 | 92.8 | 94.78 | 94.89 | 95.27 | 95.3 | 95 | 95.1 | SunPower9.995SPR-10001f [208V]
SunPower | SPR-10001f [240V] | Y | N | N | 10000 W, 240 Vac Utility Interactive Inverter | 9.995 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 10 | 1 | 100 | 390 | 480 | 0.9995 | 1.999 | 2.999 | 4.998 | 7.496 | 9.995 | 94.18 | 95.24 | 95.61 | 95.7 | 95.51 | 94.94 | 95.47 | 93.77 | 95.61 | 95.8 | 96.04 | 96.12 | 95.86 | 95.93 | 93.16 | 95.13 | 95.2 | 95.55 | 95.79 | 95.7 | 95.52 | SunPower9.995SPR-10001f [240V]
SunPower | SPR-10001f [277V] | Y | N | N | 10000 W, 277 Vac Utility Interactive Inverter | 9.995 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.36 | 10 | 1.36 | 100 | 330 | 480 | 0.9995 | 1.999 | 2.999 | 4.998 | 7.496 | 9.995 | 94.28 | 95.67 | 95.87 | 96.05 | 95.98 | 95.59 | 95.88 | 94.07 | 95.87 | 96.02 | 96.23 | 96.3 | 96.08 | 96.13 | 93.68 | 95.46 | 95.44 | 95.8 | 96.12 | 96.16 | 95.84 | SunPower9.995SPR-10001f [277V]
SunPower | SPR-10000f [208V] | Y | N | N | 10000 W, 208 Vac Utility Interactive Inverter | 10 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.64 |  |  | 100 | 366 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 93.8 | 94.5 | 95.2 | 95.3 | 94.9 | 93.8 | 94.9 | 93.5 | 95.2 | 95.6 | 95.9 | 95.8 | 95.3 | 95.6 | 92.5 | 94.4 | 94.8 | 95.2 | 95.2 | 95 | 95 | SunPower10SPR-10000f [208V]
SunPower | SPR-10000f [240V] | Y | N | N | 10000 W, 240 Vac Utility Interactive Inverter | 10 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.85 |  |  | 100 | 390 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.1 | 95.1 | 95.7 | 95.8 | 95.5 | 94.9 | 95.5 | 93.7 | 95.5 | 95.9 | 96.2 | 96.2 | 96 | 96 | 93.2 | 95 | 95.3 | 95.6 | 95.7 | 95.6 | 95.5 | SunPower10SPR-10000f [240V]
SunPower | SPR-10000f [277V] | Y | N | N | 10000 W, 277 Vac Utility Interactive Inverter | 10 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.13 |  |  | 100 | 330 | 480 | 1 | 2 | 3 | 5 | 7.5 | 10 | 94.2 | 95.7 | 95.9 | 96.1 | 96 | 95.6 | 95.9 | 94.5 | 96 | 96.1 | 96.3 | 96.4 | 96.3 | 96.3 | 94.5 | 95.6 | 95.7 | 96 | 96.1 | 96.2 | 96 | SunPower10SPR-10000f [277V]
SunPower | SPR 11401f [208V] | Y | N | N | 11400 W, 208 Vac, 3-phase Utility Interactive Inverter | 11.4 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.77 | 11.4 | 0.77 | 230 | 366 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.38 | 94.56 | 95.11 | 95.08 | 94.48 | 93.34 | 94.63 | 94.57 | 95.31 | 95.74 | 95.78 | 95.43 | 94.8 | 95.47 | 93.33 | 94.99 | 95.17 | 95.33 | 95.22 | 94.66 | 95.12 | SunPower11.4SPR 11401f [208V]
SunPower | SPR 11401f [240V] | Y | N | N | 11400 W, 240 Vac, 3-phase Utility Interactive Inverter | 11.4 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 11.4 | 1 | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.59 | 95.19 | 95.62 | 95.67 | 95.28 | 94.5 | 95.33 | 94.33 | 95.72 | 95.9 | 96.12 | 96.01 | 95.61 | 95.92 | 93.56 | 95.36 | 95.49 | 95.7 | 95.77 | 95.51 | 95.6 | SunPower11.4SPR 11401f [240V]
SunPower | SPR 11401f [277V] | Y | N | N | 12000 W, 240 Vac, 3-phase Utility Interactive Inverter | 11.4 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.36 | 11.4 | 1.36 | 240 | 330 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.66 | 95.65 | 95.94 | 96.03 | 95.84 | 95.31 | 95.81 | 94.49 | 95.89 | 96.13 | 96.27 | 96.21 | 95.88 | 96.11 | 93.86 | 95.69 | 95.65 | 95.97 | 96.14 | 96.05 | 95.93 | SunPower11.4SPR 11401f [277V]
SunPower | SPR-11400f-3 [208V] | Y | N | N | 11400 W, 208 Vac, 3-phase Utility Interactive Inverter | 11.4 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 230 | 365 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.2 | 94.3 | 95.1 | 95.1 | 94.4 | 93 | 94.55 | 94.4 | 95.3 | 95.8 | 95.9 | 95.6 | 94.9 | 95.59 | 93.4 | 94.6 | 95 | 95.3 | 95.2 | 94.7 | 95.05 | SunPower11.4SPR-11400f-3 [208V]
SunPower | SPR-11400f-3 [240V] | Y | N | N | 11400 W, 240 Vac, 3-phase Utility Interactive Inverter | 11.4 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.3 | 95 | 95.6 | 95.7 | 95.2 | 94.2 | 95.25 | 94.1 | 95.7 | 96 | 96.2 | 96.1 | 95.7 | 95.99 | 93.4 | 95.1 | 95.4 | 95.7 | 95.7 | 95.6 | 95.54 | SunPower11.4SPR-11400f-3 [240V]
SunPower | SPR-11401f-3 Delta [208V] | Y | N | N | 11400 W, 208 Vac, 3-phase Utility Interactive Inverter | 11.4 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 | 11.4 | 0.9 | 230 | 366 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.57 | 94.79 | 95.21 | 95.21 | 94.63 | 93.51 | 94.77 | 94.66 | 95.45 | 95.78 | 95.89 | 95.55 | 94.88 | 95.57 | 93.71 | 94.96 | 95.25 | 95.43 | 95.29 | 94.8 | 95.21 | SunPower11.4SPR-11401f-3 Delta [208V]
SunPower | SPR-11401f-3 Delta [240V] | Y | N | N | 11400 W, 240 Vac, 3-phase Utility Interactive Inverter | 11.4 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.2 | 11.4 | 1.2 | 230 | 390 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.67 | 95.44 | 95.75 | 95.82 | 95.47 | 94.68 | 95.5 | 94.49 | 95.79 | 96.03 | 96.25 | 96.15 | 95.75 | 96.05 | 94.01 | 95.42 | 95.54 | 95.83 | 95.87 | 95.65 | 95.71 | SunPower11.4SPR-11401f-3 Delta [240V]
SunPower | SPR-12000f [208V] | Y | N | N | 11400 W, 208 Vac, 3-phase Utility Interactive Inverter | 11.4 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.9 |  |  | 230 | 365 | 480 | 1.14 | 2.28 | 3.42 | 5.7 | 8.55 | 11.4 | 94.2 | 94.3 | 95.1 | 95.1 | 94.4 | 93 | 94.55 | 94.4 | 95.3 | 95.8 | 95.9 | 95.6 | 94.9 | 95.59 | 93.4 | 94.6 | 95 | 95.3 | 95.2 | 94.7 | 95.05 | SunPower11.4SPR-12000f [208V]
SunPower | SPR-12000f [240V] | Y | N | N | 12000 W, 240 Vac, 3-Phase Utility Interactive Inverter | 12 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 230 | 390 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 94.4 | 94.8 | 95.5 | 95.7 | 95.1 | 94 | 95.17 | 94.2 | 95.5 | 95.9 | 96.2 | 96 | 95.5 | 95.93 | 93.4 | 95.1 | 95.4 | 95.6 | 95.7 | 95.4 | 95.49 | SunPower12SPR-12000f [240V]
SunPower | SPR-12000f-3 [277V] | Y | N | N | 12000 W, 277 Vac, 3-phase Utility Interactive Inverter | 12 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 |  |  | 240 | 330 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 94.7 | 95.5 | 95.9 | 96 | 95.8 | 95.1 | 95.8 | 94.7 | 95.9 | 96.1 | 96.3 | 96.3 | 95.8 | 96.2 | 94.3 | 95.7 | 95.8 | 96 | 96.2 | 96 | 96 | SunPower12SPR-12000f-3 [277V]
SunPower | SPR-12000m-3 [480V] | Y | Y | Y | Sunny Tripower TL-US 12 kW, 480 Vac 3-phase, Grid Support Utility Interactive Inverter | 12 | 480 | 97.5 | [7/13/2017] | [2.03.04.R] | 2018-10-15 | Y | N | Multiple Listing of SMA America | 1.79 |  |  | 300 | 675 | 800 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.8947 | 95.8254 | 96.4946 | 96.6907 | 96.6273 | 96.507 | 96.4293 | 94.8857 | 96.883 | 97.4944 | 97.777 | 97.8321 | 97.8114 | 97.6137 | 94.1548 | 97.204 | 97.7008 | 98.014 | 98.1838 | 98.1898 | 97.8803 | SunPower12SPR-12000m-3 [480V] | 2017-09-01 | 2018-10-15
SunPower | SPR-12000m-3-H [480V] | Y | Y | Y | Sunny Tripower TL-US 12 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter | 12 | 480 | 97.5 | [7/13/2017] | [2.03.04.R] | 2018-10-15 | Y | N | Multiple Listing of SMA America | 1.79 |  |  | 300 | 675 | 800 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.8947 | 95.8254 | 96.4946 | 96.6907 | 96.6273 | 96.507 | 96.4293 | 94.8857 | 96.883 | 97.4944 | 97.777 | 97.8321 | 97.8114 | 97.6137 | 94.1548 | 97.204 | 97.7008 | 98.014 | 98.1838 | 98.1898 | 97.8803 | SunPower12SPR-12000m-3-H [480V] | 2017-09-01 | 2018-10-15
SunPower | SPR-12001f-3 WYE [277V] | Y | N | N | 12000 W, 277 Vac, 3-phase Utility Interactive Inverter | 12 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 | 12 | 0.5 | 240 | 330 | 480 | 1.2 | 2.4 | 3.6 | 6 | 9 | 12 | 92.62 | 95.2 | 96.16 | 96.32 | 96.05 | 95.44 | 95.91 | 92.45 | 95.69 | 96.17 | 96.56 | 96.45 | 96.06 | 96.22 | 94.43 | 95.61 | 95.78 | 96.24 | 96.43 | 96.29 | 96.19 | SunPower12SPR-12001f-3 WYE [277V]
SunPower | SPR-15000m-3 [480V] | Y | Y | Y | Sunny Tripower TL-US 15 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter | 15 | 480 | 97.5 | [7/13/2017] | [2.03.04.R] | 2018-10-15 | Y | N | Multiple Listing of SMA America | 1.79 |  |  | 300 | 675 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.8557 | 96.2201 | 96.7314 | 96.6627 | 96.5254 | 96.3471 | 96.448 | 95.4959 | 97.1929 | 97.7963 | 97.8029 | 97.833 | 97.7774 | 97.694 | 95.5529 | 97.5151 | 97.9236 | 98.173 | 98.2148 | 98.1572 | 98.0267 | SunPower15SPR-15000m-3 [480V] | 2017-09-01 | 2018-10-15
SunPower | SPR-15000m-3-H [480V] | Y | Y | Y | Sunny Tripower TL-US 15 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter | 15 | 480 | 97.5 | [7/13/2017] | [2.03.04.R] | 2018-10-15 | Y | N | Multiple Listing of SMA America | 1.79 |  |  | 300 | 675 | 800 | 1.5 | 3 | 4.5 | 7.5 | 11.25 | 15 | 93.8557 | 96.2201 | 96.7314 | 96.6627 | 96.5254 | 96.3471 | 96.448 | 95.4959 | 97.1929 | 97.7963 | 97.8029 | 97.833 | 97.7774 | 97.694 | 95.5529 | 97.5151 | 97.9236 | 98.173 | 98.2148 | 98.1572 | 98.0267 | SunPower15SPR-15000m-3-H [480V] | 2017-09-01 | 2018-10-15
SunPower | SPR-20000m-3 [480V] | Y | Y | Y | Sunny Tripower TL-US 20 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter | 20 | 480 | 97.5 | [7/13/2017] | [2.03.04.R] | 2018-10-15 | Y | N | Multiple Listing of SMA America | 1.79 |  |  | 380 | 695 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 95.166 | 96.9605 | 97.2062 | 97.0835 | 96.9341 | 96.7051 | 96.9173 | 97.2288 | 98.2895 | 98.5099 | 98.5485 | 97.8368 | 97.7051 | 98.0588 | 96.4929 | 97.8688 | 98.1306 | 98.2198 | 98.1746 | 98.0422 | 98.0897 | SunPower20SPR-20000m-3 [480V] | 2017-09-01 | 2018-10-15
SunPower | SPR-20000m-3-H [480V] | Y | Y | Y | Sunny Tripower TL-US 20 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter | 20 | 480 | 97.5 | [7/13/2017] | [2.03.04.R] | 2018-10-15 | Y | N | Multiple Listing of SMA America | 1.79 |  |  | 380 | 695 | 800 | 2 | 4 | 6 | 10 | 15 | 20 | 95.166 | 96.9605 | 97.2062 | 97.0835 | 96.9341 | 96.7051 | 96.9173 | 97.2288 | 98.2895 | 98.5099 | 98.5485 | 97.8368 | 97.7051 | 98.0588 | 96.4929 | 97.8688 | 98.1306 | 98.2198 | 98.1746 | 98.0422 | 98.0897 | SunPower20SPR-20000m-3-H [480V] | 2017-09-01 | 2018-10-15
SunPower | SPR-24000m-3 [480V] | Y | Y | Y | Sunny Tripower TL-US 24 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter | 24.06 | 480 | 98 | [7/13/2017] | [2.03.04.R] | 2018-10-15 | Y | N | Multiple Listing of SMA America | 1.79 |  |  | 450 | 712 | 800 | 2.406 | 4.812 | 7.218 | 12.03 | 18.045 | 24.06 | 96.0825 | 97.4242 | 97.4447 | 97.3151 | 97.1222 | 96.8659 | 97.1621 | 97.4599 | 98.348 | 98.5031 | 98.5314 | 98.4351 | 98.2665 | 98.4117 | 96.9099 | 98.0049 | 98.1886 | 98.2041 | 98.0766 | 97.8823 | 98.0569 | SunPower24.06SPR-24000m-3 [480V] | 2017-09-01 | 2018-10-15
SunPower | SPR-24000m-3-H [480V] | Y | Y | Y | Sunny Tripower TL-US 24 kW, 480 Vac, 3-phase, transformerless Grid Support Utility Interactive Inverter | 24.06 | 480 | 98 | [7/13/2017] | [2.03.04.R] | 2018-10-15 | Y | N | Multiple Listing of SMA America | 1.79 |  |  | 450 | 712 | 800 | 2.406 | 4.812 | 7.218 | 12.03 | 18.045 | 24.06 | 96.0825 | 97.4242 | 97.4447 | 97.3151 | 97.1222 | 96.8659 | 97.1621 | 97.4599 | 98.348 | 98.5031 | 98.5314 | 98.4351 | 98.2665 | 98.4117 | 96.9099 | 98.0049 | 98.1886 | 98.2041 | 98.0766 | 97.8823 | 98.0569 | SunPower24.06SPR-24000m-3-H [480V] | 2017-09-01 | 2018-10-15
SunPower | SPR-30000m-3 [480V] | Y | Y | Y | Sunny Tripower TL-US, 30kW, 480Vac 3-phase, Transformerless, Grid Support Utility Interactive Inverter | 30.01 | 480 | 98 | [7/6/2017] | [2.03.04.R] | 2018-10-15 | Y | N | Multiple Listing of SMA America | 1.22 |  |  | 500 | 720 | 800 | 3.001 | 6.002 | 9.003 | 15.005 | 22.5075 | 30.01 | 96.588 | 97.716 | 97.926 | 97.98 | 97.838 | 97.622 | 97.8115 | 97.588 | 98.448 | 98.69 | 98.602 | 98.538 | 98.328 | 98.5167 | 97.026 | 98.06 | 98.452 | 98.386 | 98.282 | 98.08 | 98.2528 | SunPower30.01SPR-30000m-3 [480V] | 2017-09-01 | 2018-10-15
Sunset | SUNstring 4000 [240V] | Y | N | N | 2.9 kW, 240 Vac, 125-400 Vdc Utility Interactive Inverter | 2.86 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 2.77 |  |  | 100 | 175 | 300 | 0.29 | 0.57 | 0.86 | 1.43 | 2.15 | 2.86 | 91.1 | 94.1 | 94.5 | 94.7 | 94.1 | 93.3 | 94.1 | 90.5 | 93.7 | 94.3 | 94.5 | 93.8 | 93 | 93.8 | 90.6 | 93.2 | 94.3 | 93.9 | 93.2 | 92.5 | 93.4 | Sunset2.86SUNstring 4000 [240V]
Sunset | SUNstring 5000 [240V] | Y | N | N | 3.6 kW, 240 Vac, 125-400 Vdc Utility Interactive Inverter | 3.6 | 240 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 3.11 |  |  | 100 | 175 | 300 | 0.36 | 0.72 | 1.08 | 1.8 | 2.7 | 3.6 | 89.9 | 93.3 | 94.2 | 94.3 | 94 | 93.3 | 93.8 | 89.7 | 93.1 | 94.1 | 94.2 | 93.9 | 93.2 | 93.7 | 89 | 92.4 | 93.5 | 93.8 | 93.6 | 92.9 | 93.3 | Sunset3.6SUNstring 5000 [240V]
Sustainable Energy Technologies | SUNERGY ELV 208 [208V] | Y | N | N | 5000 W, 208 Vac, Grid-Direct Solar PV Inverter | 5 | 208 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.27 |  |  | 54 | 65 | 95 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90.38 | 95.05 | 95.76 | 95.79 | 94.96 | 93.79 | 94.99 | 88.56 | 94 | 94.95 | 95.14 | 94.48 | 93.59 | 94.37 | 83.41 | 91.15 | 92.88 | 93.5 | 93.29 | 92.63 | 92.75 | Sustainable Energy Technologies5SUNERGY ELV 208 [208V]
Sustainable Energy Technologies | SUNERGY LV 208 [208V] | Y | N | N | 5000 W, 208 Vac, Grid-Direct Solar PV Inverter | 5 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 | 5 | 0.03 | 70 | 85 | 130 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 90.4 | 94.7 | 95.6 | 95.8 | 95.2 | 94.4 | 95.1 | 88.8 | 93.9 | 95 | 95.3 | 94.9 | 94.2 | 94.7 | 84.4 | 91.4 | 93.2 | 93.9 | 94.1 | 93.4 | 93.4 | Sustainable Energy Technologies5SUNERGY LV 208 [208V]
Sustainable Energy Technologies | SUNERGY TENK 240D [240V] | Y | N | N | 5000 W, 240 Vac, Grid-Direct Solar PV Inverter | 5 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.19 |  |  | 50 | 63 | 95 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 92.29 | 95.48 | 96 | 95.96 | 95.21 | 94.16 | 95.31 | 90.15 | 94.4 | 95.25 | 95.3 | 94.9 | 93.89 | 94.76 | 85.05 | 91.96 | 93.38 | 93.99 | 93.89 | 93.13 | 93.36 | Sustainable Energy Technologies5SUNERGY TENK 240D [240V]
Sustainable Energy Technologies | Sunergy 5000-70/240 [240V] | Y | N | N | 5000 W, 240 Vac, Grid-Direct Solar PV Inverter | 5.009 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.52 |  |  | 70 | 78 | 100 | 0.5 | 1 | 1.5 | 2.5 | 3.76 | 5.01 | 90.2 | 94.6 | 95.4 | 95.7 | 95.3 | 94.6 | 95.1 | 88.8 | 93.9 | 95 | 95.4 | 95.1 | 94.5 | 94.8 | 87.8 | 93.2 | 94.6 | 95 | 94.9 | 94.2 | 94.5 | Sustainable Energy Technologies5.009Sunergy 5000-70/240 [240V]
Sysgration | Soleil 2000-120 [120V] | Y | N | N | 2000 W, 120Vac Utility Interactive Inverter | 2 | 120 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 14.18 |  |  | 100 | 240 | 360 | 0.2 | 0.4 | 0.6 | 1 | 1.5 | 2 | 89 | 92.2 | 92.8 | 92.6 | 91.7 | 90.8 | 91.9 | 88.6 | 91.9 | 92.8 | 92.6 | 91.6 | 90.5 | 91.8 | 87.1 | 90.8 | 91.8 | 92.2 | 91.3 | 90.1 | 91.3 | Sysgration2Soleil 2000-120 [120V]
Sysgration | SG-4000 [240V] | Y | N | N | 4000 W, 240 Vac, Utility Interactive Inverter | 4.03 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.19 |  |  | 100 | 310 | 440 | 0.4 | 0.81 | 1.21 | 2.02 | 3.02 | 4.03 | 91.6 | 94.5 | 95.2 | 95.3 | 95 | 93.9 | 94.9 | 90.2 | 94.5 | 95.5 | 95.8 | 95.6 | 95 | 95.3 | 87.4 | 92.8 | 94 | 95 | 95.2 | 94.6 | 94.5 | Sysgration4.03SG-4000 [240V]
Tabuchi Electric Co., Ltd. | EHW-S55P3B-PNUS [240V] | Y | N | N | 5346 W, 240 Vac, Utility Interactive Inverter | 5.346 | 240 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.017 |  |  | 100 | 300 | 450 | 0.53 | 1.07 | 1.6 | 2.67 | 4.01 | 5.35 | 77.2 | 87 | 90 | 92.4 | 92.8 | 92.2 | 91.4 | 80.3 | 88.8 | 91.2 | 93 | 93.4 | 93.3 | 92.3 | 81.5 | 88.6 | 90.5 | 91.7 | 92.1 | 92.2 | 91.2 | Tabuchi Electric Co., Ltd.5.346EHW-S55P3B-PNUS [240V] |  | 2017-12-15
Tabuchi Electric Co., Ltd. | THD-S55P3BB-US [240V] | N | Y | Y | 5.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with 3.3 kW Discharge Rate/20 kWh Storage Capacity | 5.5189 | 240 | 94.5 | [9/20/2017] | [4.1] | 2018-10-15 | N | N |  | 10.1 |  |  | 240 | 380 | 520 | 0.55189 | 1.1038 | 1.6557 | 2.7595 | 4.1392 | 5.5189 | 89.3 | 93.3 | 94.3 | 94.7 | 94.1 | 94.2 | 94 | 89.7 | 93.7 | 94.7 | 95.4 | 95.5 | 95.4 | 95.1 | 88.8 | 93.1 | 94.3 | 95.1 | 95.2 | 94.9 | 94.7 | Tabuchi Electric Co., Ltd.5.51892THD-S55P3BB-US | 2017-12-15 | 2018-10-15
Tabuchi Electric Co., Ltd. | THD-S55P3B-US [240V] | N | Y | Y | 5.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with 2 kW Discharge Rate/10 kWh Storage Capacity | 5.5189 | 240 | 94.5 | [9/20/2017] | [4.1] | 2018-10-15 | N | N |  | 10.1 |  |  | 240 | 380 | 520 | 0.55189 | 1.1038 | 1.6557 | 2.7595 | 4.1392 | 5.5189 | 89.3 | 93.3 | 94.3 | 94.7 | 94.1 | 94.2 | 94 | 89.7 | 93.7 | 94.7 | 95.4 | 95.5 | 95.4 | 95.1 | 88.8 | 93.1 | 94.3 | 95.1 | 95.2 | 94.9 | 94.7 | Tabuchi Electric Co., Ltd.5.51892THD-S55P3B-US | 2017-12-15 | 2018-10-15
Tabuchi Electric Co., Ltd. | THE-S55P3BB-USW [240V] | N | Y | Y | 5.5 kW, 240 Vac Grid Support Utility Interactive Hybrid Inverter with 4.0 kW Discharge Rate/20 kWh Storage Capacity | 5.5189 | 240 | 94.5 | [04/26/2018] | [4.11] | 2018-10-15 | N | N |  | 10.1 |  |  | 240 | 380 | 520 | 0.55189 | 1.1038 | 1.6557 | 2.7595 | 4.1392 | 5.5189 | 89.326 | 93.286 | 94.304 | 94.656 | 94.048 | 94.174 | 93.9857 | 89.688 | 93.666 | 94.706 | 95.44 | 95.498 | 95.41 | 95.0624 | 88.78 | 93.076 | 94.276 | 95.094 | 95.166 | 94.922 | 94.6719 | Tabuchi Electric Co., Ltd.5.51892THE-S55P3BB-USW [240V] | 2018-06-01 | 2018-10-15
Tabuchi Electric Co., Ltd. | EPW-T250P6-US [480V] | Y | N | N | 24 kW, 480 Vac, transformerless Utility Interactive Inverter | 24.13 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 7.127 |  |  | 500 | 700 | 800 | 2.41 | 4.83 | 7.24 | 12.07 | 18.1 | 24.13 | 93.8 | 96.9 | 97.7 | 97.2 | 97.2 | 97.1 | 97.1 | 94.3 | 96.6 | 98.1 | 98.5 | 98 | 97.4 | 97.9 | 94.1 | 96.5 | 97.9 | 97.4 | 97.6 | 98 | 97.4 | Tabuchi Electric Co., Ltd.24.13EPW-T250P6-US [480V] |  | 2017-12-15
Tabuchi Electric Co., Ltd. | TPD-T250P6-US [480V] | Y | N | N | 25 kW, 480 Vac, transformerless Utility Interactive Inverter | 24.895 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 7.129 |  |  | 500 | 700 | 800 | 2.49 | 4.98 | 7.47 | 12.45 | 18.67 | 24.9 | 93.9956 | 96.6194 | 98.2385 | 96.7456 | 98.0242 | 97.2681 | 97.5122 | 93.2322 | 96.6486 | 98.7005 | 97.6598 | 97.8204 | 97.7219 | 97.6452 | 92.8068 | 96.3838 | 98.097 | 96.976 | 97.4662 | 97.4504 | 97.1977 | Tabuchi Electric Co., Ltd.24.895TPD-T250P6-US [480V] |  | 2017-12-15
Talesun Solar | TP660AM225 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.23 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.02 |  |  | 21 | 31.5 | 35 | 0.02 | 0.05 | 0.07 | 0.11 | 0.17 | 0.23 | 87 | 92 | 93.4 | 94.5 | 94.5 | 94.1 | 93.9 | 85.8 | 91.5 | 93.5 | 95.1 | 96.1 | 95.3 | 94.9 | 85.4 | 91.3 | 93.3 | 94.9 | 95.3 | 95.5 | 94.4 | Talesun Solar0.23TP660AM225 [240V]
Talesun Solar | TP660AM240 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 33.5 | 42.5 | 46 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 89.1 | 93.6 | 94.7 | 95 | 95.1 | 94.8 | 94.7 | 88.6 | 93.5 | 94.7 | 95.3 | 95.6 | 94.8 | 95 | 88.1 | 93.3 | 94.7 | 95.3 | 95.7 | 95.7 | 95.1 | Talesun Solar0.24TP660AM240 [240V]
Talesun Solar | TP660AM255 [240V] | Y | N | N | 225 W, 240 Vac Inverter | 0.25 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.28 |  |  | 46 | 53.5 | 57 | 0.02 | 0.05 | 0.07 | 0.13 | 0.19 | 0.25 | 91.2 | 95.2 | 96 | 95.5 | 95.7 | 95.5 | 95.5 | 91.4 | 95.5 | 95.9 | 95.5 | 95.1 | 94.3 | 95.1 | 90.8 | 95.3 | 96.1 | 95.7 | 96.1 | 95.9 | 95.8 | Talesun Solar0.25TP660AM255 [240V]
Talesun Solar | TP660AM270 [240V] | Y | N | N | 241 W, 240 Vac Inverter | 0.26 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.41 |  |  | 58.5 | 64.5 | 68 | 0.02 | 0.05 | 0.07 | 0.14 | 0.2 | 0.26 | 93.3 | 96.8 | 97.3 | 96 | 96.3 | 96.2 | 96.3 | 94.2 | 97.5 | 97.1 | 95.7 | 94.6 | 93.8 | 95.2 | 93.5 | 97.3 | 97.5 | 96.1 | 96.5 | 96.1 | 96.5 | Talesun Solar0.26TP660AM270 [240V]
TMEIC | PVL-L0500U | Y | N | N | 500 kW Utility Interactive Inverter for medium voltage transformer | 500 |  | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 60 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 91.4 | 95.1 | 96 | 96.4 | 96 | 95.4 | 95.8 | 91 | 94.8 | 95.8 | 96.2 | 95.9 | 95.2 | 95.7 | 89.7 | 94.2 | 95.7 | 95.8 | 95.5 | 94.9 | 95.3 | TMEIC500PVL-L0500U
TMEIC | PVL-L0630U-S | Y | N | N | 630 kW Utility Interactive Inverter for medium voltage transformer | 630 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 53 |  |  | 550 | 615 | 800 | 63 | 126 | 189 | 315 | 472.5 | 630 | 94.2 | 96.9 | 97.3 | 97.8 | 97.4 | 96.9 | 97.3 | 94 | 96.8 | 97.2 | 97.7 | 97.3 | 96.8 | 97.2 | 93.2 | 96.5 | 96.9 | 97.6 | 97.2 | 96.6 | 97 | TMEIC630PVL-L0630U-S
TMEIC | PVL-L0833GR | Y | N | N | 1.35 MW Utility Interactive Inverter for medium voltage transformer | 833 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 78 |  |  | 605 | 655 | 800 | 83.3 | 166.6 | 249.9 | 416.5 | 624.75 | 833 | 95.4 | 97.4 | 97.9 | 98 | 97.8 | 97.5 | 97.7 | 95.1 | 97.3 | 97.8 | 97.9 | 97.7 | 97.3 | 97.6 | 94.6 | 97 | 97.5 | 97.7 | 97.5 | 97.1 | 97.4 | TMEIC833PVL-L0833GR
TMEIC | PVH-L1350GR | Y | N | N | 1.35 MW Utility Interactive Inverter for medium voltage transformer | 1350 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 106 |  |  | 875 | 960 | 1200 | 135 | 270 | 405 | 675 | 1012.5 | 1350 | 95.4133 | 97.4401 | 97.9838 | 98.1254 | 97.9325 | 97.5613 | 97.8352 | 95.0511 | 97.3945 | 97.881 | 98.0214 | 97.8127 | 97.4201 | 97.7137 | 94.5754 | 97.0141 | 97.6434 | 97.8014 | 97.6385 | 97.2585 | 97.5006 | TMEIC1350PVH-L1350GR
TMEIC | PVH-L1350GR-EG | Y | N | N | 1.35 MW Utility Interactive Inverter for medium voltage transformer | 1350 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 106 |  |  | 875 | 960 | 1200 | 135 | 270 | 405 | 675 | 1012.5 | 1350 | 95.4133 | 97.4401 | 97.9838 | 98.1254 | 97.9325 | 97.5613 | 97.8352 | 95.0511 | 97.3945 | 97.881 | 98.0214 | 97.8127 | 97.4201 | 97.7137 | 94.5754 | 97.0141 | 97.6434 | 97.8014 | 97.6385 | 97.2585 | 97.5006 | TMEIC1350PVH-L1350GR-EG
TMEIC | PVL-L1833GRQ | Y | N | N | 1667 kW Utility Interactive Inverter for medium voltage transformer | 1667 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 100 |  |  | 605 | 655 | 800 | 166.7 | 333.4 | 500.1 | 833.5 | 1250 | 1667 | 96.2 | 97.8 | 98.1 | 98.1 | 97.9 | 97.3 | 97.8 | 96.1 | 97.7 | 98.1 | 98 | 97.7 | 97.2 | 97.7 | 96 | 97.6 | 97.9 | 97.9 | 97.5 | 97 | 97.6 | TMEIC1667PVL-L1833GRQ
TMEIC | PVL-L1833GRM | Y | N | N | 1.833 MW Utility Interactive Inverter for medium voltage transformer | 1833 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 110 |  |  | 605 | 655 | 800 | 183.3 | 366.6 | 549.9 | 916.5 | 1374.75 | 1833 | 95.9 | 97.7 | 98.2 | 98.2 | 98 | 97.5 | 97.9 | 95.6 | 97.6 | 98 | 98.1 | 97.8 | 97.4 | 97.8 | 95.3 | 97.4 | 97.9 | 97.9 | 97.7 | 97.3 | 97.6 | TMEIC1833PVL-L1833GRM
TMEIC | PVH-L2500GR | Y | N | N | 2.5 MW Utility Interactive Inverter | 2500 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 235 |  |  | 800 | 900 | 1200 | 250 | 500 | 750 | 1250 | 1875 | 2500 | 95.9 | 97.6 | 97.9 | 98 | 97.8 | 97.4 | 97.8 | 95.6 | 97.5 | 97.8 | 97.9 | 97.7 | 97.2 | 97.6 | 95.2 | 97.2 | 97.6 | 97.7 | 97.5 | 97.1 | 97.4 | TMEIC2500PVH-L2500GR |  | 2017-12-15
TMEIC | PVH-L2500GR-EG | Y | N | N | 2.5 MW Utility Interactive Inverter | 2500 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 235 |  |  | 800 | 900 | 1200 | 250 | 500 | 750 | 1250 | 1875 | 2500 | 95.9 | 97.6 | 97.9 | 98 | 97.8 | 97.4 | 97.8 | 95.6 | 97.5 | 97.8 | 97.9 | 97.7 | 97.2 | 97.6 | 95.2 | 97.2 | 97.6 | 97.7 | 97.5 | 97.1 | 97.4 | TMEIC2500PVH-L2500GR-EG |  | 2017-12-15
TMEIC | PVH-L2700GR | Y | N | N | 2.7 MW Utility Interactive Inverter | 2700 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 265 |  |  | 875 | 960 | 1200 | 270 | 540 | 810 | 1350 | 2025 | 2700 | 95.8 | 97.6 | 98 | 98 | 97.9 | 97.5 | 97.8 | 95.6 | 97.5 | 97.9 | 97.9 | 97.8 | 97.3 | 97.7 | 95.3 | 97.3 | 97.7 | 97.8 | 97.6 | 97.1 | 97.5 | TMEIC2700PVH-L2700GR |  | 2017-12-15
TMEIC | PVH-L2700GR-EG | Y | N | N | 2.7 MW Utility Interactive Inverter | 2700 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 265 |  |  | 875 | 960 | 1200 | 270 | 540 | 810 | 1350 | 2025 | 2700 | 95.8 | 97.6 | 98 | 98 | 97.9 | 97.5 | 97.8 | 95.6 | 97.5 | 97.9 | 97.9 | 97.8 | 97.3 | 97.7 | 95.3 | 97.3 | 97.7 | 97.8 | 97.6 | 97.1 | 97.5 | TMEIC2700PVH-L2700GR-EG |  | 2017-12-15
TMEIC | PVH-L3200GR [600V] | Y | N | N | 3200 kW, rated 1500Vdc (Negative Ground), 600Vac Utility Interactive PV Inverter | 3127.43 | 600 | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Efficiency data inclusive of transformer effect based on 3.2 MVA DOE 2016 Transformer Efficiency. | 49 |  |  | 875 | 1100 | 1200 | 312.74 | 625.49 | 938.23 | 1563.72 | 2345.57 | 3127.43 | 96.15 | 98.02 | 98.44 | 98.46 | 98.72 | 98.76 | 98.5 | 95.52 | 97.68 | 98.19 | 98.24 | 98.48 | 98.55 | 98.24 | 95.41 | 97.54 | 98.09 | 98.18 | 98.46 | 98.5 | 98.19 | TMEIC3127.43PVH-L3200GR [600V] | 2018-04-16
TMEIC | PVH-L3200GR-E7 [600V] | Y | N | N | 3200 kW, rated 1500Vdc (Negative Ground), 600Vac, 3.2MW output, compliant with NEC 2017 Utility Interactive PV Inverter | 3127.43 | 600 | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Efficiency data inclusive of transformer effect based on 3.2 MVA DOE 2016 Transformer Efficiency. | 49 |  |  | 875 | 1100 | 1200 | 312.74 | 625.49 | 938.23 | 1563.72 | 2345.57 | 3127.43 | 96.15 | 98.02 | 98.44 | 98.46 | 98.72 | 98.76 | 98.5 | 95.52 | 97.68 | 98.19 | 98.24 | 98.48 | 98.55 | 98.24 | 95.41 | 97.54 | 98.09 | 98.18 | 98.46 | 98.5 | 98.19 | TMEIC3127.43PVH-L3200GR-E7 [600V] | 2018-04-16
TMEIC | PVH-L3200GR-EG [600V] | Y | N | N | 3200 kW, rated 1500Vdc (Negative Externally Grounded), 600Vac Utility Interactive PV Inverter | 3127.43 | 600 | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Efficiency data inclusive of transformer effect based on 3.2 MVA DOE 2016 Transformer Efficiency. | 49 |  |  | 875 | 1100 | 1200 | 312.74 | 625.49 | 938.23 | 1563.72 | 2345.57 | 3127.43 | 96.15 | 98.02 | 98.44 | 98.46 | 98.72 | 98.76 | 98.5 | 95.52 | 97.68 | 98.19 | 98.24 | 98.48 | 98.55 | 98.24 | 95.41 | 97.54 | 98.09 | 98.18 | 98.46 | 98.5 | 98.19 | TMEIC3127.43PVH-L3200GR-EG [600V] | 2018-04-16
Topper Sun Energy Technology | TS-S1500 [208V] | Y | N | N | 1.5 kW, 208 Vac Utility Interactive Inverter | 1.55 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.21 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.46 | 90.49 | 92.52 | 94.25 | 94.92 | 95.02 | 93.86 | 85.04 | 91.04 | 93.19 | 94.79 | 95.41 | 95.53 | 94.38 | 85.31 | 91.19 | 93.54 | 95.02 | 95.55 | 95.76 | 94.58 | Topper Sun Energy Technology1.55TS-S1500 [208V]
Topper Sun Energy Technology | TS-S1500 [240V] | Y | N | N | 1.5 kW, 240 Vac Utility Interactive Inverter | 1.55 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.32 |  |  | 100 | 325 | 360 | 0.155 | 0.31 | 0.465 | 0.775 | 1.163 | 1.55 | 84.62 | 90.46 | 92.57 | 94.42 | 95.07 | 95.25 | 93.99 | 84.89 | 90.97 | 93.04 | 94.81 | 95.51 | 95.73 | 94.42 | 85.22 | 91.38 | 93.44 | 95.12 | 95.65 | 95.93 | 94.66 | Topper Sun Energy Technology1.55TS-S1500 [240V]
Topper Sun Energy Technology | TS-S2000 [208V] | Y | N | N | 2 kW, 208 Vac Utility Interactive Inverter | 2.06 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.29 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 88.28 | 93.12 | 94.41 | 95.27 | 95.43 | 95.37 | 94.87 | 89.63 | 93.68 | 94.91 | 95.73 | 95.84 | 95.8 | 95.34 | 89.74 | 94.01 | 95.11 | 96.13 | 96.38 | 96.07 | 95.77 | Topper Sun Energy Technology2.06TS-S2000 [208V]
Topper Sun Energy Technology | TS-S2000 [240V] | Y | N | N | 2 kW, 240 Vac Utility Interactive Inverter | 2.06 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.36 |  |  | 100 | 325 | 360 | 0.206 | 0.412 | 0.618 | 1.03 | 1.545 | 2.06 | 86.91 | 92.14 | 93.78 | 94.94 | 95.3 | 95.37 | 94.55 | 87.84 | 92.87 | 94.26 | 95.56 | 95.79 | 95.73 | 95.09 | 88.1 | 93.05 | 94.37 | 95.71 | 96 | 95.94 | 95.28 | Topper Sun Energy Technology2.06TS-S2000 [240V]
Topper Sun Energy Technology | TS-S3000 [208V] | Y | N | N | 3 kW, 208 Vac Utility Interactive Inverter | 3 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 91.57 | 94.41 | 95.16 | 95.47 | 95.31 | 94.62 | 95.1 | 92.05 | 94.92 | 95.58 | 95.89 | 95.76 | 95.37 | 95.56 | 92.22 | 95.17 | 95.79 | 96.25 | 95.93 | 95.8 | 95.78 | Topper Sun Energy Technology3TS-S3000 [208V]
Topper Sun Energy Technology | TS-S3000 [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.301 | 0.602 | 0.903 | 1.505 | 2.258 | 3.01 | 90 | 93.9 | 94.85 | 95.4 | 95.31 | 94.83 | 94.97 | 90.64 | 94.34 | 95.34 | 95.79 | 95.87 | 95.6 | 95.49 | 91 | 94.59 | 95.44 | 95.97 | 96.01 | 95.77 | 95.65 | Topper Sun Energy Technology3.01TS-S3000 [240V]
Topper Sun Energy Technology | TS-S4000 [208V] | Y | N | N | 4 kW, 208 Vac Utility Interactive Inverter | 3.98 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.18 |  |  | 100 | 325 | 360 | 0.398 | 0.796 | 1.194 | 1.99 | 2.985 | 3.98 | 90.53 | 94.32 | 95.17 | 95.44 | 95.41 | 95.16 | 95.13 | 91.58 | 94.87 | 95.63 | 96.05 | 96 | 95.45 | 95.7 | 91.82 | 95.03 | 95.8 | 96.45 | 96.31 | 95.76 | 96.01 | Topper Sun Energy Technology3.98TS-S4000 [208V]
Topper Sun Energy Technology | TS-S4000 [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 3.99 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 325 | 360 | 0.399 | 0.798 | 1.197 | 1.995 | 2.993 | 3.99 | 90.55 | 94.3 | 95.24 | 95.69 | 95.74 | 95.56 | 95.38 | 91.53 | 94.95 | 95.81 | 96.33 | 96.33 | 96.05 | 95.99 | 91.95 | 95.23 | 95.96 | 96.4 | 96.48 | 96.25 | 96.15 | Topper Sun Energy Technology3.99TS-S4000 [240V]
Toshiba International | PVT-AAA50K6U | Y | N | N | 500 kW Utility Interactive Inverter for medium voltage transformer | 500 |  | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 60 |  |  | 320 | 360 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 91.4 | 95.1 | 96 | 96.4 | 96 | 95.4 | 95.8 | 91 | 94.8 | 95.8 | 96.2 | 95.9 | 95.2 | 95.7 | 89.7 | 94.2 | 95.7 | 95.8 | 95.5 | 94.9 | 95.3 | Toshiba International500PVT-AAA50K6U
Toshiba International | PVL-L0630U-S | Y | N | N | 630 kW Utility Interactive Inverter for medium voltage transformer | 630 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 53 |  |  | 550 | 615 | 800 | 63 | 126 | 189 | 315 | 472.5 | 630 | 94.2 | 96.9 | 97.3 | 97.8 | 97.4 | 96.9 | 97.3 | 94 | 96.8 | 97.2 | 97.7 | 97.3 | 96.8 | 97.2 | 93.2 | 96.5 | 96.9 | 97.6 | 97.2 | 96.6 | 97 | Toshiba International630PVL-L0630U-S
Trina Energy Storage Solutions (Jiangsu) Co., Ltd | TB6000SHU [208V] | N | Y | Y | 4992 W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter | 4.992 | 208 | 97 | [03/03/2018] | [1.4.1] | 2018-10-15 | N | N |  | 1.86 |  |  | 200 | 380 | 460 | 0.4992 | 0.9984 | 1.4976 | 2.496 | 3.744 | 4.992 | 92.957 | 94.9487 | 95.9767 | 96.7593 | 96.8163 | 96.5806 | 96.444 | 95.5718 | 97.208 | 97.7454 | 97.945 | 97.7162 | 97.3118 | 97.6363 | 94.612 | 96.6111 | 97.398 | 97.7397 | 97.624 | 97.2797 | 97.4328 | Trina Energy Storage Solutions (Jiangsu) Co., Ltd4.992TB6000SHU [208V] | 2018-08-01 | 2018-10-15
Trina Energy Storage Solutions (Jiangsu) Co., Ltd | TB6000SHU [240V] | N | Y | Y | 5760 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter | 5.76 | 240 | 97.5 | [03/03/2018] | [1.4.1] | 2018-10-15 | N | N |  | 2.25 |  |  | 200 | 380 | 460 | 0.576 | 1.152 | 1.728 | 2.88 | 4.32 | 5.76 | 93.6482 | 95.423 | 96.4707 | 97.0891 | 97.0873 | 96.8107 | 96.7791 | 96.1623 | 97.5847 | 98.0803 | 98.165 | 97.934 | 97.5803 | 97.894 | 95.2354 | 97.0478 | 97.7734 | 98.0001 | 97.8593 | 97.5051 | 97.7153 | Trina Energy Storage Solutions (Jiangsu) Co., Ltd5.76TB6000SHU [240V] | 2018-08-01 | 2018-10-15
Trina Energy Storage Solutions (Jiangsu) Co., Ltd | TB8000SHU [208V] | N | Y | Y | 6656W, 208 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter | 6.656 | 208 | 97.5 | [03/03/2018] | [1.4.1] | 2018-10-15 | N | N |  | 1.15 |  |  | 270 | 380 | 460 | 0.6656 | 1.3312 | 1.9968 | 3.328 | 4.992 | 6.656 | 94.5771 | 96.3015 | 96.9963 | 97.3878 | 97.2948 | 96.929 | 97.1019 | 95.9053 | 97.3314 | 97.7633 | 97.8619 | 97.5862 | 97.2138 | 97.5667 | 94.9781 | 96.8811 | 97.4182 | 97.6928 | 97.4986 | 97.1525 | 97.3807 | Trina Energy Storage Solutions (Jiangsu) Co., Ltd6.656TB8000SHU [208V] | 2018-08-01 | 2018-10-15
Trina Energy Storage Solutions (Jiangsu) Co., Ltd | TB8000SHU [240V] | N | Y | Y | 7680 W, 240 Vac, transformerless, Bi-dierctional, Muti-mode Grid Support Utility Interactive Solar and Energy Storage Inverter | 7.68 | 240 | 97.5 | [03/03/2018] | [1.4.1] | 2018-10-15 | N | N |  | 1.19 |  |  | 270 | 380 | 460 | 0.768 | 1.536 | 2.304 | 3.84 | 5.76 | 7.68 | 95.1418 | 96.5566 | 97.3325 | 97.5972 | 97.5104 | 97.1304 | 97.3459 | 96.4957 | 97.6782 | 98.0328 | 98.0644 | 97.7762 | 97.4311 | 97.7942 | 95.6637 | 97.2768 | 97.7475 | 97.9312 | 97.7346 | 97.4232 | 97.6562 | Trina Energy Storage Solutions (Jiangsu) Co., Ltd7.68TB8000SHU [240V] | 2018-08-01 | 2018-10-15
Ubiquiti Networks International | SM-MI-250 [240V] | Y | N | N | 250 W, 240 Vac Utility Interactive Inverter | 0.25 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.12 |  |  | 28.7 | 30 | 31 | 0.03 | 0.05 | 0.13 | 0.13 | 0.19 | 0.25 | 94.8 | 95.7 | 95.8 | 95.7 | 95.4 | 95 | 95.5 | 94.8 | 95.7 | 95.8 | 95.7 | 95.4 | 95.2 | 95.5 | 94.7 | 95.6 | 95.8 | 95.7 | 95.4 | 95.2 | 95.5 | Ubiquiti Networks International0.25SM-MI-250 [240V]
Westinghouse Solar | WLW-230-1-AC1-A-B [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Westinghouse Solar0.19WLW-230-1-AC1-A-B [240V]
Westinghouse Solar | WLW-235-1-AC1-A-B [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Westinghouse Solar0.19WLW-235-1-AC1-A-B [240V]
Westinghouse Solar | WLW-235-1-AC3-B-B [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Westinghouse Solar0.19WLW-235-1-AC3-B-B [240V]
Westinghouse Solar | WLW-240-1-AC1-A-B [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Westinghouse Solar0.19WLW-240-1-AC1-A-B [240V]
Westinghouse Solar | WLW-240-1-AC3-B-B [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Westinghouse Solar0.19WLW-240-1-AC3-B-B [240V]
Westinghouse Solar | WS-175-1AC1-A-A [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Westinghouse Solar0.19WS-175-1AC1-A-A [240V]
Westinghouse Solar | WS-175-1AC3-B-A [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.02 | 0.04 | 0.06 | 0.1 | 0.1 | 0.2 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Westinghouse Solar0.19WS-175-1AC3-B-A [240V]
Westinghouse Solar | WS-185-1AC1-A-A [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Westinghouse Solar0.19WS-185-1AC1-A-A [240V]
Westinghouse Solar | WS-185-1AC1-A-B [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Westinghouse Solar0.19WS-185-1AC1-A-B [240V]
Westinghouse Solar | WS-185-1AC3-B-A [208V] | Y | N | N | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.02 | 0.04 | 0.06 | 0.1 | 0.1 | 0.2 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Westinghouse Solar0.19WS-185-1AC3-B-A [208V]
Westinghouse Solar | WS-185-1AC3-B-B [208V] | Y | N | N | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.02 | 0.04 | 0.06 | 0.1 | 0.1 | 0.2 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Westinghouse Solar0.19WS-185-1AC3-B-B [208V]
Westinghouse Solar | WS-190-1AC1-A-B [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Westinghouse Solar0.19WS-190-1AC1-A-B [240V]
Westinghouse Solar | WS-190-1AC3-B-B [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Westinghouse Solar0.19WS-190-1AC3-B-B [240V]
Westinghouse Solar | WS-195-1AC1-A-B [240V] | Y | N | N | 190 W, 240 Vac Inverter | 0.19 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.03 | 0.19 | 0.03 | 22 | 32.5 | 40 | 0.02 | 0.04 | 0.1 | 0.1 | 0.1 | 0.2 | 93.3 | 94.4 | 94.7 | 95.1 | 94.9 | 94.2 | 94.8 | 93.3 | 94.4 | 94.6 | 95.2 | 95.4 | 95.1 | 95.1 | 93.5 | 94.4 | 94.6 | 94.9 | 95.4 | 95.4 | 95.1 | Westinghouse Solar0.19WS-195-1AC1-A-B [240V]
Westinghouse Solar | WS-195-1AC3-B-B [208V] | Y | N | N | 190 W, 208 Vac Inverter | 0.19 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.01 | 0.19 | 0.01 | 22 | 32 | 40 | 0.019 | 0.038 | 0.057 | 0.095 | 0.1425 | 0.19 | 93.6 | 94.6 | 94.9 | 95 | 94.6 | 93.7 | 94.6 | 93.4 | 94.6 | 94.7 | 95.2 | 95.2 | 94.8 | 95 | 93.4 | 94.4 | 94.8 | 95.1 | 95.3 | 95.1 | 95.1 | Westinghouse Solar0.19WS-195-1AC3-B-B [208V]
Westinghouse Solar | WLW-230-1-AC0-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WLW-230-1-AC0-D-B [208V]
Westinghouse Solar | WLW-230-1-AC0-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WLW-230-1-AC0-D-B [240V]
Westinghouse Solar | WLW-230-1-AC2-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WLW-230-1-AC2-D-B [208V]
Westinghouse Solar | WLW-230-1-AC2-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WLW-230-1-AC2-D-B [240V]
Westinghouse Solar | WLW-235-1-AC0-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WLW-235-1-AC0-D-B [208V]
Westinghouse Solar | WLW-235-1-AC0-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WLW-235-1-AC0-D-B [240V]
Westinghouse Solar | WLW-235-1-AC2-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WLW-235-1-AC2-D-B [208V]
Westinghouse Solar | WLW-235-1-AC2-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WLW-235-1-AC2-D-B [240V]
Westinghouse Solar | WLW-240-1-AC0-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WLW-240-1-AC0-D-B [208V]
Westinghouse Solar | WLW-240-1-AC0-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WLW-240-1-AC0-D-B [240V]
Westinghouse Solar | WLW-240-1-AC2-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WLW-240-1-AC2-D-B [208V]
Westinghouse Solar | WLW-240-1-AC2-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 | 0.215 | 0.04 | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WLW-240-1-AC2-D-B [240V]
Westinghouse Solar | WTW-240-1-AC2-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WTW-240-1-AC2-D-B [208V]
Westinghouse Solar | WTW-240-1-AC2-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WTW-240-1-AC2-D-B [240V]
Westinghouse Solar | WTW-245-1-AC2-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WTW-245-1-AC2-D-B [208V]
Westinghouse Solar | WTW-245-1-AC2-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WTW-245-1-AC2-D-B [240V]
Westinghouse Solar | WTW-250-1-AC2-D-B [208V] | Y | N | N | 215 W, 208 Vac Inverter | 0.215 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WTW-250-1-AC2-D-B [208V]
Westinghouse Solar | WTW-250-1-AC2-D-B [240V] | Y | N | N | 215 W, 240 Vac Inverter | 0.215 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.04 |  |  | 22 | 29 | 36 | 0.02 | 0.04 | 0.06 | 0.11 | 0.16 | 0.22 | 94.5 | 95.5 | 95.9 | 96 | 95.5 | 94.7 | 95.6 | 94.5 | 95.5 | 95.9 | 96.1 | 96 | 95.5 | 95.9 | 94.4 | 95.4 | 95.7 | 96.1 | 96.1 | 95.8 | 95.9 | Westinghouse Solar0.215WTW-250-1-AC2-D-B [240V]
Xantrex Technology | GT2.5-NA-DS-240 [240V] | Y | N | N | 2.5 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 2.5 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 2.5 | 1 | 100 | 266 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 88.5 | 92.7 | 94.1 | 94.8 | 94.8 | 94.5 | 94.4 | 87.7 | 92.3 | 93.7 | 94.5 | 94.6 | 94.4 | 94.1 | 86.3 | 90.9 | 92.6 | 93.8 | 94 | 93.8 | 93.3 | Xantrex Technology2.5GT2.5-NA-DS-240 [240V]
Xantrex Technology | GT2.5-NA-DS-240-POS [240V] | Y | N | N | 2.5 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter (positive ground) | 2.5 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 2.5 | 1 | 100 | 266 | 480 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 88.5 | 92.7 | 94.1 | 94.8 | 94.8 | 94.5 | 94.4 | 87.7 | 92.3 | 93.7 | 94.5 | 94.6 | 94.4 | 94.1 | 86.3 | 90.9 | 92.6 | 93.8 | 94 | 93.8 | 93.3 | Xantrex Technology2.5GT2.5-NA-DS-240-POS [240V]
Xantrex Technology | GT2.8-NA-240/208 [208V] | Y | N | N | 2.7 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 2.7 | 208 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 2.7 | 1 | 100 | 266 | 480 | 0.27 | 0.54 | 0.81 | 1.35 | 2.025 | 2.7 | 88.7 | 93.1 | 94.1 | 94.6 | 94.5 | 94 | 94.1 | 88 | 92.8 | 93.8 | 94.4 | 94.3 | 93.8 | 93.9 | 84.6 | 90.6 | 92.3 | 93.4 | 93.4 | 92.5 | 92.7 | Xantrex Technology2.7GT2.8-NA-240/208 [208V]
Xantrex Technology | GT2.8-NA-240/208 [240V] | Y | N | N | 2.8 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 2.8 | 240 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.3 | 2.8 | 1.3 | 100 | 266 | 480 | 0.28 | 0.56 | 0.84 | 1.4 | 2.1 | 2.8 | 89.3 | 93.5 | 94.4 | 95 | 94.8 | 94.4 | 94.5 | 88.6 | 93.1 | 94.2 | 94.7 | 94.6 | 94.2 | 94.3 | 85.3 | 91 | 92.7 | 93.8 | 93.7 | 92.7 | 93.1 | Xantrex Technology2.8GT2.8-NA-240/208 [240V]
Xantrex Technology | GT3.0-NA-DS-240 [240V] | Y | N | N | 3.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 3 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 3 | 1 | 100 | 266 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 90.2 | 93.7 | 94.6 | 95 | 95 | 94.6 | 94.7 | 89.5 | 93.7 | 94.5 | 95 | 95 | 94.6 | 94.6 | 88.7 | 92.6 | 94 | 94.6 | 94.6 | 94.3 | 94.2 | Xantrex Technology3GT3.0-NA-DS-240 [240V]
Xantrex Technology | GT3.0-NA-DS-240-POS [240V] | Y | N | N | 3.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter (positive ground) | 3 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 3 | 1 | 100 | 266 | 480 | 0.3 | 0.6 | 0.9 | 1.5 | 2.25 | 3 | 90.2 | 93.7 | 94.6 | 95 | 95 | 94.6 | 94.7 | 89.5 | 93.7 | 94.5 | 95 | 95 | 94.6 | 94.6 | 88.7 | 92.6 | 94 | 94.6 | 94.6 | 94.3 | 94.2 | Xantrex Technology3GT3.0-NA-DS-240-POS [240V]
Xantrex Technology | GT3.3N-NA-240/208 [208V] | Y | N | N | 3.1 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.1 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.24 | 3.1 | 1.24 | 100 | 250 | 400 | 0.31 | 0.62 | 0.93 | 1.55 | 2.325 | 3.1 | 91.4 | 94.7 | 95.4 | 95.6 | 95.5 | 95.1 | 95.3 | 90.9 | 94.4 | 95.2 | 95.6 | 95.4 | 95.1 | 95.2 | 89.3 | 93.4 | 94.5 | 95.2 | 95.2 | 94.9 | 94.7 | Xantrex Technology3.1GT3.3N-NA-240/208 [208V]
Xantrex Technology | SW4048 [120V] | Y | N | N | 4.0 kVA, 48 Vdc, 120 Vac, Trace Engr. batt bkp, sine wave Inverter (with GTI) | 3.211 | 120 | 90.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 26.2 |  |  | 100 | 53.2 | 60 | 0.3211 | 0.6423 | 0.9634 | 1.606 | 2.408 | 3.211 | 92.7 | 94.3 | 94.1 | 92.2 | 88.5 | 85.5 | 90.3 | 92.8 | 93.7 | 93.6 | 91.8 | 89.1 | 84.8 | 90.4 | 91.1 | 92.9 | 93.1 | 91.2 | 89.3 | 85 | 90.2 | Xantrex Technology3.211SW4048 [120V]
Xantrex Technology | SW4024 [120V] | Y | N | N | 4.0 kVA, 24 Vdc, 120 Vac, Trace Engr. batt bkp, sine wave Inverter (with GTI) | 3.297 | 120 | 89 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 27.7 |  |  | 100 | 26.8 | 30 | 0.3297 | 0.6594 | 0.9891 | 1.649 | 2.473 | 3.297 | 92 | 93.6 | 93.3 | 90.9 | 88.4 | 83.7 | 89.7 | 91.3 | 93.1 | 93 | 91 | 87.5 | 83.1 | 89.1 | 88.9 | 92.3 | 92.4 | 90.7 | 87.1 | 83 | 88.6 | Xantrex Technology3.297SW4024 [120V]
Xantrex Technology | GT3.3-NA-DS-208 [208V] | Y | N | N | 3.3 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.3 | 208 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 3.3 | 1 | 100 | 266 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 90.1 | 93.3 | 94.2 | 94.6 | 94.3 | 93.6 | 94.1 | 89.5 | 93.2 | 94.1 | 94.6 | 94.3 | 93.6 | 94.1 | 87.2 | 91.7 | 93.2 | 93.9 | 93.7 | 93.1 | 93.3 | Xantrex Technology3.3GT3.3-NA-DS-208 [208V]
Xantrex Technology | GT3.3-NA-DS-208-POS [208V] | Y | N | N | 3.3 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.3 | 208 | 94 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 3.3 | 1 | 100 | 266 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 90.1 | 93.3 | 94.2 | 94.6 | 94.3 | 93.6 | 94.1 | 89.5 | 93.2 | 94.1 | 94.6 | 94.3 | 93.6 | 94.1 | 87.2 | 91.7 | 93.2 | 93.9 | 93.7 | 93.1 | 93.3 | Xantrex Technology3.3GT3.3-NA-DS-208-POS [208V]
Xantrex Technology | GT3.3-NA-DS-240 [240V] | Y | N | N | 3.3 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 3.3 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 3.3 | 1 | 100 | 266 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 90.6 | 93.8 | 94.9 | 95.3 | 95.1 | 94.6 | 94.9 | 90.1 | 93.7 | 94.6 | 95.1 | 95 | 94.4 | 94.7 | 87.2 | 91.9 | 93.4 | 94.4 | 94.3 | 93.8 | 93.8 | Xantrex Technology3.3GT3.3-NA-DS-240 [240V]
Xantrex Technology | GT3.3-NA-DS-240-POS [240V] | Y | N | N | 3.3 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 3.3 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 3.3 | 1 | 100 | 266 | 480 | 0.33 | 0.66 | 0.99 | 1.65 | 2.48 | 3.3 | 90.6 | 93.8 | 94.9 | 95.3 | 95.1 | 94.6 | 94.9 | 90.1 | 93.7 | 94.6 | 95.1 | 95 | 94.4 | 94.7 | 87.2 | 91.9 | 93.4 | 94.4 | 94.3 | 93.8 | 93.8 | Xantrex Technology3.3GT3.3-NA-DS-240-POS [240V]
Xantrex Technology | GT3.3N-NA-240/208 [240V] | Y | N | N | 3.3 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 3.3 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.52 | 3.3 | 1.52 | 100 | 250 | 400 | 0.33 | 0.66 | 0.99 | 1.65 | 2.475 | 3.3 | 91.9 | 95 | 95.7 | 95.9 | 95.9 | 95.5 | 95.6 | 91.4 | 94.7 | 95.5 | 95.9 | 95.7 | 95.4 | 95.5 | 89.8 | 93.6 | 94.8 | 95.4 | 95.3 | 95.2 | 95 | Xantrex Technology3.3GT3.3N-NA-240/208 [240V]
Xantrex Technology | GT3.8-NA-240/208 UL-05 [208V] | Y | N | N | 3.5 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 3.5 | 1 | 100 | 266 | 480 | 0.35 | 0.7 | 1.05 | 1.75 | 2.63 | 3.5 | 91.8 | 94.9 | 95.5 | 95.6 | 95.2 | 94.7 | 95.15 | 91.3 | 94.6 | 95.3 | 95.5 | 95.1 | 94.6 | 94.98 | 90 | 93.6 | 94.6 | 95.1 | 94.7 | 94.3 | 94.49 | Xantrex Technology3.5GT3.8-NA-240/208 UL-05 [208V]
Xantrex Technology | GT3.8-NA-240/208 UL-05 [240V] | Y | N | N | 3.8 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 3.8 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 3.8 | 1 | 100 | 266 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 92.5 | 95.2 | 95.8 | 95.9 | 95.6 | 95 | 95.51 | 92 | 95 | 95.6 | 95.7 | 95.5 | 94.9 | 95.37 | 90.8 | 94.1 | 95 | 95.3 | 95 | 94.6 | 94.85 | Xantrex Technology3.8GT3.8-NA-240/208 UL-05 [240V]
Xantrex Technology | GT3.8-NA-DS-240 [240V] | Y | N | N | 3.8 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 3.8 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 3.8 | 1 | 100 | 266 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93 | 95.2 | 95.7 | 95.7 | 95.4 | 94.5 | 95.3 | 92.3 | 95 | 95.5 | 95.6 | 95.3 | 94.6 | 95.2 | 91.2 | 94.2 | 94.8 | 95.1 | 95 | 94.3 | 94.7 | Xantrex Technology3.8GT3.8-NA-DS-240 [240V]
Xantrex Technology | GT3.8-NA-DS-240-POS [240V] | Y | N | N | 3.8 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter (positive ground) | 3.8 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 3.8 | 1 | 100 | 266 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 93 | 95.2 | 95.7 | 95.7 | 95.4 | 94.5 | 95.3 | 92.3 | 95 | 95.5 | 95.6 | 95.3 | 94.6 | 95.2 | 91.2 | 94.2 | 94.8 | 95.1 | 95 | 94.3 | 94.7 | Xantrex Technology3.8GT3.8-NA-DS-240-POS [240V]
Xantrex Technology | GT4.0N-NA-240/208 [208V] | Y | N | N | 3.8 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 3.8 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.99 | 3.8 | 0.99 | 100 | 300 | 480 | 0.38 | 0.76 | 1.14 | 1.9 | 2.85 | 3.8 | 91.7 | 94.8 | 95.5 | 95.7 | 95.4 | 95.1 | 95.3 | 91 | 94.6 | 95.3 | 95.6 | 95.4 | 94.9 | 95.2 | 90.2 | 93.6 | 94.7 | 95.1 | 95.1 | 94.7 | 94.7 | Xantrex Technology3.8GT4.0N-NA-240/208 [208V]
Xantrex Technology | GT4.0N-NA-240/208 [240V] | Y | N | N | 4.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 4 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1.1 | 4 | 1.1 | 100 | 300 | 480 | 0.4 | 0.8 | 1.2 | 2 | 3 | 4 | 92.2 | 95.1 | 95.8 | 96 | 95.8 | 95.5 | 95.7 | 91.6 | 94.9 | 95.7 | 95.9 | 95.8 | 95.3 | 95.5 | 90.7 | 94.2 | 95 | 95.5 | 95.4 | 95.1 | 95.1 | Xantrex Technology4GT4.0N-NA-240/208 [240V]
Xantrex Technology | SW5548 [120V] | Y | N | N | 5.5 kVA, 48Vdc, 120Vac, Trace Engr. batt bkp, sine wave Inverter (with GTI) | 4.265 | 120 | 91 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 34.1 |  |  | 100 | 53.2 | 60 | 0.4265 | 0.8529 | 1.279 | 2.132 | 3.198 | 4.265 | 92.9 | 94.7 | 94.4 | 92.2 | 90 | 87.1 | 91.2 | 92.1 | 94.2 | 94.2 | 92.3 | 89.6 | 86.2 | 90.9 | 90.1 | 93.4 | 93.6 | 92 | 89 | 86.4 | 90.3 | Xantrex Technology4.265SW5548 [120V]
Xantrex Technology | GT5.0-NA-240/208 [208V] | Y | N | N | 5.0 kW, 208 Vac, 195-600 Vdc Grid Tie Inverter | 4.5 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 4.5 | 1 | 100 | 300 | 480 | 0.45 | 0.9 | 1.35 | 2.25 | 3.375 | 4.5 | 92.1 | 94.9 | 95.5 | 95.5 | 94.9 | 94.3 | 95 | 91.8 | 94.7 | 95.3 | 95.4 | 94.9 | 94.3 | 94.9 | 90.5 | 93.9 | 94.6 | 95 | 94.7 | 94.2 | 94.5 | Xantrex Technology4.5GT5.0-NA-240/208 [208V]
Xantrex Technology | GT5.0-NA-240/208 [240V] | Y | N | N | 5.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 5 | 1 | 100 | 300 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.2 | 95.5 | 95.9 | 95.9 | 95.5 | 94.8 | 95.5 | 92.7 | 95.3 | 95.8 | 95.8 | 95.4 | 94.8 | 95.4 | 91.5 | 94.6 | 95.3 | 95.4 | 95.1 | 94.5 | 95 | Xantrex Technology5GT5.0-NA-240/208 [240V]
Xantrex Technology | GT5.0-NA-DS-240 [240V] | Y | N | N | 5.0 kW, 240 Vac, 195-600 Vdc Grid Tie Inverter | 5 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 1 | 5 | 1 | 100 | 300 | 480 | 0.5 | 1 | 1.5 | 2.5 | 3.75 | 5 | 93.6 | 95.7 | 96 | 96.1 | 95.5 | 94.8 | 95.6 | 93.2 | 95.6 | 95.9 | 95.9 | 95.5 | 94.8 | 95.5 | 92.3 | 94.8 | 95.5 | 95.6 | 95.2 | 94.6 | 95.2 | Xantrex Technology5GT5.0-NA-DS-240 [240V]
Xantrex Technology | PV10-208 [208V] | Y | N | N | 10 kW, 208 Vac, 3-phase Utility Interactive Inverter with 208 Vac Transformer | 10.19 | 208 | 90 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 203.3 |  |  | 330 | 368 | 480 | 1.02 | 2.04 | 3.06 | 5.1 | 7.64 | 10.19 | 78.5 | 86.5 | 89.2 | 91.8 | 92.8 | 92.9 | 91.3 | 77 | 84.7 | 88.3 | 91.1 | 91.7 | 92.3 | 90.3 | 73 | 82.9 | 86.8 | 89.4 | 90.7 | 90.7 | 88.9 | Xantrex Technology10.19PV10-208 [208V]
Xantrex Technology | PV10-480 [208V] | Y | N | N | 10 kW, 208 Vac, 3-phase Utility Interactive Inverter with 480 Vac Transformer | 10.24 | 208 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 114.2 |  |  | 330 | 368 | 480 | 1.02 | 2.05 | 3.07 | 5.12 | 7.68 | 10.24 | 83.3 | 89.6 | 91.9 | 93.5 | 94 | 93.9 | 93 | 82 | 88.8 | 91.2 | 92.8 | 93.4 | 93.3 | 92.3 | 79.4 | 86.1 | 89.1 | 91.1 | 91.9 | 91.7 | 90.6 | Xantrex Technology10.24PV10-480 [208V]
Xantrex Technology | PV15-480 [208V] | Y | N | N | 15 kW, 208 Vac, 3-phase Utility Interactive Inverter with 480 Vac Transformer | 15.28 | 208 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 171.6 |  |  | 330 | 368 | 480 | 1.53 | 3.06 | 4.58 | 7.64 | 11.46 | 15.28 | 79.3 | 89.3 | 91.5 | 93.2 | 93.7 | 93.6 | 92.5 | 78 | 88 | 90.6 | 92.3 | 92.9 | 92.7 | 91.6 | 74.1 | 85.6 | 88.7 | 90.6 | 91.6 | 90.7 | 90 | Xantrex Technology15.28PV15-480 [208V]
Xantrex Technology | PV15-208 [208V] | Y | N | N | 15 kW, 208 Vac, 3-phase Utility Interactive Inverter with 208 Vac Transformer | 15.31 | 208 | 91.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 165.2 |  |  | 330 | 368 | 480 | 1.53 | 3.06 | 4.59 | 7.66 | 11.49 | 15.31 | 83.3 | 89.7 | 91.6 | 93.4 | 93.8 | 93.8 | 92.8 | 81.7 | 88 | 90.8 | 92.4 | 93.2 | 92.9 | 92 | 78.3 | 85.5 | 88.7 | 90.6 | 91.7 | 90.9 | 90.2 | Xantrex Technology15.31PV15-208 [208V]
Xantrex Technology | PV20-480 [208V] | Y | N | N | 20 kW, 208 Vac, 3-phase Utility Interactive Inverter with 480 Vac Transformer | 20.32 | 208 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 203.3 |  |  | 330 | 368 | 480 | 2.03 | 4.06 | 6.1 | 10.16 | 15.24 | 20.32 | 85.1 | 90.7 | 92.6 | 93.5 | 93.8 | 93.7 | 93.1 | 84.4 | 89.6 | 91.7 | 93.4 | 93.5 | 92.9 | 92.7 | 81.9 | 87.6 | 90 | 91.3 | 91.7 | 90.5 | 90.8 | Xantrex Technology20.32PV20-480 [208V]
Xantrex Technology | PV20-208 [208V] | Y | N | N | 20 kW, 208 Vac, 3-phase Utility Interactive Inverter with 208 Vac Transformer | 20.49 | 208 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 210.6 |  |  | 330 | 368 | 480 | 2.05 | 4.1 | 6.15 | 10.25 | 15.37 | 20.49 | 84.7 | 90.3 | 92.3 | 93.8 | 94 | 93.8 | 93.2 | 83.9 | 89.7 | 91.6 | 93.1 | 93.4 | 93 | 92.5 | 81.3 | 87.1 | 89.9 | 91.3 | 91.7 | 90.7 | 90.7 | Xantrex Technology20.49PV20-208 [208V]
Xantrex Technology | PV30-480 [208V] | Y | N | N | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter with 480 Vac Transformer | 29.97 | 208 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 454.8 |  |  | 330 | 368 | 480 | 3 | 5.99 | 8.99 | 14.99 | 22.48 | 29.97 | 83.1 | 89.8 | 91.9 | 93.3 | 93.5 | 93.5 | 92.7 | 82.1 | 89.6 | 91.2 | 92.9 | 93.3 | 93.1 | 92.3 | 80 | 87.2 | 89.9 | 91.2 | 92.3 | 91.8 | 91 | Xantrex Technology29.97PV30-480 [208V]
Xantrex Technology | PV30-208 [208V] | Y | N | N | 30 kW, 208 Vac, 3-phase Utility Interactive Inverter with 208 Vac Transformer | 30.29 | 208 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 415 |  |  | 330 | 368 | 480 | 3.03 | 6.06 | 9.09 | 15.15 | 22.72 | 30.29 | 83.9 | 89.9 | 91.8 | 93.3 | 93.9 | 93.8 | 92.9 | 83 | 88.8 | 91 | 92.5 | 93.5 | 93.2 | 92.3 | 79.9 | 86.4 | 89.2 | 91.1 | 92.5 | 92 | 91 | Xantrex Technology30.29PV30-208 [208V]
Xantrex Technology | PV45-480 [208V] | Y | N | N | 45 kW, 208 Vac, 3-phase Utility Interactive Inverter with 480 Vac Transformer | 45.21 | 208 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 595.6 |  |  | 330 | 368 | 480 | 4.52 | 9.04 | 13.56 | 22.6 | 33.91 | 45.21 | 83.3 | 89.6 | 91.7 | 93.1 | 93.4 | 93.1 | 92.5 | 83.1 | 89.2 | 91.2 | 92.6 | 92.8 | 92.6 | 92 | 81.2 | 87.8 | 90 | 91.6 | 92 | 91.2 | 91 | Xantrex Technology45.21PV45-480 [208V]
Xantrex Technology | PV45-208 [208V] | Y | N | N | 45 kW, 208 Vac, 3-phase Utility Interactive Inverter with 208 Vac Transformer | 45.35 | 208 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 489 |  |  | 330 | 368 | 480 | 4.53 | 9.07 | 13.6 | 22.67 | 34.01 | 45.35 | 85 | 90.7 | 92.5 | 93.8 | 94.1 | 93.8 | 93.3 | 84.4 | 90.3 | 91.9 | 93.3 | 93.6 | 93.6 | 92.8 | 83.1 | 88.9 | 91 | 92.3 | 92.6 | 92.1 | 91.7 | Xantrex Technology45.35PV45-208 [208V]
Xantrex Technology | PV100S-480 [480V] | Y | N | N | 100 kW 480 Vac, 330-600 Vdc Inverter System with Automatic Transformer Disconnect | 100.3 | 480 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 94.6 |  |  | 330 | 368 | 480 | 10.03 | 20.06 | 30.09 | 50.15 | 75.22 | 100.3 | 85.1 | 90.6 | 92.6 | 93.9 | 94.1 | 93.7 | 93.3 | 84.9 | 90.3 | 92.4 | 93.8 | 93.8 | 93.4 | 93.1 | 83.4 | 89 | 91.2 | 92.6 | 92.8 | 92.3 | 92 | Xantrex Technology100.3PV100S-480 [480V]
Xantrex Technology | PV100S-208 [208V] | Y | N | N | 100 kW 208 Vac, 330-600 Vdc Inverter System with Automatic Transformer Disconnect | 101 | 208 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 86.6 |  |  | 330 | 368 | 480 | 10.1 | 20.21 | 30.31 | 50.52 | 75.78 | 101 | 84.3 | 90.4 | 92.6 | 93.8 | 94 | 93.8 | 93.2 | 84.5 | 90.3 | 92.4 | 93.6 | 93.8 | 93.6 | 93 | 83 | 88.9 | 91.2 | 92.4 | 92.7 | 92.3 | 91.9 | Xantrex Technology101PV100S-208 [208V]
Xantrex Technology | PV100S-480-HE [480V] | Y | N | N | 100 kW 480 Vac, 330-600 Vdc Inverter System with Automatic Transformer Disconnect | 101.1 | 480 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 96 |  |  | 300 | 345 | 480 | 10.11 | 20.22 | 30.33 | 50.56 | 75.83 | 101.1 | 89.4 | 93.4 | 94.8 | 95.7 | 95.8 | 95.6 | 95.3 | 88.7 | 93 | 94.4 | 95.3 | 95.5 | 95.3 | 94.9 | 87.3 | 91.9 | 93.5 | 94.5 | 94.8 | 94.6 | 94.1 | Xantrex Technology101.1PV100S-480-HE [480V]
Xantrex Technology | PV100S-208-HE [208V] | Y | N | N | 100 kW 208 Vac, 330-600 Vdc Inverter System with Automatic Transformer Disconnect | 101.3 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 100 |  |  | 300 | 345 | 480 | 10.13 | 20.26 | 30.39 | 50.65 | 75.97 | 101.3 | 89.6 | 93.4 | 94.8 | 95.6 | 95.7 | 95.2 | 95.2 | 88 | 93 | 94.4 | 95.2 | 95.3 | 95.1 | 94.8 | 87.4 | 91.8 | 93.4 | 94.5 | 94.7 | 94.4 | 94 | Xantrex Technology101.3PV100S-208-HE [208V]
Xantrex Technology | PV225S-480-P [480V] | Y | N | N | 225 kW 480 Vac, 330-600 Vdc Inverter System with Automatic Transformer Disconnect | 225.3 | 480 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 107 |  |  | 300 | 345 | 480 | 22.53 | 45.05 | 67.58 | 112.6 | 169 | 225.3 | 89.4 | 93.7 | 94.8 | 95.4 | 95.3 | 95.1 | 94.9 | 88.5 | 93.2 | 94.4 | 95 | 95 | 94.8 | 94.6 | 87.2 | 92.1 | 93.4 | 94.3 | 94.3 | 93.9 | 93.8 | Xantrex Technology225.3PV225S-480-P [480V]
Xantrex Technology | PV225S-480 [480V] | Y | N | N | 225 kW 480 Vac, 330-600 Vdc Inverter System with Automatic Transformer Disconnect | 227.3 | 480 | 93.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 103.8 |  |  | 330 | 368 | 480 | 22.73 | 45.46 | 68.19 | 113.7 | 170.5 | 227.3 | 88.5 | 92.7 | 94.1 | 94.9 | 94.9 | 94.6 | 94.4 | 87.4 | 92.1 | 93.6 | 94.7 | 94.5 | 94 | 94 | 84.5 | 89.7 | 91.5 | 92.6 | 92.6 | 92.5 | 92 | Xantrex Technology227.3PV225S-480 [480V]
Xiamen Kehua Hengsheng Co., Ltd. | SPI50K-BHV [480V] | N | Y | Y | 50 kW, 480 Vac Grid Support Utility Interactive Inverter | 49.825 | 480 | 98 | [11/27/2017] | [Main CPU(28335):V1] | 2018-10-15 | N | N |  | 2.8 |  |  | 540 | 695 | 850 | 4.983 | 9.966 | 14.949 | 24.915 | 37.3725 | 49.83 | 96.7703 | 96.973 | 97.3637 | 97.6805 | 97.7045 | 97.6785 | 97.5833 | 97.3153 | 98.4954 | 98.6189 | 98.7698 | 98.6611 | 98.2836 | 98.5979 | 96.5521 | 97.8957 | 98.1552 | 98.33 | 98.283 | 98.0881 | 98.1792 | Xiamen Kehua Hengsheng Co., Ltd.49.825SPI50K-BHV [480V] | 2018-01-02 | 2018-10-15
Xiamen Kehua Hengsheng Co., Ltd. | SPI60K-BHV [480V] | N | Y | Y | 60 kW, 480 Vac Grid Support Utility Interactive Inverter | 59.668 | 480 | 98 | [11/27/2017] | [Main CPU(28335):V1] | 2018-10-15 | N | N |  | 2.8 |  |  | 540 | 695 | 850 | 5.967 | 11.934 | 17.901 | 29.835 | 44.7525 | 59.67 | 97.0114 | 97.6315 | 97.6409 | 97.9122 | 97.5927 | 97.3714 | 97.6332 | 98.5714 | 98.8538 | 98.8416 | 98.7205 | 98.6058 | 98.3476 | 98.6563 | 97.7579 | 98.3751 | 98.523 | 98.3758 | 98.1648 | 97.9527 | 98.2357 | Xiamen Kehua Hengsheng Co., Ltd.59.668SPI60K-BHV [480V] | 2018-01-02 | 2018-10-15
Xslent Energy Technologies | XPX A1000 [120V] | Y | N | N | 180 W, 120 Vac, 1-phase Utility Interactive Smart Grid Inverter | 0.18 | 120 | 89 | No Information Submitted | No Information Submitted | Not Applicable | N | Y |  | 0.32 |  |  | 21 | 28 | 35 | 0.018 | 0.036 | 0.054 | 0.09 | 0.135 | 0.18 | 75.77 | 83.35 | 87.45 | 90.25 | 90.79 | 90.95 | 89.31 | 76.24 | 84.34 | 86.22 | 89.87 | 91.11 | 91.23 | 89.34 | 71.27 | 81.84 | 86.44 | 89.15 | 90.88 | 91.27 | 88.77 | Xslent Energy Technologies0.18XPX A1000 [120V]
Yaskawa Solectria Solar | PVI 1800-208 [208V] | Y | N | N | 1800 W, 208 Vac Grid-Tied Solar PV Inverter | 1.8 | 208 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.26 | 1.8 | 0.26 | 100 | 290 | 320 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 83.5 | 90 | 91.6 | 92.5 | 92.8 | 92.4 | 92 | 84 | 91.4 | 91.6 | 93.1 | 93.4 | 93.5 | 92.6 | 84.8 | 90.4 | 92.1 | 93.4 | 93.6 | 93.5 | 92.8 | Yaskawa Solectria Solar1.8PVI 1800-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 1800-240 [240V] | Y | N | N | 1800 W, 240 Vac Grid-Tied Solar PV Inverter | 1.8 | 240 | 92.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.14 | 1.8 | 0.14 | 100 | 290 | 320 | 0.18 | 0.36 | 0.54 | 0.9 | 1.35 | 1.8 | 83.6 | 89.6 | 91.2 | 92.3 | 92.6 | 92.3 | 91.8 | 84.1 | 90.1 | 91.8 | 93.2 | 93.4 | 93.2 | 92.6 | 85 | 90.1 | 92.2 | 93.3 | 93.5 | 93.3 | 92.8 | Yaskawa Solectria Solar1.8PVI 1800-240 [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 2500-208 [208V] | Y | N | N | 2500 W, 208 Vac Grid-Tied Solar PV Inverter | 2.5 | 208 | 92 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.1 | 2.5 | 0.1 | 100 | 290 | 320 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 85.3 | 90.2 | 91.6 | 92.1 | 91.8 | 90.8 | 91.4 | 86.7 | 90.7 | 92.3 | 92.7 | 92.6 | 92.1 | 92.2 | 86.6 | 91 | 92.4 | 93 | 92.5 | 92 | 92.3 | Yaskawa Solectria Solar2.5PVI 2500-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 2500-240 [240V] | Y | N | N | 2500 W, 240 Vac Grid-Tied Solar PV Inverter | 2.5 | 240 | 93 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.32 | 2.5 | 0.32 | 100 | 290 | 320 | 0.25 | 0.5 | 0.75 | 1.25 | 1.88 | 2.5 | 86.5 | 91.2 | 92.7 | 93.1 | 92.6 | 91.7 | 92.4 | 86.8 | 91.7 | 93.1 | 93.7 | 93.6 | 92.9 | 93.2 | 87.6 | 92.1 | 93.3 | 93.8 | 93.6 | 93 | 93.3 | Yaskawa Solectria Solar2.5PVI 2500-240 [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3000-208 [208V] | Y | N | N | 2.7 kW, 208 Vac Utility Interactive Inverter | 2.7 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 250 | 400 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 90.7 | 94.5 | 95.8 | 96.4 | 96.3 | 95.9 | 95.9 | 89.8 | 94.1 | 95.5 | 96.2 | 96.2 | 95.8 | 95.7 | 88.2 | 92.5 | 94.3 | 95.5 | 95.6 | 95.3 | 94.9 | Yaskawa Solectria Solar2.7PVI 3000-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3000-POS-208 [208V] | Y | N | N | 2.7 kW, 208 Vac Utility Interactive Inverter | 2.7 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 250 | 400 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 90.7 | 94.5 | 95.8 | 96.4 | 96.3 | 95.9 | 95.9 | 89.8 | 94.1 | 95.5 | 96.2 | 96.2 | 95.8 | 95.7 | 88.2 | 92.5 | 94.3 | 95.5 | 95.6 | 95.3 | 94.9 | Yaskawa Solectria Solar2.7PVI 3000-POS-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3000S [208V] | Y | N | N | 2.8 kW, 208 Vac Utility Interactive Inverter | 2.81 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.35 |  |  | 100 | 275 | 400 | 0.28 | 0.56 | 0.84 | 1.41 | 2.11 | 2.81 | 89.4 | 94.4 | 95.5 | 96.2 | 96.2 | 95.9 | 95.8 | 88.7 | 93.8 | 95.2 | 95.9 | 96 | 95.7 | 95.5 | 86.5 | 92.1 | 94 | 95.1 | 95.3 | 95.2 | 94.6 | Yaskawa Solectria Solar2.81PVI 3000S [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3000S-P [208V] | Y | N | N | 2.8 kW, 208 Vac Utility Interactive Inverter | 2.81 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.35 |  |  | 100 | 275 | 400 | 0.28 | 0.56 | 0.84 | 1.41 | 2.11 | 2.81 | 89.4 | 94.4 | 95.5 | 96.2 | 96.2 | 95.9 | 95.8 | 88.7 | 93.8 | 95.2 | 95.9 | 96 | 95.7 | 95.5 | 86.5 | 92.1 | 94 | 95.1 | 95.3 | 95.2 | 94.6 | Yaskawa Solectria Solar2.81PVI 3000S-P [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3000-240 [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 2.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 250 | 400 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.9 | 91.9 | 95.1 | 96.2 | 96.7 | 96.5 | 96.1 | 96.3 | 91.3 | 94.7 | 95.9 | 96.5 | 96.4 | 96 | 96.1 | 89.3 | 93.3 | 94.8 | 95.8 | 95.8 | 95.4 | 95.3 | Yaskawa Solectria Solar2.9PVI 3000-240 [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3000-POS-240 [240V] | Y | N | N | 3 kW, 240 Vac Utility Interactive Inverter | 2.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 250 | 400 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.9 | 91.9 | 95.1 | 96.2 | 96.7 | 96.5 | 96.1 | 96.3 | 91.3 | 94.7 | 95.9 | 96.5 | 96.4 | 96 | 96.1 | 89.3 | 93.3 | 94.8 | 95.8 | 95.8 | 95.4 | 95.3 | Yaskawa Solectria Solar2.9PVI 3000-POS-240 [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3000S [240V] | Y | N | N | 2.7 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.47 |  |  | 100 | 275 | 400 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 90.6 | 95 | 96 | 96.6 | 96.6 | 96.2 | 96.2 | 89.8 | 94.4 | 95.6 | 96.4 | 96.4 | 96 | 95.9 | 87.7 | 92.9 | 94.5 | 95.6 | 95.8 | 95.5 | 95.1 | Yaskawa Solectria Solar3.01PVI 3000S [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3000S-P [240V] | Y | N | N | 2.9 kW, 240 Vac Utility Interactive Inverter | 3.01 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.47 |  |  | 100 | 275 | 400 | 0.3 | 0.6 | 0.9 | 1.51 | 2.26 | 3.01 | 90.6 | 95 | 96 | 96.6 | 96.6 | 96.2 | 96.2 | 89.8 | 94.4 | 95.6 | 96.4 | 96.4 | 96 | 95.9 | 87.7 | 92.9 | 94.5 | 95.6 | 95.8 | 95.5 | 95.1 | Yaskawa Solectria Solar3.01PVI 3000S-P [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3800TL [208V] | Y | N | N | 3.8 kW, non-isolated PV Inverter | 3.32 | 208 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 1.14 |  |  | 100 | 380 | 500 | 0.33 | 0.66 | 1 | 1.66 | 2.49 | 3.32 | 94.6 | 96.1 | 97 | 97.3 | 97.1 | 96.8 | 97 | 96.3 | 96.9 | 97.8 | 97.9 | 98.1 | 97.5 | 97.8 | 95.9 | 95.8 | 96.9 | 97.4 | 97.4 | 97.1 | 97.2 | Yaskawa Solectria Solar3.32PVI 3800TL [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 4000-208 [208V] | Y | N | N | 3.4 kW, 208 Vac Utility Interactive Inverter | 3.4 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2 | Yaskawa Solectria Solar3.4PVI 4000-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 4000-POS-208 [208V] | Y | N | N | 3.4 kW, 208 Vac Utility Interactive Inverter | 3.4 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2 | Yaskawa Solectria Solar3.4PVI 4000-POS-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 4000S [208V] | Y | N | N | 3.4 kW, 208 Vac Utility Interactive Inverter | 3.51 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.35 |  |  | 100 | 275 | 400 | 0.35 | 0.7 | 1.05 | 1.76 | 2.63 | 3.51 | 91.3 | 95.1 | 96 | 96.3 | 96.1 | 95.4 | 95.9 | 90.4 | 94.7 | 95.7 | 96 | 95.9 | 95.3 | 95.6 | 88.4 | 93.3 | 94.7 | 95.3 | 95.3 | 94.7 | 94.8 | Yaskawa Solectria Solar3.51PVI 4000S [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 4000S-P [208V] | Y | N | N | 3.5 kW, 208 Vac Utility Interactive Inverter | 3.51 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.35 |  |  | 100 | 275 | 400 | 0.35 | 0.7 | 1.05 | 1.76 | 2.63 | 3.51 | 91.3 | 95.1 | 96 | 96.3 | 96.1 | 95.4 | 95.9 | 90.4 | 94.7 | 95.7 | 96 | 95.9 | 95.3 | 95.6 | 88.4 | 93.3 | 94.7 | 95.3 | 95.3 | 94.7 | 94.8 | Yaskawa Solectria Solar3.51PVI 4000S-P [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 3800TL [240V] | Y | N | N | 3.8 kW, non-isolated PV Inverter | 3.81 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 1.19 |  |  | 100 | 380 | 500 | 0.38 | 0.76 | 1.14 | 1.91 | 2.86 | 3.81 | 94.1 | 95.9 | 96.9 | 97.3 | 97.2 | 96.8 | 97 | 95.5 | 96.9 | 98 | 98.3 | 98.1 | 98 | 98 | 94.6 | 95.6 | 97.3 | 97.8 | 97.8 | 97.6 | 97.5 | Yaskawa Solectria Solar3.81PVI 3800TL [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 4000-240 [240V] | Y | N | N | 3.9 kW, 240 Vac Utility Interactive Inverter | 3.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2 | Yaskawa Solectria Solar3.9PVI 4000-240 [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 4000-POS-240 [240V] | Y | N | N | 3.9 kW, 240 Vac Utility Interactive Inverter | 3.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2 | Yaskawa Solectria Solar3.9PVI 4000-POS-240 [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 4000S [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 4.02 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.47 |  |  | 100 | 275 | 400 | 0.4 | 0.8 | 1.21 | 2.01 | 3.02 | 4.02 | 92.6 | 95.7 | 96.4 | 96.5 | 96.3 | 95.5 | 96.1 | 91.8 | 95.3 | 96.1 | 96.3 | 96.1 | 95.4 | 95.9 | 90 | 94.1 | 95.2 | 95.7 | 95.5 | 94.9 | 95.2 | Yaskawa Solectria Solar4.02PVI 4000S [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 4000S-P [240V] | Y | N | N | 4 kW, 240 Vac Utility Interactive Inverter | 4.02 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.47 |  |  | 100 | 275 | 400 | 0.4 | 0.8 | 1.21 | 2.01 | 3.02 | 4.02 | 92.6 | 95.7 | 96.4 | 96.5 | 96.3 | 95.5 | 96.1 | 91.8 | 95.3 | 96.1 | 96.3 | 96.1 | 95.4 | 95.9 | 90 | 94.1 | 95.2 | 95.7 | 95.5 | 94.9 | 95.2 | Yaskawa Solectria Solar4.02PVI 4000S-P [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5000-208 [208V] | Y | N | N | 4.3 kW, 208 Vac Utility Interactive Inverter | 4.3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.43 | 0.86 | 1.29 | 2.15 | 3.23 | 4.3 | 93.3 | 95.5 | 96.2 | 96.4 | 96.1 | 95.6 | 96 | 92.7 | 95.2 | 95.9 | 96.2 | 96 | 95.5 | 95.8 | 91.4 | 94.2 | 95.2 | 95.8 | 95.7 | 95.2 | 95.4 | Yaskawa Solectria Solar4.3PVI 5000-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5000-POS-208 [208V] | Y | N | N | 4.3 kW, 208 Vac Utility Interactive Inverter | 4.3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.43 | 0.86 | 1.29 | 2.15 | 3.23 | 4.3 | 93.3 | 95.5 | 96.2 | 96.4 | 96.1 | 95.6 | 96 | 92.7 | 95.2 | 95.9 | 96.2 | 96 | 95.5 | 95.8 | 91.4 | 94.2 | 95.2 | 95.8 | 95.7 | 95.2 | 95.4 | Yaskawa Solectria Solar4.3PVI 5000-POS-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5000S [208V] | Y | N | N | 4.3 kW, 208 Vac Utility Interactive Inverter | 4.4 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.47 |  |  | 100 | 275 | 400 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 92.9 | 95.8 | 96.5 | 96.8 | 96.6 | 95.9 | 96.4 | 92.2 | 95.3 | 96.2 | 96.4 | 96.2 | 95.5 | 96 | 90.1 | 93.9 | 95 | 95.7 | 95.6 | 95.2 | 95.2 | Yaskawa Solectria Solar4.4PVI 5000S [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5000S-P [208V] | Y | N | N | 4.3 kW, 208 Vac Utility Interactive Inverter | 4.4 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.47 |  |  | 100 | 275 | 400 | 0.44 | 0.88 | 1.32 | 2.2 | 3.3 | 4.4 | 92.9 | 95.8 | 96.5 | 96.8 | 96.6 | 95.9 | 96.4 | 92.2 | 95.3 | 96.2 | 96.4 | 96.2 | 95.5 | 96 | 90.1 | 93.9 | 95 | 95.7 | 95.6 | 95.2 | 95.2 | Yaskawa Solectria Solar4.4PVI 5000S-P [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5300-208 [208V] | Y | N | N | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.5 | 95.6 | 96.2 | 96.1 | 95.9 | 95.3 | 95.9 | 93 | 95.3 | 96 | 95.9 | 95.9 | 95.2 | 95.7 | 91.7 | 94.4 | 95.2 | 95.7 | 95.5 | 95 | 95.3 | Yaskawa Solectria Solar4.6PVI 5300-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5300-POS-208 [208V] | Y | N | N | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.5 | 95.6 | 96.2 | 96.1 | 95.9 | 95.3 | 95.9 | 93 | 95.3 | 96 | 95.9 | 95.9 | 95.2 | 95.7 | 91.7 | 94.4 | 95.2 | 95.7 | 95.5 | 95 | 95.3 | Yaskawa Solectria Solar4.6PVI 5300-POS-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5000-240 [240V] | Y | N | N | 4.6 kW, 208 Vac Utility Interactive Inverter | 4.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.49 | 0.98 | 1.47 | 2.45 | 3.68 | 4.9 | 93.9 | 96 | 96.5 | 96.6 | 96.2 | 95.6 | 96.2 | 93.4 | 95.7 | 96.3 | 96.5 | 96 | 95.4 | 96 | 92.1 | 94.8 | 95.7 | 96 | 95.8 | 95.2 | 95.6 | Yaskawa Solectria Solar4.9PVI 5000-240 [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5000-POS-240 [240V] | Y | N | N | 4.9 kW, 240 Vac Utility Interactive Inverter | 4.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.49 | 0.98 | 1.47 | 2.45 | 3.68 | 4.9 | 93.9 | 96 | 96.5 | 96.6 | 96.2 | 95.6 | 96.2 | 93.4 | 95.7 | 96.3 | 96.5 | 96 | 95.4 | 96 | 92.1 | 94.8 | 95.7 | 96 | 95.8 | 95.2 | 95.6 | Yaskawa Solectria Solar4.9PVI 5000-POS-240 [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5000S [240V] | Y | N | N | 4.9 kW, 240 Vac Utility Interactive Inverter | 5.01 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.47 |  |  | 100 | 275 | 400 | 0.5 | 1 | 1.5 | 2.51 | 3.76 | 5.01 | 93.9 | 96.1 | 96.6 | 96.7 | 96.4 | 95.7 | 96.3 | 92.7 | 95.8 | 96.4 | 96.5 | 96.2 | 95.6 | 96.1 | 91.2 | 94.7 | 95.7 | 96.1 | 95.9 | 95.4 | 95.7 | Yaskawa Solectria Solar5.01PVI 5000S [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5000S-P [240V] | Y | N | N | 5 kW, 240 Vac Utility Interactive Inverter | 5.01 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.47 |  |  | 100 | 275 | 400 | 0.5 | 1 | 1.5 | 2.51 | 3.76 | 5.01 | 93.9 | 96.1 | 96.6 | 96.7 | 96.4 | 95.7 | 96.3 | 92.7 | 95.8 | 96.4 | 96.5 | 96.2 | 95.6 | 96.1 | 91.2 | 94.7 | 95.7 | 96.1 | 95.9 | 95.4 | 95.7 | Yaskawa Solectria Solar5.01PVI 5000S-P [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5200TL [208V] | Y | N | N | 5.2 kVA, 1-phase, transformerless Utility Interactive Inverter | 5.2 | 208 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 1.31 |  |  | 100 | 380 | 500 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 93.6 | 95.6 | 96.3 | 97.2 | 97.1 | 96.8 | 96.8 | 95.2 | 96.6 | 97.5 | 98 | 98 | 97.7 | 97.7 | 93.6 | 96.3 | 97 | 97.7 | 97.7 | 97.5 | 97.4 | Yaskawa Solectria Solar5.2PVI 5200TL [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5200TL [240V] | Y | N | N | 5.2 kVA, 1-phase, transformerless Utility Interactive Inverter | 5.2 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 1.42 |  |  | 100 | 380 | 500 | 0.52 | 1.04 | 1.56 | 2.6 | 3.9 | 5.2 | 94 | 95.8 | 96.4 | 97.3 | 97.4 | 97.1 | 97 | 95.2 | 97 | 97.5 | 98.2 | 98.3 | 98.1 | 98 | 93.8 | 96.6 | 97.2 | 97.9 | 98 | 98 | 97.7 | Yaskawa Solectria Solar5.2PVI 5200TL [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5300-240 [240V] | Y | N | N | 5.3 kW, 240 Vac Utility Interactive Inverter | 5.3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 94.3 | 96.1 | 96.3 | 96.4 | 96 | 95.2 | 96 | 93.8 | 95.9 | 96.1 | 96.3 | 95.8 | 95.2 | 95.8 | 92.5 | 95 | 95.7 | 96 | 95.5 | 94.9 | 95.4 | Yaskawa Solectria Solar5.3PVI 5300-240 [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 5300-POS-240 [240V] | Y | N | N | 5.3 kW, 240 Vac Utility Interactive Inverter | 5.3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 94.3 | 96.1 | 96.3 | 96.4 | 96 | 95.2 | 96 | 93.8 | 95.9 | 96.1 | 96.3 | 95.8 | 95.2 | 95.8 | 92.5 | 95 | 95.7 | 96 | 95.5 | 94.9 | 95.4 | Yaskawa Solectria Solar5.3PVI 5300-POS-240 [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 6500-208 [208V] | Y | N | N | 6.43 kW, 208 Vac Utility Interactive Inverter | 6.43 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 100 | 275 | 400 | 0.643 | 1.286 | 1.929 | 3.215 | 4.823 | 6.43 | 93.3 | 95.6 | 96 | 96 | 95.6 | 94.8 | 95.6 | 92.9 | 95.4 | 95.9 | 95.9 | 95.5 | 94.8 | 95.5 | 91.6 | 94.8 | 95.4 | 95.6 | 95.2 | 94.6 | 95.1 | Yaskawa Solectria Solar6.43PVI 6500-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 6500-240 [240V] | Y | N | N | 6.43 kW, 240 Vac Utility Interactive Inverter | 6.45 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.65 |  |  | 100 | 275 | 400 | 0.645 | 1.29 | 1.935 | 3.225 | 4.838 | 6.45 | 93.5 | 95.9 | 96.3 | 96.3 | 96 | 95.4 | 96 | 93.1 | 95.7 | 96.2 | 96.3 | 96 | 95.3 | 95.9 | 91.8 | 95 | 95.6 | 95.9 | 95.7 | 95.2 | 95.5 | Yaskawa Solectria Solar6.45PVI 6500-240 [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 6500-277 [277V] | Y | N | N | 6.43 kW, 277 Vac Utility Interactive Inverter | 6.45 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.9 |  |  | 100 | 275 | 400 | 0.645 | 1.29 | 1.935 | 3.225 | 4.838 | 6.45 | 93.8 | 96.1 | 96.5 | 96.7 | 96.4 | 95.8 | 96.3 | 93.4 | 95.9 | 96.4 | 96.5 | 96.3 | 95.8 | 96.2 | 92 | 95.3 | 95.9 | 96.2 | 96 | 95.6 | 95.8 | Yaskawa Solectria Solar6.45PVI 6500-277 [277V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 6600TL [208V] | Y | N | N | 6.6 kVA, 1-phase, transformerless Utility Interactive Inverter | 6.6 | 208 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 1.23 |  |  | 100 | 380 | 500 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.4 | 96.1 | 97 | 97.2 | 96.9 | 96.2 | 96.8 | 95.9 | 96.9 | 97.8 | 98 | 97.7 | 97.3 | 97.7 | 95 | 96.4 | 97.4 | 97.7 | 97.6 | 97.1 | 97.4 | Yaskawa Solectria Solar6.6PVI 6600TL [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 6600TL [240V] | Y | N | N | 6.6 kVA, 1-phase, transformerless Utility Interactive Inverter | 6.6 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 1.45 |  |  | 100 | 380 | 500 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.3 | 96.2 | 96.9 | 97.4 | 97.2 | 96.8 | 97 | 96 | 97.3 | 97.9 | 98.3 | 98.2 | 97.9 | 98 | 95 | 96.8 | 97.6 | 98 | 98 | 97.7 | 97.7 | Yaskawa Solectria Solar6.6PVI 6600TL [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 7600TL [208V] | Y | N | N | 7.6 kVA, 1-phase, transformerless Utility Interactive Inverter | 6.6 | 208 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 1.23 |  |  | 100 | 380 | 500 | 0.66 | 1.32 | 1.98 | 3.3 | 4.95 | 6.6 | 94.4 | 96.1 | 97 | 97.2 | 96.9 | 96.2 | 96.8 | 95.9 | 96.9 | 97.8 | 98 | 97.7 | 97.3 | 97.7 | 95 | 96.4 | 97.4 | 97.7 | 97.6 | 97.1 | 97.4 | Yaskawa Solectria Solar6.6PVI 7600TL [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 7500-208 [208V] | Y | N | N | 7.43 kW, 208 Vac Utility Interactive Inverter | 7.43 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.52 |  |  | 100 | 275 | 400 | 0.743 | 1.486 | 2.229 | 3.715 | 5.573 | 7.43 | 94.1 | 96 | 96.2 | 96.1 | 95.4 | 94.6 | 95.6 | 93.7 | 95.7 | 96 | 96 | 95.3 | 94.5 | 95.5 | 92.5 | 95.1 | 95.6 | 95.6 | 95.1 | 94.3 | 95.1 | Yaskawa Solectria Solar7.43PVI 7500-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 7500-240 [240V] | Y | N | N | 7.43 kW, 240 Vac Utility Interactive Inverter | 7.45 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.68 |  |  | 100 | 275 | 400 | 0.745 | 1.49 | 2.235 | 3.725 | 5.588 | 7.45 | 94.3 | 96.2 | 96.5 | 96.5 | 95.9 | 95.2 | 96 | 93.9 | 96 | 96.3 | 96.3 | 95.8 | 95.1 | 95.9 | 92.7 | 95.4 | 95.9 | 96 | 95.5 | 94.9 | 95.5 | Yaskawa Solectria Solar7.45PVI 7500-240 [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 7500-277 [277V] | Y | N | N | 7.43 kW, 277 Vac Utility Interactive Inverter | 7.46 | 277 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.9 |  |  | 100 | 275 | 400 | 0.746 | 1.492 | 2.238 | 3.73 | 5.595 | 7.46 | 94.4 | 96.4 | 96.7 | 96.6 | 96.2 | 95.5 | 96.3 | 94 | 96.1 | 96.5 | 96.6 | 96.2 | 95.5 | 96.2 | 92.9 | 95.5 | 96.1 | 96.2 | 95.9 | 95.3 | 95.8 | Yaskawa Solectria Solar7.46PVI 7500-277 [277V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 7600TL [240V] | Y | N | N | 7.6 kVA, 1-phase, transformerless Utility Interactive Inverter | 7.6 | 240 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 1.43 |  |  | 100 | 380 | 500 | 0.76 | 1.52 | 2.28 | 3.8 | 5.7 | 7.6 | 95 | 96.4 | 97.3 | 97.4 | 97 | 96.4 | 97 | 96.3 | 97.4 | 98.1 | 98.3 | 98 | 97.7 | 98 | 95.5 | 97.2 | 97.7 | 98 | 97.9 | 97.5 | 97.7 | Yaskawa Solectria Solar7.6PVI 7600TL [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 10kW-208 [208V] | Y | N | N | 10 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 10.36 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 2.56 |  |  | 225 | 270 | 380 | 1.04 | 2.07 | 3.11 | 5.18 | 7.77 | 10.36 | 88.6 | 93.7 | 95 | 96.4 | 96.3 | 96.1 | 95.7 | 93.2 | 94.8 | 95.7 | 96.4 | 96.2 | 95.8 | 96 | 82.5 | 93.9 | 95.8 | 96.7 | 96.7 | 96.2 | 95.9 | Yaskawa Solectria Solar10.36PVI 10kW-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 10kW-480 [480V] | Y | N | N | 10 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 10.41 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 11.36 |  |  | 225 | 270 | 380 | 1.04 | 2.08 | 3.12 | 5.2 | 7.81 | 10.41 | 91.7 | 95.4 | 96 | 96.4 | 96.3 | 96.1 | 96.1 | 91.7 | 95.5 | 96.2 | 96.4 | 96.3 | 96.1 | 96.1 | 92.3 | 95.5 | 96.2 | 96.6 | 96.4 | 96.2 | 96.2 | Yaskawa Solectria Solar10.41PVI 10kW-480 [480V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 13 kW-208 [208V] | Y | N | N | 13 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 13.69 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 2.56 |  |  | 225 | 270 | 380 | 1.37 | 2.74 | 4.11 | 6.85 | 10.27 | 13.69 | 91.2 | 94.7 | 96.1 | 96.3 | 96.1 | 95.7 | 95.9 | 93.5 | 95.9 | 96.9 | 96.3 | 95.8 | 95.3 | 95.9 | 94.3 | 96.4 | 96.9 | 96.5 | 96.2 | 95.8 | 96.2 | Yaskawa Solectria Solar13.69PVI 13 kW-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 13 kW-480 [480V] | Y | N | N | 13 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 13.7 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 11.36 |  |  | 225 | 270 | 380 | 1.37 | 2.74 | 4.11 | 6.85 | 10.27 | 13.7 | 93.3 | 95.8 | 96.3 | 96.4 | 96.1 | 95.6 | 96 | 93.6 | 96 | 96.4 | 96.4 | 96.1 | 95.6 | 96 | 93.2 | 96.1 | 96.5 | 96.5 | 96.2 | 95.8 | 96.2 | Yaskawa Solectria Solar13.7PVI 13 kW-480 [480V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 14TL-208 | Y | N | N | Photovoltaic Inverter | 14 |  | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 4 |  |  | 300 | 385 | 540 | 1.4 | 2.8 | 4.2 | 7 | 10.5 | 14 | 94.9 | 95.4 | 95.6 | 95.6 | 95.2 | 94.7 | 95.3 | 95.7 | 96.5 | 96.9 | 96.8 | 96.5 | 96.1 | 96.6 | 93.7 | 96.8 | 95.9 | 96.2 | 96 | 95.6 | 96 | Yaskawa Solectria Solar14PVI 14TL-208 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 15kW-208 [208V] | Y | N | N | 15 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 15.05 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 2.56 |  |  | 225 | 270 | 380 | 1.5 | 3.01 | 4.51 | 7.52 | 11.28 | 15.05 | 92.2 | 95 | 96.4 | 96.3 | 95.9 | 95.4 | 95.8 | 92.2 | 95.7 | 96.4 | 96.3 | 95.7 | 95 | 95.7 | 92.1 | 95.8 | 96.5 | 96.5 | 96.3 | 95.3 | 96.1 | Yaskawa Solectria Solar15.05PVI 15kW-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 15kW-480 [480V] | Y | N | N | 15 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 15.35 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 11.36 |  |  | 225 | 270 | 380 | 1.54 | 3.07 | 4.61 | 7.68 | 11.51 | 15.35 | 93.9 | 96 | 96.4 | 96.3 | 96 | 95.3 | 96 | 94.2 | 96.2 | 96.4 | 96.4 | 96 | 95.3 | 96 | 94.1 | 96.2 | 96.6 | 96.5 | 96 | 95.5 | 96.1 | Yaskawa Solectria Solar15.35PVI 15kW-480 [480V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 20TL-480 | Y | N | N | Photovoltaic Inverter | 20 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 2 |  |  | 300 | 480 | 550 | 2 | 4 | 6 | 10 | 15 | 20 | 94.9 | 96.2 | 96.4 | 96.6 | 96.2 | 95.7 | 96.2 | 95.2 | 96.7 | 97.1 | 97.2 | 97.1 | 96.9 | 97 | 95.3 | 96.8 | 97.2 | 97.4 | 97.3 | 97.2 | 97.2 | Yaskawa Solectria Solar20PVI 20TL-480 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 23TL-480 | Y | N | N | 23kVA, 3-phase, transformerless Utility Interactive Inverter | 23 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 480 | 720 | 800 | 2.3 | 4.6 | 6.9 | 11.5 | 17.25 | 23 | 95.8 | 97 | 97.2 | 97.4 | 97.4 | 97.3 | 97.3 | 97 | 98.2 | 98.4 | 98.6 | 98.5 | 98.4 | 98.4 | 96.6 | 98 | 98.2 | 98.4 | 98.4 | 98.3 | 98.3 | Yaskawa Solectria Solar23PVI 23TL-480 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 28TL-480 | Y | N | N | 28kVA, 3-phase, transformerless Utility Interactive Inverter | 28 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.9 |  |  | 500 | 725 | 800 | 2.8 | 5.6 | 8.4 | 14 | 21 | 28 | 96.3 | 97.2 | 97.4 | 97.5 | 97.4 | 97.2 | 97.3 | 97.5 | 98.3 | 98.5 | 98.5 | 98.4 | 98.2 | 98.4 | 97.2 | 98.1 | 98.4 | 98.4 | 98.3 | 98.1 | 98.3 | Yaskawa Solectria Solar28PVI 28TL-480 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 36TL-480 | Y | N | N | 36kVA, 3-phase, transformerless Utility Interactive Inverter | 36 |  | 98 | Not Applicable | Not Applicable | Not Applicable | Y | N | Multiple Listing of CHINT POWER SYSTEMS America CPS SCA36KTL-DO/US and Canadian Solar Inc CSI-36KTL-CT Formerly "Solectria Renewables, LLC" | 0 |  |  | 540 | 730 | 800 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 95.5 | 96.8 | 97.2 | 97.5 | 97.5 | 97.3 | 97.3 | 97.4 | 98.3 | 98.5 | 98.5 | 98.5 | 98.3 | 98.4 | 97.1 | 98 | 98.3 | 98.4 | 98.3 | 98.2 | 98.3 | Yaskawa Solectria Solar36PVI 36TL-480 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 36TL-480 [480V] | N | Y | Y | 36 kVA , 480 Vac, 3-phase Grid Support Utility Interactive Inverter, non-isolated, 1000 Vdc | 36 | 480 | 98 | [8/2/2017] | [V0.60] | 2018-10-15 | N | N | Multiple Listing of CHINT POWER SYSTEMS America CPS SCA36KTL-DO/US and Canadian Solar Inc CSI-36KTL-CT Formerly "Solectria Renewables, LLC" | 0 |  |  | 540 | 730 | 800 | 3.6 | 7.2 | 10.8 | 18 | 27 | 36 | 95.5 | 96.8 | 97.2 | 97.5 | 97.5 | 97.3 | 97.3 | 97.4 | 98.3 | 98.5 | 98.5 | 98.5 | 98.3 | 98.4 | 97.1 | 98 | 98.3 | 98.4 | 98.3 | 98.2 | 98.3 | Yaskawa Solectria Solar36PVI 36TL-480 [480V] | 2017-10-01 | 2018-10-15
Yaskawa Solectria Solar | PVI 50 kW-240 | Y | N | N | Photovoltaic Inverter | 50 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 300 | 345 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 92.5 | 96.1 | 97.3 | 97.7 | 97.5 | 97.1 | 97.2 | 92.8 | 96.3 | 96.9 | 97.6 | 97.4 | 97.2 | 97.1 | 90.7 | 95.5 | 96.5 | 97 | 97 | 96.9 | 96.6 | Yaskawa Solectria Solar50PVI 50 kW-240 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 50 kW-480 [480V] | Y | N | N | 50 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 50 | 480 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 2.85 |  |  | 300 | 345 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.3 | 94.7 | 95.8 | 96.4 | 96.5 | 96.3 | 96.1 | 89.7 | 94.5 | 95.7 | 96.4 | 96.4 | 96.2 | 95.9 | 87.8 | 93.6 | 95 | 95.9 | 96.1 | 96 | 95.5 | Yaskawa Solectria Solar50PVI 50 kW-480 [480V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 50TL-480 [480V] | Y | Y | Y | 50 kVA , 480 Vac, 3-phase Grid Support Utility Interactive Inverter, non-isolated, 1000Vdc | 50 | 480 | 98.5 | [7/6/2017] | [V5.00] | 2018-10-15 | Y | N | Multiple Listing of CHINT POWER SYSTEMS America CPS SCA50KTL-DO/US and Canadian Solar Inc CSI-50KTL-CT Formerly "Solectria Renewables, LLC" | 0.88 |  |  | 480 | 730 | 850 | 5 | 10 | 15 | 25 | 37.5 | 50 | 95.6 | 96.8 | 97.5 | 97.9 | 97.8 | 97.7 | 97.6 | 98 | 98.6 | 98.8 | 98.8 | 98.7 | 98.6 | 98.7 | 97.7 | 98.5 | 98.6 | 98.7 | 98.6 | 98.5 | 98.6 | Yaskawa Solectria Solar50PVI 50TL-480 [480V] | 2017-10-01 | 2018-10-15
Yaskawa Solectria Solar | PVI-50-208 [208V] | Y | N | N |  | 50 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.49 |  |  | 300 | 345 | 480 | 5 | 10 | 15 | 25 | 37.5 | 50 | 90.4 | 95.3 | 96.5 | 96.6 | 96.6 | 96.4 | 96.3 | 91.4 | 95.3 | 96.2 | 96.6 | 96.7 | 96.3 | 96.3 | 88.8 | 94.6 | 96.1 | 96.3 | 96.4 | 96.2 | 95.9 | Yaskawa Solectria Solar50PVI-50-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 60kW-208 [208V] | Y | N | N | 60 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 60 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.49 |  |  | 300 | 345 | 480 | 6 | 12 | 18 | 30 | 45 | 60 | 92.5 | 95.7 | 96.4 | 96.6 | 96.5 | 96.2 | 96.3 | 91.9 | 95.5 | 96.5 | 96.7 | 96.5 | 96.1 | 96.3 | 90.2 | 95.2 | 96.1 | 96.4 | 96.2 | 95.9 | 96 | Yaskawa Solectria Solar60PVI 60kW-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 60kW-240 | Y | N | N | Photovoltaic Inverter | 60 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 300 | 345 | 480 | 6 | 12 | 18 | 30 | 45 | 60 | 93.6 | 96.8 | 97.2 | 97.8 | 97.5 | 97 | 97.3 | 93.6 | 96.7 | 97.6 | 97.4 | 97.2 | 97 | 97.1 | 92.1 | 96.1 | 96.9 | 97.2 | 96.9 | 96.6 | 96.7 | Yaskawa Solectria Solar60PVI 60kW-240 |  | 2018-02-15
Yaskawa Solectria Solar | PVI 60kW-480 [180V] | Y | N | N | 60 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 60 | 180 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 2.85 |  |  | 300 | 345 | 480 | 6 | 12 | 18 | 30 | 45 | 60 | 91.6 | 95.2 | 96.1 | 96.5 | 96.4 | 96.1 | 96.1 | 91.3 | 95.1 | 96.1 | 96.4 | 96.4 | 96.1 | 96.1 | 89.5 | 94.1 | 95.2 | 96 | 96 | 95.8 | 95.5 | Yaskawa Solectria Solar60PVI 60kW-480 [180V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 60TL-480 [480V] | Y | Y | Y | 60 kVA , 480 Vac, 3-phase Grid Support Utility Interactive Inverter, non-isolated, 1000Vdc | 60 | 480 | 98.5 | [7/6/2017] | [V5.00] | 2018-10-15 | Y | N | Multiple Listing of CHINT POWER SYSTEMS America CPS SCA60KTL-DO/US and Canadian Solar Inc CSI-60KTL-CT Formerly "Solectria Renewables, LLC" | 0.88 |  |  | 540 | 730 | 850 | 6 | 12 | 18 | 30 | 45 | 60 | 96.5 | 97.5 | 97.9 | 98.1 | 97.9 | 97.7 | 97.9 | 98.2 | 98.7 | 98.8 | 98.8 | 98.7 | 98.5 | 98.7 | 98 | 98.6 | 98.7 | 98.7 | 98.5 | 98.4 | 98.5 | Yaskawa Solectria Solar60PVI 60TL-480 [480V] | 2017-10-01 | 2018-10-15
Yaskawa Solectria Solar | XGI 1000-60 [480V] | Y | N | N | 60 kW, 1000 Vdc, 480 Vac Utility Interactive Inverter | 61.36 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.10909 |  |  | 580 | 715 | 850 | 6.1364 | 12.2728 | 18.4092 | 30.682 | 46.023 | 61.364 | 95.7 | 96.9 | 97.4 | 97.6 | 97.5 | 97.3 | 97.4 | 96.5 | 97.7 | 97.9 | 98 | 97.9 | 97.7 | 97.8 | 96.8 | 97.9 | 98 | 98.2 | 98.1 | 97.9 | 98 | Yaskawa Solectria Solar61.36XGI 1000-60 [480V] | 2018-02-15
Yaskawa Solectria Solar | XGI 1000-65 [480V] | Y | N | N | 65 kW, 1000 Vdc, 480 Vac Utility Interastive Inverter | 65.31 | 480 | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 0.10909 |  |  | 600 | 725 | 850 | 6.5311 | 13.0622 | 19.5933 | 32.6555 | 48.9833 | 65.311 | 96 | 97.2 | 97.4 | 97.6 | 97.5 | 97.2 | 97.4 | 96.7 | 97.8 | 97.9 | 98 | 97.9 | 97.7 | 97.9 | 97 | 98 | 98.1 | 98.2 | 98.1 | 97.9 | 98 | Yaskawa Solectria Solar65.31XGI 1000-65 [480V] | 2018-02-15
Yaskawa Solectria Solar | PVI 75 kW-208 [208V] | Y | N | N | 75 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 75 | 208 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 300 | 345 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 93.7 | 96.6 | 97 | 97.3 | 97.1 | 96.7 | 97 | 93.5 | 96.6 | 97.1 | 97.3 | 97 | 96.5 | 96.9 | 92.4 | 96.2 | 97 | 97.1 | 97 | 96.5 | 96.8 | Yaskawa Solectria Solar75PVI 75 kW-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 75 kW-240 [240V] | Y | N | N | 75 kW, 240 Vac Commercial Grid-Tied Solar PV Inverter | 75 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Formerly "Solectria Renewables, LLC" | 2 |  |  | 300 | 345 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 90.4 | 94.5 | 96 | 96.6 | 96.7 | 96.3 | 96.2 | 88 | 94.7 | 95.8 | 96.6 | 97.1 | 96.3 | 96.3 | 87.8 | 94.3 | 95.5 | 96.1 | 96.4 | 96.3 | 95.8 | Yaskawa Solectria Solar75PVI 75 kW-240 [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 75 kW-480 [480V] | Y | N | N | 75 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 75 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 2.71 |  |  | 300 | 345 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 93.8 | 96.4 | 97 | 97.2 | 97 | 96.6 | 96.9 | 93.3 | 96.4 | 96.9 | 97.2 | 96.9 | 96.4 | 96.8 | 92.6 | 96 | 96.6 | 96.9 | 96.9 | 96.5 | 96.6 | Yaskawa Solectria Solar75PVI 75 kW-480 [480V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 75 kW-480PE | Y | N | N | Photovoltaic Inverter | 75 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Formerly "Solectria Renewables, LLC" | 3.89 |  |  | 300 | 345 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 95.3 | 97.3 | 97.7 | 97.7 | 97.4 | 97.2 | 97.4 | 95.4 | 96.9 | 97.4 | 97.6 | 97.4 | 97.1 | 97.3 | 95.3 | 96.2 | 97.1 | 97.4 | 97.1 | 96.9 | 97 | Yaskawa Solectria Solar75PVI 75 kW-480PE |  | 2018-02-15
Yaskawa Solectria Solar | PVI 75-208-PE | Y | N | N | Photovoltaic Inverter | 75 |  | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 300 | 345 | 480 | 7.5 | 15 | 22.5 | 37.5 | 56.25 | 75 | 95.6 | 97.4 | 97.6 | 97.8 | 97.6 | 97.2 | 97.5 | 95.6 | 97.6 | 97.6 | 97.8 | 97.5 | 97.2 | 97.5 | 92.2 | 96.6 | 97.2 | 97.5 | 97.2 | 96.9 | 97 | Yaskawa Solectria Solar75PVI 75-208-PE |  | 2018-02-15
Yaskawa Solectria Solar | PVI 82 kW-480 [480V] | Y | N | N | 82 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 81.99 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 347 | 390 | 480 | 8.2 | 16.4 | 24.6 | 40.99 | 61.49 | 81.99 | 87.9 | 91.9 | 93.2 | 94.2 | 94.4 | 94.1 | 93.8 | 90.9 | 94.7 | 96.2 | 97.4 | 97.6 | 96.5 | 96.9 | 88.9 | 93.1 | 95.3 | 97.1 | 96.8 | 96.2 | 96.2 | Yaskawa Solectria Solar81.99PVI 82 kW-480 [480V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 82 kW-208 [208V] | Y | N | N | 82 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 83.3 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 346 | 390 | 480 | 8.33 | 16.66 | 24.99 | 41.65 | 62.48 | 83.3 | 84.8 | 91.2 | 93.3 | 94.8 | 95.2 | 94.8 | 94.2 | 87.3 | 93.4 | 94.8 | 95.1 | 95 | 94.8 | 94.6 | 87.6 | 92.7 | 94.1 | 94.8 | 95.6 | 95.4 | 94.8 | Yaskawa Solectria Solar83.3PVI 82 kW-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 85-208-PE | Y | N | N | Photovoltaic Inverter | 85 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 300 | 345 | 480 | 8.5 | 17 | 25.5 | 42.5 | 63.75 | 85 | 93.5 | 96.5 | 97 | 97.4 | 97.3 | 96.8 | 97.1 | 92.2 | 96.3 | 96.8 | 97.3 | 97.1 | 96.8 | 96.8 | 92.7 | 96 | 96.9 | 97.1 | 97.1 | 96.7 | 96.8 | Yaskawa Solectria Solar85PVI 85-208-PE |  | 2018-02-15
Yaskawa Solectria Solar | PVI 85kW-208 [208V] | Y | N | N | 85 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 85 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 300 | 345 | 480 | 8.5 | 17 | 25.5 | 42.5 | 63.75 | 85 | 89.7 | 94.6 | 95.8 | 96.6 | 96.4 | 96.3 | 96 | 88.4 | 94.1 | 95.4 | 96.2 | 96.2 | 96 | 95.7 | 86.9 | 94.5 | 95.6 | 96.3 | 96.5 | 96.1 | 95.8 | Yaskawa Solectria Solar85PVI 85kW-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 85kW-240 [240V] | Y | N | N | 85 kW, 240 Vac Commercial Grid-Tied Solar PV Inverter | 85 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 2 |  |  | 300 | 345 | 480 | 8.5 | 17 | 25.5 | 42.5 | 63.75 | 85 | 91.4 | 95.3 | 96.4 | 96.7 | 96.6 | 96 | 96.3 | 89.9 | 95.1 | 96.2 | 96.7 | 96.4 | 96.2 | 96.1 | 89 | 94.5 | 95.7 | 96.4 | 96.3 | 96.2 | 95.9 | Yaskawa Solectria Solar85PVI 85kW-240 [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 85kW-480 [480V] | Y | N | N | 85 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 85 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 2.86 |  |  | 300 | 345 | 480 | 8.5 | 17 | 25.5 | 42.5 | 63.75 | 85 | 90.4 | 95.2 | 96.3 | 96.7 | 96.7 | 96.3 | 96.3 | 90.1 | 94.9 | 96 | 96.7 | 96.8 | 96.5 | 96.3 | 89 | 94 | 96 | 96.7 | 96.9 | 96.3 | 96.3 | Yaskawa Solectria Solar85PVI 85kW-480 [480V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 95kW-480 [480V] | Y | N | N | 95 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 95.32 | 480 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 347 | 390 | 480 | 9.53 | 19.06 | 28.6 | 47.66 | 71.49 | 95.32 | 89 | 91.9 | 94 | 94.2 | 94.3 | 94 | 93.9 | 89.4 | 94.7 | 97.8 | 98 | 97.1 | 96 | 96.9 | 89.8 | 94.3 | 96.3 | 97.1 | 96.6 | 95.7 | 96.2 | Yaskawa Solectria Solar95.32PVI 95kW-480 [480V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 95kW-208 [208V] | Y | N | N | 95 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 95.47 | 208 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 347 | 390 | 480 | 9.55 | 19.09 | 28.64 | 47.73 | 71.6 | 95.47 | 86.1 | 92.6 | 94.4 | 94.8 | 94.8 | 94.3 | 94.3 | 89.3 | 93.6 | 94.6 | 95.1 | 94.9 | 94.4 | 94.6 | 89.5 | 93.7 | 94.2 | 94.8 | 95.3 | 94.7 | 94.7 | Yaskawa Solectria Solar95.47PVI 95kW-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 100 kW-208 [208V] | Y | N | N | 100 kW, 208 Vac Commercial Grid-Tied Solar PV Inverter | 100 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 1 |  |  | 300 | 354 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.2 | 95.3 | 96.2 | 96.5 | 96.4 | 95.9 | 96.1 | 90.3 | 94.7 | 95.9 | 96.2 | 96.1 | 95.8 | 95.8 | 90.2 | 95 | 95.9 | 96.4 | 96.3 | 95.9 | 95.9 | Yaskawa Solectria Solar100PVI 100 kW-208 [208V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 100 kW-240 [240V] | Y | N | N | 100 kW, 240 Vac Commercial Grid-Tied Solar PV Inverter | 100 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Formerly "Solectria Renewables, LLC" | 2 |  |  | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 91.8 | 95.6 | 96.5 | 96.7 | 96.3 | 95.6 | 96.2 | 92 | 95.6 | 96.3 | 96.9 | 96.3 | 96.5 | 96.2 | 91.2 | 94.9 | 96 | 96.7 | 96.3 | 95.9 | 96 | Yaskawa Solectria Solar100PVI 100 kW-240 [240V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 100 kW-480 [480V] | Y | N | N | 100 kW, 480 Vac Commercial Grid-Tied Solar PV Inverter | 100 | 480 | 96.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 2.86 |  |  | 300 | 354 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 92.1 | 95.6 | 96.4 | 96.8 | 96.6 | 95.9 | 96.3 | 91.2 | 95.3 | 96.4 | 96.8 | 96.6 | 96.2 | 96.3 | 90.3 | 95.1 | 96.5 | 96.9 | 96.4 | 96.1 | 96.2 | Yaskawa Solectria Solar100PVI 100 kW-480 [480V] |  | 2018-02-15
Yaskawa Solectria Solar | PVI 100-208-PE | Y | N | N | Photovoltaic Inverter | 100 |  | 97 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Formerly "Solectria Renewables, LLC" | 0.5 |  |  | 300 | 345 | 480 | 10 | 20 | 30 | 50 | 75 | 100 | 94 | 96.8 | 97.3 | 97.3 | 97 | 96.4 | 97 | 94.4 | 96.5 | 97.2 | 97.2 | 97.1 | 96.4 | 97 | 93.6 | 96.3 | 97 | 97 | 96.9 | 96.4 | 96.7 | Yaskawa Solectria Solar100PVI 100-208-PE |  | 2018-02-15
Yaskawa Solectria Solar | XGI 1500-150/166 [600V] | Y | N | N | SOLECTRIA XGI 1500 UTILITY INVERTERS, 1500VDC, 3-PHASE 600VAC OUTPUT | 150 | 600 | 98.5 | No Information Submitted | No Information Submitted | Not Applicable | N | N |  | 2.75 |  |  | 860 | 1100 | 1250 | 15 | 30 | 45 | 75 | 112.5 | 150 | 98.4688 | 98.9332 | 98.9862 | 98.8872 | 98.8088 | 98.718 | 98.8346 | 98.1948 | 98.2298 | 98.5054 | 98.5424 | 98.4976 | 98.38 | 98.4766 | 98.2596 | 98.2596 | 98.2786 | 98.3684 | 98.298 | 98.178 | 98.301 | Yaskawa Solectria Solar150XGI 1500-150/166 [600V] | 2018-11-01
Yaskawa Solectria Solar | SGI 225-480 [480V] | Y | N | N | 225 kW, 480 Vac Utility Scale Grid-Tied Smartgrid PV Inverter | 230.1 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 28 |  |  | 300 | 360 | 480 | 23.01 | 46.03 | 69.04 | 115.1 | 172.6 | 230.1 | 95.16 | 97.39 | 97.82 | 97.99 | 97.88 | 97.7 | 97.76 | 94.02 | 96.8 | 97.47 | 97.76 | 97.76 | 97.61 | 97.52 | 93.06 | 96.24 | 97.21 | 97.56 | 97.66 | 97.51 | 97.32 | Yaskawa Solectria Solar230.1SGI 225-480 [480V] |  | 2018-02-15
Yaskawa Solectria Solar | SGI 250-480 [480V] | Y | N | N | 250 kW, 480 Vac Utility Scale Grid-Tied Smartgrid PV Inverter | 258.2 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 28 |  |  | 300 | 360 | 480 | 25.82 | 51.63 | 77.45 | 129.1 | 193.6 | 258.2 | 95.48 | 97.54 | 97.89 | 97.98 | 97.84 | 97.75 | 97.76 | 94.71 | 97.15 | 97.63 | 97.79 | 97.75 | 97.56 | 97.58 | 93.93 | 96.47 | 97.32 | 97.59 | 97.62 | 97.44 | 97.36 | Yaskawa Solectria Solar258.2SGI 250-480 [480V] |  | 2018-02-15
Yaskawa Solectria Solar | SGI 266-480 [480V] | Y | N | N | 266 kW, 480 Vac Utility Scale Grid-Tied Smartgrid PV Inverter | 269.8 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 28 |  |  | 300 | 360 | 480 | 26.98 | 53.97 | 80.95 | 134.9 | 202.4 | 269.8 | 95.79 | 97.59 | 97.9 | 97.96 | 97.81 | 97.68 | 97.75 | 94.99 | 97.15 | 97.66 | 97.83 | 97.72 | 97.49 | 97.59 | 93.93 | 96.88 | 97.39 | 97.6 | 97.59 | 97.38 | 97.38 | Yaskawa Solectria Solar269.8SGI 266-480 [480V] |  | 2018-02-15
Yaskawa Solectria Solar | SGI 300-480 [480V] | Y | N | N | 300 kW, 480 Vac Utility Scale Grid-Tied Smartgrid PV Inverter | 304.9 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 28 |  |  | 300 | 360 | 480 | 30.49 | 60.97 | 91.46 | 152.4 | 228.6 | 304.9 | 95.97 | 97.73 | 97.9 | 97.88 | 97.72 | 97.49 | 97.7 | 95.43 | 97.36 | 97.67 | 97.76 | 97.7 | 97.41 | 97.58 | 94.51 | 97.07 | 97.49 | 97.66 | 97.52 | 97.2 | 97.39 | Yaskawa Solectria Solar304.9SGI 300-480 [480V] |  | 2018-02-15
Yaskawa Solectria Solar | SGI 500XT | Y | N | N | Photovoltaic Inverter | 500 |  | 98 | No Information Submitted | No Information Submitted | Not Applicable | N | N | Formerly "Solectria Renewables, LLC" | 39.82 |  |  | 300 | 345 | 480 | 50 | 100 | 150 | 250 | 375 | 500 | 96.1 | 97.7 | 98 | 98.1 | 98 | 97.7 | 97.9 | 95.7 | 97.4 | 97.8 | 98 | 98 | 97.6 | 97.8 | 94.9 | 97.3 | 97.6 | 97.9 | 97.8 | 97.7 | 97.7 | Yaskawa Solectria Solar500SGI 500XT |  | 2018-02-15
Yaskawa Solectria Solar | SGI 500-480 [480V] | Y | N | N | 500 kW, 480 Vac Utility Scale Grid-Tied Smartgrid PV Inverter | 500.8 | 480 | 97 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 32 |  |  | 300 | 360 | 480 | 50.08 | 100.2 | 150.2 | 250.4 | 375.6 | 500.8 | 95.11 | 97.42 | 97.87 | 97.49 | 97.31 | 96.84 | 97.31 | 94.53 | 96.87 | 97.34 | 97.51 | 97.28 | 96.94 | 97.19 | 93.76 | 96.4 | 97 | 97.2 | 97.09 | 96.82 | 96.92 | Yaskawa Solectria Solar500.8SGI 500-480 [480V] |  | 2018-02-15
Yaskawa Solectria Solar | SGI 500XTM [380V] | Y | Y | N | 500 kW, 1000 Vdc, 380 Vac, 3-Phase Grid Support Utility Interactive Inverter | 507 | 380 | 96.5 | [01/09/2018] | [D003 Checksum- D9E00BD0] | Not Applicable | N | N | Efficiency data is inclusive of three Phase transformer from the CSA C802.2 table with transformer efficiency of 98.8%. | 88.78 |  |  | 545 | 615 | 820 | 50.7 | 101.4 | 152.1 | 253.5 | 380.25 | 507 | 93.6 | 96.1 | 96.7 | 97.1 | 97.2 | 97.1 | 96.9 | 93.2 | 95.8 | 96.5 | 96.9 | 97 | 97 | 96.7 | 92.1 | 95.3 | 96.1 | 96.6 | 96.8 | 96.8 | 96.4 | Yaskawa Solectria Solar507SGI 500XTM [380V] | 2018-02-15
Yaskawa Solectria Solar | SGI 499PE [480V] | Y | N | N | 499 kW, 480 Vac Utility Scale Grid-Tied PV Inverter | 508.2 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 17 |  |  | 300 | 360 | 480 | 50.82 | 101.6 | 152.5 | 254.1 | 381.1 | 508.2 | 97.5 | 98.2 | 98.2 | 97.8 | 97.4 | 97 | 97.6 | 96.7 | 98.3 | 98.2 | 97.6 | 97.1 | 96.5 | 97.3 | 97.6 | 97.9 | 97.7 | 97.6 | 96.9 | 96.4 | 97.2 | Yaskawa Solectria Solar508.2SGI 499PE [480V] |  | 2018-02-15
Yaskawa Solectria Solar | SGI 500PE [480V] | Y | N | N | 500 kW, 480 Vac Utility Scale Grid-Tied PV Inverter | 508.2 | 480 | 97.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N | Formerly "Solectria Renewables, LLC" | 17 |  |  | 300 | 360 | 480 | 50.82 | 101.6 | 152.5 | 254.1 | 381.1 | 508.2 | 97.5 | 98.2 | 98.2 | 97.8 | 97.4 | 97 | 97.6 | 96.7 | 98.3 | 98.2 | 97.6 | 97.1 | 96.5 | 97.3 | 97.6 | 97.9 | 97.7 | 97.6 | 96.9 | 96.4 | 97.2 | Yaskawa Solectria Solar508.2SGI 500PE [480V] |  | 2018-02-15
Yaskawa Solectria Solar | SGI 750XTM [380V] | Y | Y | N | 750 kW, 1000 Vdc, 380Vac, 3-Phase Grid Support Utility Interactive Inverter | 753.2 | 380 | 96.5 | [01/09/2018] | [D003 Checksum- D9E00BD0] | Not Applicable | N | N | Efficiency data is inclusive of three Phase transformer from the CSA C802.2 table with transformer efficiency of 98.8%. | 122.55 |  |  | 545 | 615 | 820 | 75.32 | 150.64 | 225.96 | 376.6 | 564.9 | 753.2 | 94 | 96.2 | 96.7 | 97 | 97 | 96.9 | 96.8 | 93.7 | 96.2 | 96.7 | 97.1 | 97.1 | 97 | 96.9 | 91.9 | 95.3 | 96.2 | 96.7 | 96.7 | 96.8 | 96.4 | Yaskawa Solectria Solar753.2SGI 750XTM [380V] | 2018-02-15
Yes! Solar | ES3000 [208V] | Y | N | N | 2.7 kW 208 Vac Utility Interactive Inverter | 2.7 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 90.7 | 94.5 | 95.8 | 96.4 | 96.3 | 95.9 | 95.9 | 89.8 | 94.1 | 95.5 | 96.2 | 96.2 | 95.8 | 95.7 | 88.2 | 92.5 | 94.3 | 95.5 | 95.6 | 95.3 | 94.9 | Yes! Solar2.7ES3000 [208V]
Yes! Solar | ES3000P [208V] | Y | N | N | 2.7 kW 208 Vac Utility Interactive Inverter | 2.7 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.27 | 0.54 | 0.81 | 1.35 | 2.03 | 2.7 | 90.7 | 94.5 | 95.8 | 96.4 | 96.3 | 95.9 | 95.9 | 89.8 | 94.1 | 95.5 | 96.2 | 96.2 | 95.8 | 95.7 | 88.2 | 92.5 | 94.3 | 95.5 | 95.6 | 95.3 | 94.9 | Yes! Solar2.7ES3000P [208V]
Yes! Solar | ES3000 [240V] | Y | N | N | 2.9 kW 240 Vac Utility Interactive Inverter | 2.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.9 | 91.9 | 95.1 | 96.2 | 96.7 | 96.5 | 96.1 | 96.3 | 91.3 | 94.7 | 95.9 | 96.5 | 96.4 | 96 | 96.1 | 89.3 | 93.3 | 94.8 | 95.8 | 95.8 | 95.4 | 95.3 | Yes! Solar2.9ES3000 [240V]
Yes! Solar | ES3000P [240V] | Y | N | N | 2.9 kW 240 Vac Utility Interactive Inverter | 2.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.29 | 0.58 | 0.87 | 1.45 | 2.18 | 2.9 | 91.9 | 95.1 | 96.2 | 96.7 | 96.5 | 96.1 | 96.3 | 91.3 | 94.7 | 95.9 | 96.5 | 96.4 | 96 | 96.1 | 89.3 | 93.3 | 94.8 | 95.8 | 95.8 | 95.4 | 95.3 | Yes! Solar2.9ES3000P [240V]
Yes! Solar | ES4000 [208V] | Y | N | N | 3.4 kW 208 Vac Utility Interactive Inverter | 3.4 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2 | Yes! Solar3.4ES4000 [208V]
Yes! Solar | ES4000P [208V] | Y | N | N | 3.4 kW 208 Vac Utility Interactive Inverter | 3.4 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.34 | 0.68 | 1.02 | 1.7 | 2.55 | 3.4 | 92.4 | 95.4 | 96.3 | 96.5 | 96.1 | 95.3 | 96 | 91.8 | 95.1 | 96 | 96.3 | 96 | 95.2 | 95.8 | 90.1 | 93.8 | 95.1 | 95.7 | 95.5 | 94.9 | 95.2 | Yes! Solar3.4ES4000P [208V]
Yes! Solar | ES4000 [240V] | Y | N | N | 3.9 kW 240 Vac Utility Interactive Inverter | 3.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2 | Yes! Solar3.9ES4000 [240V]
Yes! Solar | ES4000P [240V] | Y | N | N | 3.9 kW 240 Vac Utility Interactive Inverter | 3.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 250 | 400 | 0.39 | 0.78 | 1.17 | 1.95 | 2.93 | 3.9 | 93 | 95.7 | 96.5 | 96.7 | 96.1 | 95.5 | 96.1 | 92.9 | 95.6 | 96.4 | 96.5 | 96 | 95.4 | 96 | 90 | 93.7 | 95.2 | 95.7 | 95.5 | 95 | 95.2 | Yes! Solar3.9ES4000P [240V]
Yes! Solar | ES5000 [208V] | Y | N | N | 4.3 kW 208 Vac Utility Interactive Inverter | 4.3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.43 | 0.86 | 1.29 | 2.15 | 3.23 | 4.3 | 93.3 | 95.5 | 96.2 | 96.4 | 96.1 | 95.6 | 96 | 92.7 | 95.2 | 95.9 | 96.2 | 96 | 95.5 | 95.8 | 91.4 | 94.2 | 95.2 | 95.8 | 95.7 | 95.2 | 95.4 | Yes! Solar4.3ES5000 [208V]
Yes! Solar | ES5000P [208V] | Y | N | N | 4.3 kW 208 Vac Utility Interactive Inverter | 4.3 | 208 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.43 | 0.86 | 1.29 | 2.15 | 3.23 | 4.3 | 93.3 | 95.5 | 96.2 | 96.4 | 96.1 | 95.6 | 96 | 92.7 | 95.2 | 95.9 | 96.2 | 96 | 95.5 | 95.8 | 91.4 | 94.2 | 95.2 | 95.8 | 95.7 | 95.2 | 95.4 | Yes! Solar4.3ES5000P [208V]
Yes! Solar | ES5400 [208V] | Y | N | N | 4.6 kW 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.5 | 95.6 | 96.2 | 96.1 | 95.9 | 95.3 | 95.9 | 93 | 95.3 | 96 | 95.9 | 95.9 | 95.2 | 95.7 | 91.7 | 94.4 | 95.2 | 95.7 | 95.5 | 95 | 95.3 | Yes! Solar4.6ES5400 [208V]
Yes! Solar | ES5400P [208V] | Y | N | N | 4.6 kW 208 Vac Utility Interactive Inverter | 4.6 | 208 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.46 | 0.92 | 1.38 | 2.3 | 3.45 | 4.6 | 93.5 | 95.6 | 96.2 | 96.1 | 95.9 | 95.3 | 95.9 | 93 | 95.3 | 96 | 95.9 | 95.9 | 95.2 | 95.7 | 91.7 | 94.4 | 95.2 | 95.7 | 95.5 | 95 | 95.3 | Yes! Solar4.6ES5400P [208V]
Yes! Solar | ES5000 [240V] | Y | N | N | 4.9 kW 240 Vac Utility Interactive Inverter | 4.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.49 | 0.98 | 1.47 | 2.45 | 3.68 | 4.9 | 93.9 | 96 | 96.5 | 96.6 | 96.2 | 95.6 | 96.2 | 93.4 | 95.7 | 96.3 | 96.5 | 96 | 95.4 | 96 | 92.1 | 94.8 | 95.7 | 96 | 95.8 | 95.2 | 95.6 | Yes! Solar4.9ES5000 [240V]
Yes! Solar | ES5000P [240V] | Y | N | N | 4.9 kW 240 Vac Utility Interactive Inverter | 4.9 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.49 | 0.98 | 1.47 | 2.45 | 3.68 | 4.9 | 93.9 | 96 | 96.5 | 96.6 | 96.2 | 95.6 | 96.2 | 93.4 | 95.7 | 96.3 | 96.5 | 96 | 95.4 | 96 | 92.1 | 94.8 | 95.7 | 96 | 95.8 | 95.2 | 95.6 | Yes! Solar4.9ES5000P [240V]
Yes! Solar | ES5400 [240V] | Y | N | N | 5.3 kW 240 Vac Utility Interactive Inverter | 5.3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 94.3 | 96.1 | 96.3 | 96.4 | 96 | 95.2 | 96 | 93.8 | 95.9 | 96.1 | 96.3 | 95.8 | 95.2 | 95.8 | 92.5 | 95 | 95.7 | 96 | 95.5 | 94.9 | 95.4 | Yes! Solar5.3ES5400 [240V]
Yes! Solar | ES5400P [240V] | Y | N | N | 5.3 kW 240 Vac Utility Interactive Inverter | 5.3 | 240 | 96 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.5 |  |  | 100 | 275 | 400 | 0.53 | 1.06 | 1.59 | 2.65 | 3.98 | 5.3 | 94.3 | 96.1 | 96.3 | 96.4 | 96 | 95.2 | 96 | 93.8 | 95.9 | 96.1 | 96.3 | 95.8 | 95.2 | 95.8 | 92.5 | 95 | 95.7 | 96 | 95.5 | 94.9 | 95.4 | Yes! Solar5.3ES5400P [240V]
Zhongli Talesun Solar | TAC208/240 [208V] | Y | N | N | 240 W, 208 Vac Inverter | 0.24 | 208 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Zhongli Talesun Solar0.24TAC208/240 [208V]
Zhongli Talesun Solar | TAC208/240 [240V] | Y | N | N | 240 W, 240 Vac Inverter | 0.24 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | N | Y | This component is specific to ACPV modules and is not available as an individual unit. | 0.15 |  |  | 25 | 32 | 37 | 0.02 | 0.05 | 0.07 | 0.12 | 0.18 | 0.24 | 90.9 | 94.5 | 95.6 | 95 | 95 | 94.6 | 94.9 | 89.6 | 94.6 | 95.1 | 95.2 | 95.3 | 95.1 | 95 | 86.8 | 93.6 | 94 | 94.8 | 95.2 | 95.4 | 94.6 | Zhongli Talesun Solar0.24TAC208/240 [240V]
Zigor | Sunzet 2 TL-US [240V] | Y | N | N | 2110 W, 240 Vac Utility Interactive Inverter | 2.11 | 240 | 94.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.21 | 0.42 | 0.63 | 1.06 | 1.58 | 2.11 | 85.3 | 91.6 | 92.9 | 94.3 | 94.6 | 94.5 | 93.8 | 82.1 | 91.9 | 94.2 | 95.6 | 96.1 | 96.4 | 95 | 82.2 | 91.5 | 93.8 | 95.6 | 96.1 | 96.3 | 95 | Zigor2.11Sunzet 2 TL-US [240V]
Zigor | Sunzet 3 TL-US [240V] | Y | N | N | 3180 W, 240 Vac Utility Interactive Inverter | 3.18 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.25 |  |  | 100 | 375 | 400 | 0.32 | 0.64 | 0.95 | 1.59 | 2.39 | 3.18 | 88.8 | 92.9 | 94.1 | 94.6 | 94.3 | 94 | 94 | 88.8 | 94.4 | 95.3 | 96.2 | 96.3 | 95.9 | 95.7 | 89.5 | 93.7 | 95.3 | 96.2 | 96.3 | 96.1 | 95.7 | Zigor3.18Sunzet 3 TL-US [240V]
Zigor | SUNZET4-USA [240V] | Y | N | N | 4000 W, 240 Vac Utility Interactive Inverter | 4.03 | 240 | 95 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.19 |  |  | 100 | 310 | 440 | 0.4 | 0.81 | 1.21 | 2.02 | 3.02 | 4.03 | 91.6 | 94.5 | 95.2 | 95.3 | 95 | 93.9 | 94.9 | 90.2 | 94.5 | 95.5 | 95.8 | 95.6 | 95 | 95.3 | 87.4 | 92.8 | 94 | 95 | 95.2 | 94.6 | 94.5 | Zigor4.03SUNZET4-USA [240V]
Zigor | SUNZET 4 TL-US [240V] | Y | N | N | 4100 W, 240 Vac Utility Interactive Inverter | 4.16 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.42 | 0.83 | 1.25 | 2.08 | 3.12 | 4.16 | 90.6 | 93.8 | 94.5 | 94.8 | 94.6 | 94.2 | 94.4 | 91.4 | 95 | 95.7 | 96.1 | 96.2 | 95.9 | 95.9 | 90.7 | 94.7 | 95.5 | 96.1 | 96.1 | 95.9 | 95.7 | Zigor4.16SUNZET 4 TL-US [240V]
Zigor | SUNZET 5 TL-US [240V] | Y | N | N | 5000 W, 240 Vac Utility Interactive Inverter | 5.24 | 240 | 95.5 | No Information Submitted | No Information Submitted | Not Applicable | Y | N |  | 0.2 |  |  | 100 | 380 | 400 | 0.52 | 1.05 | 1.57 | 2.62 | 3.93 | 5.24 | 91.8 | 94.1 | 94.6 | 94.7 | 94.3 | 93.5 | 94.3 | 92.5 | 95.1 | 96.1 | 96.2 | 95.9 | 95.6 | 95.8 | 92.3 | 95.3 | 95.8 | 96.1 | 95.9 | 95.5 | 95.8 | Zigor5.24SUNZET 5 TL-US [240V]

## Dropdown (hidden)
'ABB MICRO-0.25-I-OUTD-US-240 [240V],N,96,Y'
'ABB MICRO-0.3HV-I-OUTD-US-208 [208V],N,96,Y'
'ABB MICRO-0.3HV-I-OUTD-US-240 [240V],N,96,Y'
'ABB MICRO-0.3-I-OUTD-US-208 [208V],N,96,Y'
'ABB MICRO-0.3-I-OUTD-US-240 [240V],N,96,Y'
'ABB UNO-2.0-I-OUTD-S-US [208V],Y,95.5,N'
'ABB UNO-2.0-I-OUTD-S-US [240V],Y,95.5,N'
'ABB UNO-2.0-I-OUTD-S-US [277V],Y,95.5,N'
'ABB UNO-2.0-TL-OUTD-S-US [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-A [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-A [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-A [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-C-M [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-C-M [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-C-M [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-C-M-A [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-C-M-A [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-C-M-A [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-M [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-M [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-M [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-M-A [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-M-A [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-B-M-A [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-C-M [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-C-M [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-C-M [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-C-M-A [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-C-M-A [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-C-M-A [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-Z-A [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-Z-A [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-Z-A [277V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-Z-M-A [208V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-Z-M-A [240V],Y,96.5,N'
'ABB UNO-2.0-TL-OUTD-S-US-Z-M-A [277V],Y,96.5,N'
'ABB UNO-2.5-I-OUTD-S-US [208V],Y,95.5,N'
'ABB UNO-2.5-I-OUTD-S-US [240V],Y,96,N'
'ABB UNO-2.5-I-OUTD-S-US [277V],Y,96,N'
'ABB PVI-3.0-OUTD-S-US [208V],Y,96,N'
'ABB PVI-3.0-OUTD-S-US [240V],Y,96,N'
'ABB PVI-3.0-OUTD-S-US [277V],Y,96,N'
#REF!
'ABB PVI-3.0-OUTD-S-US-A [208V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.0-OUTD-S-US-A [240V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.0-OUTD-S-US-A [277V],Y,96,N'
#REF!
'ABB PVI-3.0-OUTD-S-US-Z [208V],Y,96,N'
'ABB PVI-3.0-OUTD-S-US-Z [240V],Y,96,N'
'ABB PVI-3.0-OUTD-S-US-Z [277V],Y,96,N'
#REF!
'ABB PVI-3.0-OUTD-S-US-Z-A [208V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.0-OUTD-S-US-Z-A [240V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.0-OUTD-S-US-Z-A [277V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.0-OUTD-S-US-Z-M-A [208V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.0-OUTD-S-US-Z-M-A [240V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.0-OUTD-S-US-Z-M-A [277V],Y,96,N'
#REF!
'ABB PVI-3.0-OUTD-US [208V],Y,96,N'
'ABB PVI-3.0-OUTD-US [240V],Y,96,N'
'ABB PVI-3.0-OUTD-US [277V],Y,96,N'
'ABB UNO-3.0-TL-OUTD-S-US [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-A [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-A [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-A [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-C-M [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-C-M [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-C-M [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-C-M-A [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-C-M-A [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-C-M-A [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-M [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-M [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-M [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-M-A [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-M-A [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-B-M-A [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-C-M [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-C-M [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-C-M [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-C-M-A [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-C-M-A [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-C-M-A [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-Z-A [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-Z-A [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-Z-A [277V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-Z-M-A [208V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-Z-M-A [240V],Y,96.5,N'
'ABB UNO-3.0-TL-OUTD-S-US-Z-M-A [277V],Y,96.5,N'
'ABB UNO-DM-3.3-TL-PLUS-US-SB-RA [208V],Y,96,N'
#REF!
#REF!
#REF!
'ABB UNO-DM-3.3-TL-PLUS-US-SE-RA [208V],Y,96,N'
'ABB UNO-DM-3.3-TL-PLUS-US-SZM-RA [208V],Y,96,N'
'ABB UNO-DM-3.3-TL-PLUS-US-SZ-RA [208V],Y,96,N'
'ABB PVI-3.8-I-OUTD-x-US-y-Z [208V],Y,96,N'
'ABB UNO-DM-3.3-TL-PLUS-US-SB-RA [240V],Y,96.5,N'
#REF!
'ABB UNO-DM-3.3-TL-PLUS-US-SE-RA [240V],Y,96.5,N'
'ABB UNO-DM-3.3-TL-PLUS-US-SZM-RA [240V],Y,96.5,N'
#REF!
'ABB UNO-DM-3.3-TL-PLUS-US-SZ-RA [240V],Y,96.5,N'
'ABB UNO-DM-3.8-TL-PLUS-US-SB-RA [208V],Y,96,N'
#REF!
'ABB UNO-DM-3.8-TL-PLUS-US-SE-RA [208V],Y,96,N'
'ABB UNO-DM-3.8-TL-PLUS-US-SZM-RA [208V],Y,96,N'
'ABB UNO-DM-3.8-TL-PLUS-US-SZ-RA [208V],Y,96,N'
'ABB PVI-3.6-OUTD-S-US [208V],Y,96,N'
'ABB PVI-3.6-OUTD-S-US [240V],Y,96,N'
#REF!
'ABB PVI-3.6-OUTD-S-US [277V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.6-OUTD-S-US-A [208V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.6-OUTD-S-US-A [240V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.6-OUTD-S-US-A [277V],Y,96,N'
'ABB PVI-3.6-OUTD-S-US-Z [208V],Y,96,N'
#REF!
'ABB PVI-3.6-OUTD-S-US-Z [240V],Y,96,N'
'ABB PVI-3.6-OUTD-S-US-Z [277V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.6-OUTD-S-US-Z-A [208V],Y,96,N'
#REF!
'ABB PVI-3.6-OUTD-S-US-Z-A [240V],Y,96,N'
#REF!
'ABB PVI-3.6-OUTD-S-US-Z-A [277V],Y,96,N'
#REF!
'ABB PVI-3.6-OUTD-S-US-Z-M-A [208V],Y,96,N'
#REF!
'ABB PVI-3.6-OUTD-S-US-Z-M-A [240V],Y,96,N'
#REF!
'ABB PVI-3.6-OUTD-S-US-Z-M-A [277V],Y,96,N'
#REF!
#REF!
#REF!
'ABB PVI-3.6-OUTD-US [208V],Y,96,N'
#REF!
'ABB PVI-3.6-OUTD-US [240V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.6-OUTD-US [277V],Y,96,N'
'ABB PVI-3.8-I-OUTD-x-US-y-Z [240V],Y,96.5,N'
'ABB PVI-3.8-I-OUTD-x-US-y-Z [277V],Y,96.5,N'
'ABB PVI-3.8-OUTD-S-US [208V],Y,95.5,N'
'ABB PVI-3.8-OUTD-S-US [240V],Y,96,N'
'ABB PVI-3.8-OUTD-S-US [277V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.8-OUTD-S-US-A [208V],Y,95.5,N'
#REF!
#REF!
'ABB PVI-3.8-OUTD-S-US-A [240V],Y,96,N'
#REF!
'ABB PVI-3.8-OUTD-S-US-A [277V],Y,96,N'
'ABB PVI-3.8-OUTD-S-US-Z [208V],Y,95.5,N'
#REF!
'ABB PVI-3.8-OUTD-S-US-Z [240V],Y,96,N'
'ABB PVI-3.8-OUTD-S-US-Z [277V],Y,96,N'
#REF!
#REF!
'ABB PVI-3.8-OUTD-S-US-Z-A [208V],Y,95.5,N'
#REF!
'ABB PVI-3.8-OUTD-S-US-Z-A [240V],Y,96,N'
#REF!
'ABB PVI-3.8-OUTD-S-US-Z-A [277V],Y,96,N'
#REF!
'ABB PVI-3.8-OUTD-S-US-Z-M-A [208V],Y,95.5,N'
#REF!
'ABB PVI-3.8-OUTD-S-US-Z-M-A [240V],Y,96,N'
#REF!
'ABB PVI-3.8-OUTD-S-US-Z-M-A [277V],Y,96,N'
'ABB PVI-3.8-OUTD-US [208V],Y,95.5,N'
'ABB PVI-3.8-OUTD-US [240V],Y,96,N'
#REF!
'ABB PVI-3.8-OUTD-US [277V],Y,96,N'
#REF!
#REF!
#REF!
#REF!
#REF!
'ABB UNO-DM-3.8-TL-PLUS-US-SB-RA [240V],Y,96.5,N'
#REF!
#REF!
'ABB UNO-DM-3.8-TL-PLUS-US-SE-RA [240V],Y,96.5,N'
#REF!
#REF!
'ABB UNO-DM-3.8-TL-PLUS-US-SZM-RA [240V],Y,96.5,N'
#REF!
'ABB UNO-DM-3.8-TL-PLUS-US-SZ-RA [240V],Y,96.5,N'
'ABB PVI-4.2-OUTD-S-US [208V],Y,96,N'
'ABB PVI-4.2-OUTD-S-US [240V],Y,96,N'
#REF!
'ABB PVI-4.2-OUTD-S-US [277V],Y,96,N'
#REF!
#REF!
'ABB PVI-4.2-OUTD-S-US-A [208V],Y,96,N'
#REF!
#REF!
'ABB PVI-4.2-OUTD-S-US-A [240V],Y,96,N'
#REF!
#REF!
'ABB PVI-4.2-OUTD-S-US-A [277V],Y,96,N'
'ABB PVI-4.2-OUTD-S-US-Z [208V],Y,96,N'
#REF!
'ABB PVI-4.2-OUTD-S-US-Z [240V],Y,96,N'
'ABB PVI-4.2-OUTD-S-US-Z [277V],Y,96,N'
#REF!
#REF!
'ABB PVI-4.2-OUTD-S-US-Z-A [208V],Y,96,N'
#REF!
'ABB PVI-4.2-OUTD-S-US-Z-A [240V],Y,96,N'
#REF!
'ABB PVI-4.2-OUTD-S-US-Z-A [277V],Y,96,N'
#REF!
'ABB PVI-4.2-OUTD-S-US-Z-M-A [208V],Y,96,N'
#REF!
'ABB PVI-4.2-OUTD-S-US-Z-M-A [240V],Y,96,N'
#REF!
'ABB PVI-4.2-OUTD-S-US-Z-M-A [277V],Y,96,N'
'ABB PVI-4.2-OUTD-US [208V],Y,96,N'
'ABB PVI-4.2-OUTD-US [240V],Y,96,N'
'ABB PVI-4.2-OUTD-US [277V],Y,96,N'
'ABB UNO-DM-4.6-TL-PLUS-US-SB-RA [208V],Y,96,N'
'ABB UNO-DM-4.6-TL-PLUS-US-SE-RA [208V],Y,96,N'
'ABB UNO-DM-4.6-TL-PLUS-US-SZM-RA [208V],Y,96,N'
'ABB UNO-DM-4.6-TL-PLUS-US-SZ-RA [208V],Y,96,N'
'ABB PVI-4.6-1-OUTD-x-US-y [208V],Y,96,N'
'ABB PVI-4.6-1-OUTD-x-US-y [240V],Y,96.5,N'
'ABB PVI-4.6-1-OUTD-x-US-y [277V],Y,96.5,N'
'ABB PVI-4.6-I-OUTD-x-US-y-Z [208V],Y,96,N'
'ABB PVI-4.6-I-OUTD-x-US-y-Z [240V],Y,96.5,N'
'ABB PVI-4.6-I-OUTD-x-US-y-Z [277V],Y,96.5,N'
#REF!
'ABB UNO-DM-4.6-TL-PLUS-US-SB-RA [240V],Y,96.5,N'
#REF!
#REF!
'ABB UNO-DM-4.6-TL-PLUS-US-SE-RA [240V],Y,96.5,N'
#REF!
#REF!
'ABB UNO-DM-4.6-TL-PLUS-US-SZM-RA [240V],Y,96.5,N'
#REF!
#REF!
'ABB UNO-DM-4.6-TL-PLUS-US-SZ-RA [240V],Y,96.5,N'
'ABB UNO-DM-5.0-TL-PLUS-US-SB-RA [208V],Y,96.5,N'
'ABB UNO-DM-5.0-TL-PLUS-US-SE-RA [208V],Y,96.5,N'
'ABB UNO-DM-5.0-TL-PLUS-US-SZM-RA [208V],Y,96.5,N'
'ABB UNO-DM-5.0-TL-PLUS-US-SZ-RA [208V],Y,96.5,N'
#REF!
'ABB PVI-5000-OUTD-S-US-Z [208V],Y,96,N'
'ABB PVI-5000-OUTD-S-US-Z [240V],Y,96.5,N'
#REF!
'ABB PVI-5000-OUTD-S-US-Z [277V],Y,96.5,N'
'ABB PVI-5000-OUTD-S-US-Z-A [208V],Y,96,N'
#REF!
'ABB PVI-5000-OUTD-S-US-Z-A [240V],Y,96.5,N'
'ABB PVI-5000-OUTD-S-US-Z-A [277V],Y,96.5,N'
#REF!
'ABB PVI-5000-OUTD-US [208V],Y,96,N'
'ABB PVI-5000-OUTD-US [240V],Y,96.5,N'
#REF!
'ABB PVI-5000-OUTD-US [277V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-5000-OUTD-US-A [208V],Y,96,N'
#REF!
'ABB PVI-5000-OUTD-US-A [240V],Y,96.5,N'
#REF!
'ABB PVI-5000-OUTD-US-A [277V],Y,96.5,N'
'ABB PVI-5000-OUTD-US-Z [208V],Y,96,N'
'ABB PVI-5000-OUTD-US-Z [240V],Y,96.5,N'
'ABB PVI-5000-OUTD-US-Z [277V],Y,96.5,N'
#REF!
'ABB PVI-5000-OUTD-US-Z-A [208V],Y,96,N'
#REF!
'ABB PVI-5000-OUTD-US-Z-A [240V],Y,96.5,N'
#REF!
'ABB PVI-5000-OUTD-US-Z-A [277V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-5000-OUTD-US-Z-M-A [208V],Y,96,N'
#REF!
#REF!
'ABB PVI-5000-OUTD-US-Z-M-A [240V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-5000-OUTD-US-Z-M-A [277V],Y,96.5,N'
'ABB UNO-DM-5.0-TL-PLUS-US-SB-RA [240V],Y,96.5,N'
'ABB UNO-DM-5.0-TL-PLUS-US-SE-RA [240V],Y,96.5,N'
'ABB UNO-DM-5.0-TL-PLUS-US-SZM-RA [240V],Y,96.5,N'
#REF!
'ABB UNO-DM-5.0-TL-PLUS-US-SZ-RA [240V],Y,96.5,N'
'ABB PVI-6000-OUTD-S-US-A [208V],Y,96,N'
#REF!
'ABB PVI-6000-OUTD-S-US-A [240V],Y,96.5,N'
'ABB PVI-6000-OUTD-S-US-A [277V],Y,96.5,N'
#REF!
'ABB PVI-6000-OUTD-S-US-Z [208V],Y,96,N'
'ABB PVI-6000-OUTD-S-US-Z [240V],Y,96.5,N'
#REF!
'ABB PVI-6000-OUTD-S-US-Z [277V],Y,96.5,N'
'ABB PVI-6000-OUTD-S-US-Z-A [208V],Y,96,N'
#REF!
'ABB PVI-6000-OUTD-S-US-Z-A [240V],Y,96.5,N'
'ABB PVI-6000-OUTD-S-US-Z-A [277V],Y,96.5,N'
#REF!
'ABB PVI-6000-OUTD-US [208V],Y,96,N'
'ABB PVI-6000-OUTD-US [240V],Y,96.5,N'
#REF!
'ABB PVI-6000-OUTD-US [277V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-6000-OUTD-US-A [208V],Y,96,N'
#REF!
#REF!
'ABB PVI-6000-OUTD-US-A [240V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-6000-OUTD-US-A [277V],Y,96.5,N'
'ABB PVI-6000-OUTD-US-Z [208V],Y,96,N'
#REF!
'ABB PVI-6000-OUTD-US-Z [240V],Y,96.5,N'
'ABB PVI-6000-OUTD-US-Z [277V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-6000-OUTD-US-Z-A [208V],Y,96,N'
#REF!
'ABB PVI-6000-OUTD-US-Z-A [240V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-6000-OUTD-US-Z-A [277V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-6000-OUTD-US-Z-M-A [208V],Y,96,N'
#REF!
#REF!
'ABB PVI-6000-OUTD-US-Z-M-A [240V],Y,96.5,N'
#REF!
#REF!
'ABB PVI-6000-OUTD-US-Z-M-A [277V],Y,96.5,N'
'ABB UNO-DM-6.0-TL-PLUS-US-SB-RA [208V],Y,97,N'
#REF!
'ABB UNO-DM-6.0-TL-PLUS-US-SB-RA [240V],Y,97,N'
'ABB UNO-DM-6.0-TL-PLUS-US-SC-RA [208V],Y,97,N'
#REF!
'ABB UNO-DM-6.0-TL-PLUS-US-SC-RA [240V],Y,97,N'
'ABB UNO-DM-6.0-TL-PLUS-US-SE-RA [208V],Y,97,N'
#REF!
'ABB UNO-DM-6.0-TL-PLUS-US-SE-RA [240V],Y,97,N'
'ABB UNO-DM-6.0-TL-PLUS-US-S-XRA [208V],Y,97,N'
'ABB UNO-DM-6.0-TL-PLUS-US-S-XRA [240V],Y,97,N'
'ABB UNO-DM-6.0-TL-PLUS-US-SZM-RA [208V],Y,97,N'
#REF!
'ABB UNO-DM-6.0-TL-PLUS-US-SZM-RA [240V],Y,97,N'
#REF!
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-A [208V],Y,97,N'
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-A [240V],Y,97,N'
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-A [277V],Y,97,N'
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-Z-A [208V],Y,97,N'
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-Z-A [240V],Y,97,N'
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-Z-A [277V],Y,97,N'
'ABB UNO-7.6-TL-OUTD-S-US-Z-M [208V],Y,97,N'
'ABB UNO-7.6-TL-OUTD-S-US-Z-M [240V],Y,97,N'
'ABB UNO-7.6-TL-OUTD-S-US-Z-M [277V],Y,97,N'
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-Z-M-A [208V],Y,97,N'
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-Z-M-A [240V],Y,97,N'
#REF!
'ABB UNO-7.6-TL-OUTD-S-US-Z-M-A [277V],Y,97,N'
#REF!
'ABB UNO-8.6-TL-OUTD-S-US-A [240V],Y,97,N'
#REF!
#REF!
'ABB UNO-8.6-TL-OUTD-S-US-A [277V],Y,97,N'
#REF!
#REF!
'ABB UNO-8.6-TL-OUTD-S-US-Z-A [240V],Y,97,N'
#REF!
'ABB UNO-8.6-TL-OUTD-S-US-Z-A [277V],Y,97,N'
'ABB UNO-8.6-TL-OUTD-S-US-Z-M [240V],Y,97,N'
'ABB UNO-8.6-TL-OUTD-S-US-Z-M [277V],Y,97,N'
#REF!
'ABB UNO-8.6-TL-OUTD-S-US-Z-M-A [240V],Y,97,N'
#REF!
'ABB UNO-8.6-TL-OUTD-S-US-Z-M-A [277V],Y,97,N'
'ABB PVI-10.0-I-OUTD-x-US-208-y [208V],Y,96,N'
'ABB PVI-10.0-I-OUTD-x-US-480-y-z [480V],Y,97,N'
'ABB PVI-12.0-I-OUTD-x-US-480-y [480V],Y,97,N'
'ABB TRIO-20.0-TL-OUTD-S1A-US-480 [480V],Y,97.5,N'
'ABB TRIO-20.0-TL-OUTD-S1A-US-480-A [480V],Y,97.5,N'
'ABB TRIO-20.0-TL-OUTD-S1B-US-480 [480V],Y,97.5,N'
'ABB TRIO-20.0-TL-OUTD-S1B-US-480-A [480V],Y,97.5,N'
'ABB TRIO-20.0-TL-OUTD-S1-US-480-A [480V],Y,97.5,N'
'ABB TRIO-20.0-TL-OUTD-S-US-480-A [480V],Y,97.5,N'
'ABB TRIO-27.6-TL-OUTD-S1A-US-480-A [480V],Y,97.5,N'
'ABB TRIO-27.6-TL-OUTD-S1B-US-480-A [480V],Y,97.5,N'
'ABB TRIO-27.6-TL-OUTD-S1-US-480-A [480V],Y,97.5,N'
'ABB TRIO-27.6-TL-OUTD-S-US-480-A [480V],Y,97.5,N'
'ABB PVI-CENTRAL-50-US [480V],Y,95,N'
'ABB TRIO-50.0-TL-OUTD-US-480 [480V],Y,98,N'
#REF!
'ABB TRIO-60.0-TL-OUTD-US-480 [480V],Y,98,N'
'ABB TRIO-TM-60.0-US-480 [480V],Y,98,N'
'ABB PVI-CENTRAL-100-US [208V],Y,95,N'
'ABB PVI-CENTRAL-100-US [480V],Y,95,N'
'ABB PVI-CENTRAL-250-US [480V],Y,97,N'
'ABB PVI-CENTRAL-300-US [480V],Y,97,N'
'ABB ULTRA-750-TL-OUTD-2-US-690-x-y-z [690V],Y,96.5,N'
'ABB ULTRA-750-TL-OUTD-4-US-690-x-y-z [690V],Y,96.5,N'
'ABB ULTRA-750-TL-OUTD-1-US-690-x-y-z [690V],Y,96.5,N'
'ABB ULTRA-750-TL-OUTD-3-US-690-x-y-z [690V],Y,96.5,N'
'ABB ULTRA-1100-TL-OUTD-2-US-690-x-y-z [690V],Y,96.5,N'
'ABB ULTRA-1100-TL-OUTD-4-US-690-x-y-z [690V],Y,97,N'
'ABB ULTRA-1100-TL-OUTD-1-US-690-x-y-z [690V],Y,96.5,N'
'ABB ULTRA-1100-TL-OUTD-3-US-690-x-y-z [690V],Y,97,N'
'ABB ULTRA-1500-TL-OUTD-2-US-690-x-y-z [690V],Y,96.5,N'
'ABB ULTRA-1500-TL-OUTD-4-US-690-x-y-z [690V],Y,97,N'
'ABB ULTRA-1500-TL-OUTD-1-US-690-x-y-z [690V],Y,96.5,N'
'ABB ULTRA-1500-TL-OUTD-3-US-690-x-y-z [690V],Y,97,N'
'ABB PVS980-58-1818kVA-I [600V],Y,97.5,N'
'ABB PVS980-58-2000kVA-K [660V],Y,97.5,N'
'Ablerex Electronics ES 2200-US-240 [240V],Y,94.5,N'
'Ablerex Electronics ES 3300-US-240 [240V],Y,95,N'
'Ablerex Electronics ES 4200-US-240 [240V],Y,95.5,N'
'Ablerex Electronics ES 4200-US-240A [240V],Y,95.5,N'
'Ablerex Electronics ES 5000-US-240 [240V],Y,95.5,N'
'Ablerex Electronics ES 5000-US-240A [240V],Y,95.5,N'
'Advanced Energy Industries AE_3TL-12_10 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-12_10-08 [480V],Y,97.5,N'
'Advanced Energy Industries AE_3TL-12_6 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-G3_12_10 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-G3_12_10-8 [480V],N,97.5,N'
'Advanced Energy Industries 804R012 [480V],Y,97.5,N'
'Advanced Energy Industries AE_3TL-12_6-08 [480V],Y,97.5,N'
'Advanced Energy Industries AE_3TL-G3_12_6 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-G3_12_6-08 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-16_10-08 [480V],Y,97.5,N'
'Advanced Energy Industries AE_3TL-G3_16_10 [480V],N,97.5,N'
'Advanced Energy Industries 804R016 [480V],Y,97.5,N'
'Advanced Energy Industries AE_3TL-G3_16_6 [480V],N,97.5,N'
'Advanced Energy Industries 804R020 [480V],Y,97.5,N'
'Advanced Energy Industries AE_3TL-G3_20_6 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-20_10 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-20_6 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-G3_20_10-08 [480V],N,97.5,N'
'Advanced Energy Industries AE_3TL-23_10-08 [480V],Y,98,N'
'Advanced Energy Industries AE_3TL-23_06 [480V],N,98,N'
'Advanced Energy Industries AE 35TX-208 [208V],Y,95.5,N'
'Advanced Energy Industries AE 35TX-600 [600V],Y,95.5,N'
'Advanced Energy Industries AE 50TX-480 [480V],Y,96,N'
'Advanced Energy Industries AE 75TX-208 [208V],Y,95.5,N'
'Advanced Energy Industries AE 75TX-480 [480V],Y,95.5,N'
'Advanced Energy Industries AE 100TX-208 [208V],Y,95.5,N'
'Advanced Energy Industries AE 100TX-600 [600V],Y,96,N'
'Advanced Energy Industries AE 250TX-600 [600V],Y,96.5,N'
'Advanced Energy Industries Solaron 250 kW (3159200-XXXX) [480V],N,97.5,N'
'Advanced Energy Industries AE 260TX-480-LV [480V],Y,96.5,N'
'Advanced Energy Industries Solaron 333 kW (3159000-XXXX) [480V],N,97.5,N'
'Advanced Energy Industries AE 500NX-HE (3159502-XXXX) [480V],N,98,N'
'Advanced Energy Industries AE 500TX-600 [600V],N,97,N'
'Advanced Energy Industries Solaron 500kW (3159500-XXXX) [480V],N,97.5,N'
'Advanced Solar Photonics PV240 [208V],Y,97,N'
'Advanced Solar Photonics PV240 [277V],Y,97,N'
'Advanced Solar Photonics PV250 [240V],Y,97,N'
'Advanced Solar Photonics PV250 [277V],Y,97,N'
'Advanced Solar Photonics PV260 [208V],Y,97,N'
'Advanced Solar Photonics PV260 [277V],Y,97,N'
'Advanced Solar Photonics PV260 [240V],Y,97,N'
'Advanced Solar Photonics PV270 [240V],Y,97,N'
'AE Solar Energy AE3.8 [208V],Y,97,N'
'AE Solar Energy AE3.8 [277V],Y,97,N'
'AE Solar Energy AE5.0 [240V],Y,97,N'
'AE Solar Energy AE6.0 [208V],Y,97,N'
'AE Solar Energy AE6.0 [240V],Y,97,N'
'AE Solar Energy AE7.0 [240V],Y,97,N'
'AEconversion GMbH INV250-45US xxxxx [208V],N,91.5,Y'
'AEconversion GMbH INV250-45US xxxxx [240V],N,92,Y'
'AEconversion GMbH INV350-60US xxxxx [208V],N,91.5,Y'
'AEconversion GMbH INV350-60US xxxxx [240V],N,92.5,Y'
'AEconversion GMbH INV500-90US-xxxxx [208V],N,94,Y'
'AEconversion GMbH INV500-90US-xxxxx [240V],N,94.5,Y'
'AEG Power Solutions Protect MPV.030.01 [480V],N,96.5,N'
'AEG Power Solutions Protect MPV.060.01 [480V],N,96.5,N'
'AEG Power Solutions Protect MPV.090.01 [480V],N,96.5,N'
'AEG Power Solutions Protect MPV.120.01 [480V],N,96.5,N'
'AEG Power Solutions Protect MPV.150.01 [480V],N,96.5,N'
'Aero-Sharp X01-030L2E1 [240V],Y,92.5,N'
'Aero-Sharp X01-050L2E1 [240V],Y,93.5,N'
'Agepower Limit Agepower AP 1500TL-US [208V],Y,96,N'
'Agepower Limit Agepower AP 1500TL-US [277V],Y,96,N'
'Agepower Limit Agepower AP 2000TL-US [208V],Y,96.5,N'
'Agepower Limit Agepower AP 2000TL-US [240V],Y,96.5,N'
'Agepower Limit Agepower AP 2000TL-US [277V],Y,96.5,N'
'Agepower Limit Agepower AP 3000TL-US [208V],Y,96.5,N'
'Agepower Limit Agepower AP 3000TL-US [240V],Y,96.5,N'
'Agepower Limit Agepower AP 3000TL-US [277V],Y,96.5,N'
'Agepower Limit Agepower AP 3600MTL-US [208V],Y,97,N'
'Agepower Limit Agepower AP 3600MTL-US [240V],Y,97,N'
'Agepower Limit Agepower AP 3600MTL-US [277V],Y,97,N'
'Agepower Limit Agepower AP 4200MTL-US [208V],Y,97,N'
'Agepower Limit Agepower AP 4200MTL-US [240V],Y,97,N'
'Agepower Limit Agepower AP 4200MTL-US [277V],Y,97,N'
'Agepower Limit Agepower AP 5000MTL-US [208V],Y,97,N'
'Agepower Limit Agepower AP 5000MTL-US [240V],Y,97,N'
'Agepower Limit Agepower AP 5000MTL-US [277V],Y,97,N'
'Agepower Limit Agepower AP 10000 TL3-US [277V],Y,95.5,N'
'Agepower Limit Agepower AP 12000 TL3-US [277V],Y,95.5,N'
'Agepower Limit Agepower AP 18000 TL3-US [277V],Y,96,N'
'Agepower Limit Agepower AP 20000 TL3-US [277V],Y,96.5,N'
'Alpha Technologies Solaris 3500 XP [240V],Y,90.5,N'
'Altenergy Power System Inc. YC200-NA [240V],N,94,Y'
'Altenergy Power System Inc. YC250A [240V],N,94,Y'
'Altenergy Power System Inc. YC250I [240V],N,94,Y'
'Altenergy Power System Inc. YC500A [208V],N,95,Y'
'Altenergy Power System Inc. YC500A [240V],N,95,Y'
'Altenergy Power System Inc. YC500I [208V],N,95,Y'
'Altenergy Power System Inc. YC500I [240V],N,95,Y'
#REF!
'Altenergy Power System Inc. YC600 [240V],N,96.5,Y'
'Altenergy Power System Inc. YC1000-3-208 [480V],N,94.5,Y'
'Altenergy Power System Inc. YC1000-3-480 [480V],N,94.5,Y'
'Altenergy Power System Inc. YC1000-3-K480,N,94.5,Y'
'American Electric Technologies ISIS-1000-15000-60,Y,96.5,N'
'American Electric Technologies ISIS-1000-410-60,Y,96,N'
'AMETEK Solidstate Control RECon 30L-100-US,Y,98,N'
'AMETEK Solidstate Control RECon 30H-150-US [300V],Y,98,N'
'Andalay Solar LW-230-1-AC1-A-B [240V],N,95,Y'
'Andalay Solar LW-230-1-AC3-B-B [208V],N,95,Y'
'Andalay Solar LW-235-1-AC1-A-B [240V],N,95,Y'
'Andalay Solar LW-235-1-AC3-B-B [208V],N,95,Y'
'Andalay Solar LW-240-1-AC1-A-B [240V],N,95,Y'
'Andalay Solar LW-240-1-AC3-B-B [208V],N,95,Y'
'Andalay Solar ST-175-1AC1-A-A [240V],N,95,Y'
'Andalay Solar ST-175-1AC3-B-A [208V],N,95,Y'
'Andalay Solar ST-185-1AC1-A-A [240V],N,95,Y'
'Andalay Solar ST-185-1AC1-A-B [240V],N,95,Y'
'Andalay Solar ST-185-1AC3-B-A [208V],N,95,Y'
'Andalay Solar ST-185-1AC3-B-B [208V],N,95,Y'
'Andalay Solar ST-190-1AC1-A-B [240V],N,95,Y'
'Andalay Solar ST-190-1AC3-B-B [208V],N,95,Y'
'Andalay Solar ST-195-1AC1-A-B [240V],N,95,Y'
'Andalay Solar ST-195-1AC3-B-B [208V],N,95,Y'
'Andalay Solar LW-230-1-AC0-D-B [208V],N,96,Y'
'Andalay Solar LW-230-1-AC0-D-B [240V],N,96,Y'
'Andalay Solar LW-230-1-AC2-D-B [208V],N,96,Y'
'Andalay Solar LW-230-1-AC2-D-B [240V],N,96,Y'
'Andalay Solar LW-235-1-AC0-D-B [208V],N,96,Y'
'Andalay Solar LW-235-1-AC0-D-B [240V],N,96,Y'
'Andalay Solar LW-235-1-AC2-D-B [208V],N,96,Y'
'Andalay Solar LW-235-1-AC2-D-B [240V],N,96,Y'
'Andalay Solar LW-240-1-AC0-D-B [208V],N,96,Y'
'Andalay Solar LW-240-1-AC0-D-B [240V],N,96,Y'
'Andalay Solar LW-240-1-AC2-D-B [208V],N,96,Y'
'Andalay Solar LW-240-1-AC2-D-B [240V],N,96,Y'
'Andalay Solar TW-240-1-AC2-D-B [208V],N,96,Y'
'Andalay Solar TW-240-1-AC2-D-B [240V],N,96,Y'
'Andalay Solar TW-245-1-AC2-D-B [208V],N,96,Y'
'Andalay Solar TW-245-1-AC2-D-B [240V],N,96,Y'
'Andalay Solar TW-250-1-AC2-D-B [208V],N,96,Y'
'Andalay Solar TW-250-1-AC2-D-B [240V],N,96,Y'
'Apparent MGI220-xxx [240V],N,90,Y'
'Apparent SG424-120V [120V],N,91.5,Y'
'AU Optronics PM060MA0_240 [240V],N,94.5,Y'
'AU Optronics PM060MA0_245 [240V],N,94.5,Y'
'AU Optronics PM060MA0_250 [240V],N,94.5,Y'
'AU Optronics PM060MA0_255 [240V],N,94.5,Y'
'AU Optronics PM060MA0_260 [240V],N,94.5,Y'
'AU Optronics PM060MA0_265 [240V],N,94.5,Y'
'AU Optronics PM060MA0_270 [240V],N,94.5,Y'
'AU Optronics PM060MA0_275 [240V],N,94.5,Y'
'AU Optronics PM060MA1_275 [240V],N,94.5,Y'
'AU Optronics PM060MA2_275 [240V],N,94.5,Y'
'AU Optronics PM060PA0_235 [240V],N,94.5,Y'
'AU Optronics PM060PA0_240 [240V],N,94.5,Y'
'AU Optronics PM060PA0_250 [240V],N,94.5,Y'
'AU Optronics PM060PA0_255 [240V],N,94.5,Y'
'AU Optronics PM060PA0_260 [240V],N,94.5,Y'
'AU Optronics PM240PA0_235 [240V],N,94.5,Y'
'AU Optronics PM240PA0_240 [240V],N,94.5,Y'
'AU Optronics PM240PA0_245 [240V],N,94.5,Y'
'AU Optronics PM245PA0_235 [240V],N,94.5,Y'
'AU Optronics PM245PA0_240 [240V],N,94.5,Y'
'AU Optronics PM245PA0_245 [240V],N,94.5,Y'
'AU Optronics PM245PA0_250 [240V],N,94.5,Y'
'AU Optronics PM245PA0_255 [240V],N,94.5,Y'
'AU Optronics PM245PA0_260 [240V],N,94.5,Y'
'AU Optronics PM250MA0_240 [240V],N,94.5,Y'
'AU Optronics PM250MA0_245 [240V],N,94.5,Y'
'AU Optronics PM250MA0_250 [240V],N,94.5,Y'
'AU Optronics PM250MA0_255 [240V],N,94.5,Y'
'AU Optronics PM250MA0_260 [240V],N,94.5,Y'
'AU Optronics PM250MA0_265 [240V],N,94.5,Y'
'AU Optronics PM250MA0_270 [240V],N,94.5,Y'
'AU Optronics PM250MA0_275 [240V],N,94.5,Y'
'AU Optronics PM250MA1_275 [240V],N,94.5,Y'
'AU Optronics PM250MA2_275 [240V],N,94.5,Y'
'AU Optronics PM060MA1_240 [208V],N,95,Y'
'AU Optronics PM060MA1_240 [240V],N,95,Y'
'AU Optronics PM060MA1_245 [208V],N,95,Y'
'AU Optronics PM060MA1_245 [240V],N,95,Y'
'AU Optronics PM060MA1_250 [208V],N,95,Y'
'AU Optronics PM060MA1_250 [240V],N,95,Y'
'AU Optronics PM060MA1_255 [208V],N,95,Y'
'AU Optronics PM060MA1_255 [240V],N,95,Y'
'AU Optronics PM060MA1_260 [208V],N,95,Y'
'AU Optronics PM060MA1_260 [240V],N,95,Y'
'AU Optronics PM060MA1_265 [208V],N,95,Y'
'AU Optronics PM060MA1_265 [240V],N,95,Y'
'AU Optronics PM060MA1_270 [208V],N,95,Y'
'AU Optronics PM060MA1_270 [240V],N,95,Y'
'AU Optronics PM060MA2_240 [208V],N,95,Y'
'AU Optronics PM060MA2_240 [240V],N,95,Y'
'AU Optronics PM060MA2_245 [208V],N,95,Y'
'AU Optronics PM060MA2_245 [240V],N,95,Y'
'AU Optronics PM060MA2_250 [208V],N,95,Y'
'AU Optronics PM060MA2_250 [240V],N,95,Y'
'AU Optronics PM060MA2_255 [208V],N,95,Y'
'AU Optronics PM060MA2_255 [240V],N,95,Y'
'AU Optronics PM060MA2_260 [208V],N,95,Y'
'AU Optronics PM060MA2_260 [240V],N,95,Y'
'AU Optronics PM060MA2_265 [208V],N,95,Y'
'AU Optronics PM060MA2_265 [240V],N,95,Y'
'AU Optronics PM060MA2_270 [208V],N,95,Y'
'AU Optronics PM060MA2_270 [240V],N,95,Y'
'AU Optronics PM060PA0_245 [240V],N,94.5,Y'
'AU Optronics PM060PA1_235 [208V],N,95,Y'
'AU Optronics PM060PA1_235 [240V],N,95,Y'
'AU Optronics PM060PA1_240 [208V],N,95,Y'
'AU Optronics PM060PA1_240 [240V],N,95,Y'
'AU Optronics PM060PA1_245 [208V],N,95,Y'
'AU Optronics PM060PA1_245 [240V],N,95,Y'
'AU Optronics PM060PA1_250 [208V],N,95,Y'
'AU Optronics PM060PA1_250 [240V],N,95,Y'
#REF!
'AU Optronics PM060PA1_255 [208V],N,95,Y'
'AU Optronics PM060PA1_260 [208V],N,95,Y'
'AU Optronics PM060PA1_260 [240V],N,95,Y'
'AU Optronics PM060PA2_235 [208V],N,95,Y'
'AU Optronics PM060PA2_235 [240V],N,95,Y'
'AU Optronics PM060PA2_240 [208V],N,95,Y'
'AU Optronics PM060PA2_240 [240V],N,95,Y'
'AU Optronics PM060PA2_245 [208V],N,95,Y'
'AU Optronics PM060PA2_245 [240V],N,95,Y'
'AU Optronics PM060PA2_250 [208V],N,95,Y'
'AU Optronics PM060PA2_250 [240V],N,95,Y'
'AU Optronics PM060PA2_255 [208V],N,95,Y'
'AU Optronics PM060PA2_255 [240V],N,95,Y'
'AU Optronics PM060PA2_260 [208V],N,95,Y'
'AU Optronics PM060PA2_260 [240V],N,95,Y'
'AU Optronics PM245PA1_235 [240V],N,95,Y'
'AU Optronics PM245PA1_240 [240V],N,95,Y'
'AU Optronics PM245PA1_245 [240V],N,95,Y'
'AU Optronics PM245PA1_250 [240V],N,95,Y'
'AU Optronics PM245PA1_255 [208V],N,95,Y'
'AU Optronics PM245PA1_255 [240V],N,95,Y'
'AU Optronics PM245PA1_260 [208V],N,95,Y'
'AU Optronics PM245PA1_260 [240V],N,95,Y'
'AU Optronics PM245PA2_235 [208V],N,95,Y'
'AU Optronics PM245PA2_235 [240V],N,95,Y'
'AU Optronics PM245PA2_240 [208V],N,95,Y'
'AU Optronics PM245PA2_240 [240V],N,95,Y'
'AU Optronics PM245PA2_245 [208V],N,95,Y'
'AU Optronics PM245PA2_245 [240V],N,95,Y'
'AU Optronics PM245PA2_250 [208V],N,95,Y'
'AU Optronics PM245PA2_250 [240V],N,95,Y'
'AU Optronics PM245PA2_255 [208V],N,95,Y'
'AU Optronics PM245PA2_255 [240V],N,95,Y'
'AU Optronics PM245PA2_260 [208V],N,95,Y'
'AU Optronics PM245PA2_260 [240V],N,95,Y'
'AU Optronics PM250MA1_240 [240V],N,95,Y'
'AU Optronics PM250MA1_245 [240V],N,95,Y'
'AU Optronics PM250MA1_250 [240V],N,95,Y'
'AU Optronics PM250MA1_255 [240V],N,95,Y'
'AU Optronics PM250MA1_260 [240V],N,95,Y'
'AU Optronics PM250MA1_265 [208V],N,95,Y'
'AU Optronics PM250MA1_265 [240V],N,95,Y'
'AU Optronics PM250MA1_270 [208V],N,95,Y'
'AU Optronics PM250MA1_270 [240V],N,95,Y'
'AU Optronics PM250MA2_240 [208V],N,95,Y'
'AU Optronics PM250MA2_240 [240V],N,95,Y'
'AU Optronics PM250MA2_245 [208V],N,95,Y'
'AU Optronics PM250MA2_245 [240V],N,95,Y'
'AU Optronics PM250MA2_250 [208V],N,95,Y'
'AU Optronics PM250MA2_250 [240V],N,95,Y'
'AU Optronics PM250MA2_255 [208V],N,95,Y'
'AU Optronics PM250MA2_255 [240V],N,95,Y'
'AU Optronics PM250MA2_260 [208V],N,95,Y'
'AU Optronics PM250MA2_260 [240V],N,95,Y'
'AU Optronics PM250MA2_265 [208V],N,95,Y'
'AU Optronics PM250MA2_265 [240V],N,95,Y'
'AU Optronics PM250MA2_270 [208V],N,95,Y'
'AU Optronics PM250MA2_270 [240V],N,95,Y'
'Auxin Solar AXU-PV1500U [208V],Y,94.5,N'
'Auxin Solar AXU-PV1500U [240V],Y,94.5,N'
'Auxin Solar AXU-PV2000U [208V],Y,95.5,N'
'Auxin Solar AXU-PV2000U [240V],Y,95,N'
'Auxin Solar AXU-PV3000U [208V],Y,95.5,N'
'Auxin Solar AXU-PV3000U [240V],Y,95.5,N'
'Auxin Solar AXN-PV4000U [208V],Y,95.5,N'
'Auxin Solar AXN-PV4000U [240V],Y,96,N'
'Ballard Power Systems EPC-PV-208-30KW [208V],Y,93,N'
'Ballard Power Systems EPC-PV-480-30KW [480V],Y,93,N'
'Ballard Power Systems EPC-PV-208-75KW,Y,91.5,N'
'Ballard Power Systems EPC-PV-480-75KW [480V],Y,91.5,N'
'Beacon Power M4,N,90,N'
'Beacon Power M4 Plus,Y,91.5,N'
'Beacon Power M5,N,89,N'
'Beacon Power M5 Plus,Y,90,N'
'Beijing Kinglong New Energy Technology Sunteams 1500 [208V],Y,95,N'
'Beijing Kinglong New Energy Technology Sunteams 1500 [240V],Y,95,N'
'Beijing Kinglong New Energy Technology Sunteams 2000 [208V],Y,95.5,N'
'Beijing Kinglong New Energy Technology Sunteams 2000 [240V],Y,96,N'
'Beijing Kinglong New Energy Technology Sunteams 3000 [208V],Y,96,N'
'Beijing Kinglong New Energy Technology Sunteams 3000 [240V],Y,96,N'
'Beijing Kinglong New Energy Technology Sunteams 4000 [208V],Y,97,N'
'Beijing Kinglong New Energy Technology Sunteams 4000 [240V],Y,97.5,N'
'Beijing Kinglong New Energy Technology Sunteams 5000 [208V],Y,97,N'
'Beijing Kinglong New Energy Technology Sunteams 5000 [240V],Y,97.5,N'
'Beyond Building Group SR1500TLI [208V],Y,94.5,N'
'Beyond Building Group SR1500TLI [240V],Y,94.5,N'
'Beyond Building Group SR2000TLI [208V],Y,95.5,N'
'Beyond Building Group SR2000TLI [240V],Y,95,N'
'Beyond Building Group SR3000TLI [208V],Y,95.5,N'
'Beyond Building Group SR3000TLI [240V],Y,95.5,N'
'Beyond Building Group SR4000TLI [208V],Y,95.5,N'
'Beyond Building Group SR4000TLI [240V],Y,96,N'
'Beyond Building Systems SR2000TL-US-240 [240V],Y,94.5,N'
'Beyond Building Systems SR3000TL-US-240 [240V],Y,95,N'
'Beyond Building Systems SR4200TL-US-240 [240V],Y,95.5,N'
'Beyond Building Systems SR5000TL-US-240 [240V],Y,95.5,N'
'Canadian Solar Inc. CM-240-EC,N,96,Y'
'Canadian Solar Inc. CS6P-245M-EA,N,96,Y'
'Canadian Solar Inc. CS6P-245P-EA,N,96,Y'
'Canadian Solar Inc. CS6P-250M-EA,N,96,Y'
'Canadian Solar Inc. CS6P-250P-EA,N,96,Y'
'Canadian Solar Inc. CS6P-255M-EA,N,96,Y'
'Canadian Solar Inc. CS6P-255P-EA,N,96,Y'
'Canadian Solar Inc. CS6P-260M-EA,N,96,Y'
'Canadian Solar Inc. CS6P-260P-EA,N,96,Y'
'Canadian Solar Inc. CM-260-EC,N,96,Y'
'Canadian Solar Inc. CM-280-EC,N,96,Y'
'Canadian Solar Inc. CM-300-EC,N,96,Y'
'Canadian Solar Inc. CSI-3000TL-CT [208V],Y,96,N'
'Canadian Solar Inc. CSI-3000TL-CT [240V],Y,96.5,N'
'Canadian Solar Inc. CSI-4000TL-CT [208V],Y,96.5,N'
'Canadian Solar Inc. CSI-4000TL-CT [240V],Y,97,N'
'Canadian Solar Inc. CSI-5000TL-CT [208V],Y,96.5,N'
'Canadian Solar Inc. CSI-5000TL-CT [240V],Y,97,N'
'Canadian Solar Inc. CSI-6000TL-CT [208V],Y,96.5,N'
'Canadian Solar Inc. CSI-6000TL-CT [240V],Y,97,N'
'Canadian Solar Inc. CSI-23KTL-CT [480V],Y,98,N'
'Canadian Solar Inc. CSI-25KTL-GS-FL [480V],N,98,N'
'Canadian Solar Inc. CSI-28KTL-CT [480V],Y,98,N'
'Canadian Solar Inc. CSI-30KTL-GS-FL [480V],N,98,N'
'Canadian Solar Inc. CSI-36KTL-CT [480V],N,98,N'
'Canadian Solar Inc. CSI-40KTL-GS [480V],N,98.5,N'
#REF!
'Canadian Solar Incorporated. CSI-50KTL-GS [480V] ,N,98.5,N'
'Canadian Solar Incorporated. CSI-50KTL-GS-B [480V],N,98.5,N'
'Canadian Solar Incorporated. CSI-50KTL-GS-FLB [480V],N,98.5,N'
'Canadian Solar Incorporated. CSI-50KTL-GS-FL [480V] ,N,98.5,N'
'Canadian Solar Incorporated. CSI-60KTL-GS [480V],N,98.5,N'
'Canadian Solar Incorporated. CSI-60KTL-GS-B [480V],N,98.5,N'
'Canadian Solar Incorporated. CSI-66KTL-GS [480V],N,98.5,N'
'Canadian Solar Incorporated. CSI-66KTL-GS-B [480V],N,98.5,N'
'Carlo Gavazzi ISGA 1 22 [240V],Y,94.5,N'
'Carlo Gavazzi ISGA 1 33 [240V],Y,95,N'
'Carlo Gavazzi ISGA 1 42 [240V],Y,95.5,N'
'Carlo Gavazzi ISGA 1 53 [240V],Y,95.5,N'
'CFM Equipment Distributors Green Power 2000 [240V],Y,92,N'
#REF!
#REF!
'CFM Equipment Distributors Green Power 2500 [240V],Y,94.5,N'
'CFM Equipment Distributors Green Power 3000 [240V],Y,93.5,N'
'CFM Equipment Distributors Green Power 3500 [240V],Y,95.5,N'
'CFM Equipment Distributors Green Power 4600 [208V],Y,95.5,N'
'CFM Equipment Distributors Green Power 4800 [240V],Y,96,N'
'CFM Equipment Distributors Green Power 5200 [240V],Y,96,N'
'Changzhou Nesl Solartech DJ-230P-ST15 [240V],N,94.5,Y'
'Changzhou Nesl Solartech DJ-235P-ST15 [240V],N,94.5,Y'
'Changzhou Nesl Solartech DJ-240DA/C-ST15 [240V],N,94.5,Y'
'Changzhou Nesl Solartech DJ-240P-ST15 [240V],N,94.5,Y'
'Changzhou Nesl Solartech DJ-245DA/C-ST15 [240V],N,94.5,Y'
'Changzhou Nesl Solartech DJ-250DA/C-ST15 [240V],N,94.5,Y'
'Changzhou Nesl Solartech DJ-255D/C-ST15 [240V],N,94.5,'
'Chiconypower MU300SAP2 [240V],N,96,Y'
'Chilicon Power LLC CP-250-60-208/240-MC4 [208V],N,96,Y'
'Chilicon Power LLC CP-250-60-208/240-MC4 [240V],N,96,Y'
#REF!
'Chilicon Power LLC CP-250E-60/72-208/240-MC4 [208V],N,95.5,Y'
#REF!
'Chilicon Power LLC CP-250E-60/72-208/240-MC4 [240V],N,96,Y'
'Chint Power Systems America CPS SCA3KTL-O/US [208V],Y,96,N'
'Chint Power Systems America CPS SCA3KTL-O/US [240V],Y,96.5,N'
'Chint Power Systems America CPS SCE4KTL-O US [208V],Y,97,N'
'Chint Power Systems America CPS SCA4KTL-O/US [208V],Y,96.5,N'
'Chint Power Systems America CPS SCE4KTL-O US [240V],Y,97,N'
'Chint Power Systems America CPS SCE4KTL-O US [277V],Y,97,N'
'Chint Power Systems America CPS SCA4KTL-O/US [240V],Y,97,N'
'Chint Power Systems America CPS SCE5KTL-O US [208V],Y,97,N'
'Chint Power Systems America CPS SCA5KTL-O US [208V],Y,96.5,N'
'Chint Power Systems America CPS SCE5KTL-O US [240V],Y,97,N'
'Chint Power Systems America CPS SCE5KTL-O US [277V],Y,97,N'
'Chint Power Systems America CPS SCA5KTL-O US [240V],Y,97,N'
'Chint Power Systems America CPS SCA6KTL-O US [208V],Y,96.5,N'
'Chint Power Systems America CPS SCE6KTL-O US [208V],Y,97,N'
'Chint Power Systems America CPS SCA6KTL-O US [240V],Y,97,N'
'Chint Power Systems America CPS SCE6KTL-O US [240V],Y,97,N'
'Chint Power Systems America CPS SCE6KTL-O US [277V],Y,97,N'
'Chint Power Systems America CPS SCE7KTL-O US [240V],Y,97,N'
'Chint Power Systems America CPS SCE7KTL-O US [208V],Y,97,N'
'Chint Power Systems America CPS SCE7KTL-O US [277V],Y,97,N'
'Chint Power Systems America CPS SC14KTL-DO/xx-208 [208V],Y,96,N'
'Chint Power Systems America CPS SC20KTL-DO/xx-480 [480V],Y,97,N'
'Chint Power Systems America CPS SCA23KTL-DO/US-480 [480V],Y,98,N'
'Chint Power Systems America CPS SCA28KTL-DO/US-480 [480V],Y,98,N'
'Chint Power Systems America CPS SCA36KTL-DO/US [480V],Y,98,N'
#REF!
#REF!
'Chint Power Systems America CPS SCA60KTL-DO/US-480 [480V],Y,98.5,N'
'Chint Power Systems America CPS SC100KT-O/xx-480 [480V],Y,96,N'
#REF!
'Chint Power Systems America CPS SCH100KTL-DO/US-600 [600V],N,98.5,N'
#REF!
'Chint Power Systems America CPS SCH125KTL-DO/US-600 [600V],N,98.5,N'
'Chint Solar Zhejiang CHPI3KTL-US [208V],Y,96,N'
'Chint Solar Zhejiang CHPI3KTL-US [240V],Y,96.5,N'
'Chint Solar Zhejiang CHPI4KTL-US [208V],Y,96.5,N'
'Chint Solar Zhejiang CHPI4KTL-US [240V],Y,97,N'
'Chint Solar Zhejiang CHPI5KTL-US [208V],Y,96.5,N'
#REF!
'Chint Solar Zhejiang CHPI5KTL-US [240V],Y,97,N'
'Chint Solar Zhejiang CHPI 6KTL-US [208V],Y,96.5,N'
'Chint Solar Zhejiang CHPI 6KTL-US [240V],Y,97,N'
'Chint Solar Zhejiang CHPI14KTL-US,Y,96,N'
'Chint Solar Zhejiang CHPI20KTL-US,Y,97,N'
'Chint Solar Zhejiang CHPI 23KTL-US,Y,98,N'
'Chint Solar Zhejiang CHPI 28KTL-US,Y,98,N'
'Concept by US Power Station PS247-05-180 [120V],Y,94,N'
'Concept by US Power Station PS247-10-180 [120V],Y,94,N'
'Concept by US Power Station PS247-15-180 [120V],Y,94,N'
'Connect Renewable Energy CE 4000 [240V],Y,93,N'
'Danfoss MLX 480V [480V],N,98.5,N'
'Danfoss Solar DLX 2.0 UL [208V],Y,96.5,N'
'Danfoss Solar DLX 2.0 UL [240V],Y,96.5,N'
'Danfoss Solar DLX 2.9 UL [240V],Y,96.5,N'
'Danfoss Solar DLX 2.9 UL [208V],Y,96.5,N'
'Danfoss Solar DLX 3.8 UL [208V],Y,96.5,N'
'Danfoss Solar DLX 3.8 UL [240V],Y,97,N'
'Danfoss Solar DLX 4.4 UL [208V],Y,96.5,N'
#REF!
'Danfoss Solar DLX 4.4 UL [240V],Y,97,N'
'Danfoss Solar MLX 400V [400V],N,98,N'
#REF!
'Darfon Electronics Corp. MIG240UL00 [240V],N,95,N'
'Darfon Electronics Corp. MIG300UL00 [240V],N,95,N'
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
'Darfon Electronics Corp. G32xxxxxx [208V],N,95.5,Y'
'Darfon Electronics Corp. G32xxxxxx [240V],N,96.3,Y'
#REF!
'Darfon Electronics Corp. G32xxxxxx [277V],N,96,Y'
#REF!
'Darfon Electronics Corp. H5000x [240V],N,95.5,N'
'DASS tech DSP-M33250KUS,Y,95,N'
#REF!
'Delta Electronics DDP-260AB XX,N,95,Y'
#REF!
#REF!
'Delta Electronics SOLIVIA 3.8 NA G4 TL [208V],Y,97.5,N'
'Delta Electronics M4-TL-US [208V],Y,97,N'
#REF!
#REF!
'Delta Electronics SOLIVIA 3.8 NA G4 TL [240V],Y,97.5,N'
'Delta Electronics M4-TL-US [240V],Y,97.5,N'
#REF!
'Delta Electronics M5-TL-US [208V],Y,97.5,N'
'Delta Electronics M5-TL-US [240V],Y,97.5,N'
'Delta Electronics M6-TL-US [208V],Y,97,N'
'Delta Electronics E6-TL-US [208V],Y,97,N'
'Delta Electronics E6-TL-US(AC) [208V],Y,98,N'
'Delta Electronics E6-TL-US(AC) [240V],Y,98,N'
#REF!
'Delta Electronics SOLIVIA 5.2 NA G4 TL [208V],Y,97.5,N'
#REF!
'Delta Electronics SOLIVIA 5.2 NA G4 TL [240V],Y,97.5,N'
'Delta Electronics E6-TL-US [240V],Y,97.5,N'
'Delta Electronics M6-TL-US [240V],Y,97.5,N'
'Delta Electronics RPI H7U [208V],Y,97,N'
'Delta Electronics RPI H7U [240V] [6kVa],Y,97.5,N'
'Delta Electronics E8-TL-US(AC) [240V],Y,98,N'
'Delta Electronics E8-TL-US(AC) [208V],Y,98,N'
#REF!
'Delta Electronics SOLIVIA 6.6 NA G4 TL [208V],Y,97.5,N'
#REF!
'Delta Electronics SOLIVIA 6.6 NA G4 TL [240V],Y,97.5,N'
#REF!
'Delta Electronics SOLIVIA 7.6 NA G4 TL [208V],Y,97.5,N'
'Delta Electronics E8-TL-US [208V],Y,97.5,N'
'Delta Electronics M8-TL-US [208V],Y,97.5,N'
'Delta Electronics RPI H7U [240V] [7kVa],Y,97.5,N'
#REF!
'Delta Electronics SOLIVIA 7.6 NA G4 TL [240V],Y,97.5,N'
'Delta Electronics E8-TL-US [240V],Y,97.5,N'
'Delta Electronics M8-TL-US [240V],Y,97.5,N'
'Delta Electronics Delta 15 TL,Y,98,N'
'Delta Electronics Delta 20 TL,Y,98,N'
#REF!
'Delta Electronics M24U_XXX [480V],N,98,N'
#REF!
'Delta Electronics M28U_XXX [480V],N,98,N'
#REF!
'Delta Electronics M36U_XXX [480V],N,98,N'
#REF!
'Delta Electronics M42U_XXX [480V],N,98,N'
#REF!
'Delta Electronics M60U_XXX [480V],N,98.5,N'
#REF!
'Delta Electronics M80U_XXX [480V],N,98.5,N'
'Delta Energy Systems SI 1800 US [208V],Y,92.5,N'
'Delta Energy Systems SI 1800 US [240V],Y,92.5,N'
'Delta Energy Systems SI 2500 US [208V],Y,92,N'
'Delta Energy Systems SI 2500 US [240V],Y,93,N'
'Delta Energy Systems SOLIVIA 2.5 NA G4 TR [240V],Y,95,N'
'Delta Energy Systems SOLIVIA 2.5 NA G4 TR [208V],Y,94.5,N'
'Delta Energy Systems SOLIVIA 3.3 NA G4 TR [208V],Y,95,N'
'Delta Energy Systems SOLIVIA 3.3 NA G4 TR [240V],Y,95.5,N'
'Delta Energy Systems SOLIVIA 4.4 NA G4 TR [208V],Y,95,N'
'Delta Energy Systems SOLIVIA 4.4 NA G4 TR [240V],Y,95,N'
'Delta Energy Systems SOLIVIA 5.0 NA G4 TR [208V],Y,95,N'
'Delta Energy Systems SOLIVIA 5.0 NA G4 TR [240V],Y,95,N'
'Destin Power Inc. SAVEEN1000-ES02H.US [440V],N,98,N'
'Diehl AKO Stiftung 4301 S-A [208V],Y,94,N'
'Diehl AKO Stiftung 4301 S-A [240V],Y,94.5,N'
'Diehl AKO Stiftung Platinum 100 CS-A [208V],Y,94.5,N'
'Diehl AKO Stiftung Platinum 100 CS-A [480V],Y,94.5,N'
'Diehl AKO Stiftung Platinum 100 CS-A HE [480V],Y,95.5,N'
'Direct Grid Technologies DGM-S460 [240V],N,92.5,N'
'Dow Chemical 362589 (3.5 kW 2-string) [240V],N,94.5,N'
'Dow Chemical 362590 (3.5 kW 3-string) [240V],N,94,N'
'Dow Chemical 362591 (3.5 kW 4-string) [240V],N,94,N'
'Dow Chemical 362592 (5.0 kW 2-string) [240V],N,95,N'
'DYNAPOWER COMPANY LLC MPS-100 [480],N,93,N'
'DYNAPOWER COMPANY LLC MPS-250 [480V],N,95,N'
'DYNAPOWER COMPANY LLC MPS-250HV [480V],N,95.5,N'
'Eaton PV238 [208V],Y,97,N'
'Eaton PV240 [208V],Y,97,N'
'Eaton PV238 [240V],Y,97,N'
'Eaton PV238 [277V],Y,97,N'
'Eaton PV240 [240V],Y,97,N'
'Eaton PV240 [277V],Y,97,N'
'Eaton PV250 [208V],Y,97,N'
'Eaton PV250 [240V],Y,97,N'
'Eaton PV250 [277V],Y,97,N'
'Eaton PV260 [208V],Y,97,N'
#REF!
'Eaton PV260 [277V],Y,97,N'
#REF!
'Eaton PV260 [240V],Y,97,N'
#REF!
'Eaton PV270 [240V],Y,97,N'
#REF!
'Eaton PV270 [277V],Y,97,N'
'Eaton Xpert1500,Y,98,N'
'Elettronica Santerno TG100NA208Y [208V],N,96,N'
'Elettronica Santerno TG125NA208Y [208V],Y,96,N'
'Eltek Theia 2.0He-t UL [208V],Y,96.5,N'
'Eltek Theia 2.9He-t UL [240V],Y,96.5,N'
'Eltek Theia 3.8He-t UL [208V],Y,96.5,N'
'Eltek Theia 4.4He-t UL [208V],Y,96.5,N'
'Emerson Network Power SPV-4.0AIUSO [240V],N,95,N'
'Emerson Network Power SPV-5.0AIUSO [240V],N,95,N'
'Enecsys SMI-240-60,N,93.5,Y'
'Enecsys 250NL,N,95.5,Y'
'Enecsys SMI-280-72,N,94.5,Y'
'Enecsys 300-60-xx,N,96,Y'
'Enecsys SMI-480-60,N,94.5,Y'
'Enphase Energy Inc. M175-24-208-Sxx [208V],N,94.5,Y'
'Enphase Energy Inc. M175-24-240-Sxx [240V],N,94.5,Y'
'Enphase Energy Inc. M190-72-208-Sxx [208V],N,95,Y'
'Enphase Energy Inc. M190-72-240-Sxx [240V],N,95,Y'
'Enphase Energy Inc. M200-32-208-Sxx [240V],N,95,Y'
'Enphase Energy Inc. M200-32-240-Sxx [240V],N,95,Y'
#REF!
'Enphase Energy Inc. M210-84-208-Sxx-NA [208V],N,95.5,Y'
'Enphase Energy Inc. M210-84-240-Sxx [240V],N,95.5,Y'
#REF!
#REF!
'Enphase Energy Inc. M215-60-2LL-S2x [208V],N,96,Y'
#REF!
'Enphase Energy Inc. M215-60-2LL-S2x [240V],N,96,Y'
#REF!
'Enphase Energy Inc. M215-60-2LL-S2x-IG [208V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-IG [240V],N,96,Y'
#REF!
'Enphase Energy Inc. M215-60-2LL-S2x-IG-NA [208V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-IG-NA [240V],N,96,Y'
#REF!
'Enphase Energy Inc. M215-60-2LL-S2x-IG-ZC [208V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-IG-ZC [240V],N,96,Y'
#REF!
'Enphase Energy Inc. M215-60-2LL-S2x-IG-ZC-NA [208V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-IG-ZC-NA [240V],N,96,Y'
#REF!
'Enphase Energy Inc. M215-60-2LL-S2x-NA [208V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-NA [240V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-ZC [240V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-ZC-NA [208V],N,96,Y'
'Enphase Energy Inc. M215-60-2LL-S2x-ZC-NA [240V],N,96,Y'
'Enphase Energy Inc. M215-60-SIE-S2x [208V],N,96,Y'
'Enphase Energy Inc. M215-60-SIE-S2x [240V],N,96,Y'
'Enphase Energy Inc. M215-60-SIE-S2x-NA [208V],N,96,Y'
'Enphase Energy Inc. M215-60-SIE-S2x-NA [240V],N,96,Y'
'Enphase Energy Inc. M215-60-SIE-S2x-ZC [208V],N,96,Y'
#REF!
'Enphase Energy Inc. M215-60-SIE-S2x-ZC [240V],N,96,Y'
#REF!
'Enphase Energy Inc. M215-60-SIE-S2x-ZC-NA [208V],N,96,Y'
#REF!
#REF!
#REF!
'Enphase Energy Inc. M215-60-SIE-S2x-ZC-NA [240V],N,96,Y'
#REF!
#REF!
#REF!
'Enphase Energy Inc. S230-60-LL-x [208V],N,97,Y'
#REF!
#REF!
#REF!
'Enphase Energy Inc. S230-60-LL-x [240V],N,97,Y'
#REF!
#REF!
'Enphase Energy Inc. IQ6-60-ACM-US [208V],N,97,Y'
#REF!
#REF!
'Enphase Energy Inc. IQ6-60-ACM-US [240V],N,97,Y'
#REF!
#REF!
'Enphase Energy Inc. IQ6-60-x-US [208V],N,97,Y'
#REF!
#REF!
'Enphase Energy Inc. IQ6-60-x-US [240V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ7-60-x-ACM-US [208V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ7-60-x-ACM-US [240V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ7-60-x-US [208V],N,97,Y'
'Enphase Energy Inc. IQ7-60-x-US [240V],N,97,Y'
'Enphase Energy Inc. M250-60-2LL-S2x (-ZC) (-NA) [208V],N,96,Y'
'Enphase Energy Inc. M250-60-2LL-S2x (-ZC) (-NA) [240V],N,96.5,Y'
'Enphase Energy Inc. M250-72-2LL-S2x [208V],N,96.5,Y'
'Enphase Energy Inc. M250-72-2LL-S2x [240V],N,96.5,Y'
#REF!
'Enphase Energy Inc. C250-72-2LN-S2,N,96.5,Y'
#REF!
'Enphase Energy Inc. IQ6PLUS-ACB-LL [240V],N,95.5,Y'
#REF!
'Enphase Energy Inc. S280-60-LL-x [208V],N,96.5,Y'
#REF!
'Enphase Energy Inc. S280-60-LL-x [240V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ6PLUS-72-ACM-US [208V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ6PLUS-72-ACM-US [240V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ6PLUS-72-x-US [208V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ6PLUS-72-x-US [240V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ7PLUS-72-x-ACM-US [208V],N,96.5,Y'
#REF!
'Enphase Energy Inc. IQ7PLUS-72-x-ACM-US [240V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ7PLUS-72-x-US [208V],N,96.5,Y'
#REF!
'Enphase Energy Inc. IQ7PLUS-72-x-US [240V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ7X-96-x-ACM-US [208V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ7X-96-x-ACM-US [240V],N,97.5,Y'
#REF!
'Enphase Energy Inc. IQ7X-96-x-US [208V],N,97,Y'
#REF!
'Enphase Energy Inc. IQ7X-96-x-US [240V],N,97.5,Y'
#REF!
'Enphase Energy Inc. IQ7XS-96-y-ACM-z [208V],N,97,Y'
'Enphase Energy Inc. IQ7XS-96-y-ACM-z [240V],N,97.5,Y'
'Enphase Energy Inc. D380-72-208-S1x [208V],N,95,Y'
'Enphase Energy Inc. D380-72-240-S1x [240V],N,95,Y'
'Enphase Energy Inc. D380-72-2LL-S1x [208V],N,95,Y'
'Enphase Energy Inc. D380-72-2LL-S1x [240V],N,95,Y'
'Enphase Energy Inc. D380-72-2LL-S1x-NA [208V],N,95,Y'
'Enphase Energy Inc. D380-72-2LL-S1x-NA [240V],N,95,Y'
'Eoplly New Energy Technology EP156M/60-230S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-230S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-235S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-235S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-240S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-240S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-245S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-245S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-250S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-250S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-255S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-255S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-260S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-260S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-230S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-230S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-235S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-235S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-240S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-240S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-245S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-245S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-250S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156MB/60-250S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-225S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-225S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-230S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-230S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-235S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-235S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-240S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-240S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-245S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-245S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-250S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-250S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-255S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-255S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-260S AC [208V],N,96,Y'
'Eoplly New Energy Technology EP156P/60-260S AC [240V],N,96,Y'
'Eoplly New Energy Technology EP156M/60-250 AC [208V],N,95,Y'
'Eoplly New Energy Technology EP156M/60-250 AC [240V],N,95,Y'
'Eoplly New Energy Technology EP156M/60-255 AC [208V],N,95,Y'
'Eoplly New Energy Technology EP156M/60-255 AC [240V],N,95,Y'
'Eoplly New Energy Technology EP156M/60-260 AC [208V],N,95,Y'
'Eoplly New Energy Technology EP156M/60-260 AC [240V],N,95,Y'
'Eoplly New Energy Technology EP156MB/60-240 AC [208V],N,95,Y'
'Eoplly New Energy Technology EP156MB/60-240 AC [240V],N,95,Y'
'Eoplly New Energy Technology EP156MB/60-245 AC [208V],N,95,Y'
'Eoplly New Energy Technology EP156MB/60-245 AC [240V],N,95,Y'
'Eoplly New Energy Technology EP156P/60-240 AC [208V],N,95,Y'
'Eoplly New Energy Technology EP156P/60-240 AC [240V],N,95,Y'
'Eoplly New Energy Technology EP156P/60-245 AC [208V],N,95,Y'
'Eoplly New Energy Technology EP156P/60-245 AC [240V],N,95,Y'
'ET Solar Industry ET-P660245BAC [240V],N,95,Y'
'ET Solar Industry ET-P660245BBAC [240V],N,95,Y'
'ET Solar Industry ET-P660245BBZAC [240V],N,95,Y'
'ET Solar Industry ET-P660245WBZAC [240V],N,95,Y'
'ET Solar Industry ET-P660250 WBAC [240V],N,95,Y'
'ET Solar Industry ET-P660250 WBZAC [240V],N,95,Y'
'ET Solar Industry ET-P660250BAC [240V],N,95,Y'
'ET Solar Industry ET-P660250BBAC [240V],N,95,Y'
'ET Solar Industry ET-P660250BBZAC [240V],N,95,Y'
'ET Solar Industry ET-P660255BBAC,N,95,Y'
'ET Solar Industry ET-P660255BBZAC,N,95,Y'
'ET Solar Industry ET-P660255WBAC,N,95,Y'
'ET Solar Industry ET-P660255WBZAC,N,95,Y'
'ET Solar Industry ET-P660255WWAC,N,95,Y'
'ET Solar Industry ET-P660255WWZAC,N,95,Y'
'ET Solar Industry ET-P660260WBAC,N,95,Y'
'ET Solar Industry ET-P660260WBZAC,N,95,Y'
'ET Solar Industry ET-P660260WWAC,N,95,Y'
'ET Solar Industry ET-P660260WWZAC,N,95,Y'
'ETM Electromatic 290-480-60,Y,96.5,N'
'E-Village Solar EVS1100EVR [120V],Y,90.5,N'
'E-Village Solar EVS2500 [240V],Y,94.5,N'
'E-Village Solar EVS3000 [240V],Y,93.5,N'
'E-Village Solar EVS3500 [240V],Y,95.5,N'
'E-Village Solar EVS4600 [208V],Y,95.5,N'
#REF!
'E-Village Solar EVS4800 [240V],Y,96,N'
'E-Village Solar EVS5200 [208V],Y,96,N'
'Exeltech AC2-1-2-6-5-XX [120V],N,94.5,Y'
'Exeltech AC2-1-B-6-5-XX [120V],N,94.5,Y'
'Exeltech AC2-1-C-6-5-XX [120V],N,94.5,Y'
'Exeltech AC2-1-L-6-5-XX [120V],N,94.5,Y'
'Exeltech AM24-1-B-6-0-00 [120V],N,94.5,Y'
'Exeltech XLGT18A60 [120V],Y,96.5,N'
'Exeltech XLGT18A60-01 [120V],Y,96.5,N'
'Flextronics Industrial FLV-IA-6.0S1UA,Y,97.5,N'
'Flextronics Industrial FLV-IA-7.0S1UA,Y,97.5,N'
'Flextronics Industrial FLV-IA-7.6S1UA,Y,97.5,N'
'Flextronics Industrial FLV-IA-8.0S1UA,Y,97.5,N'
'Flextronics Industrial FLV-IA-9.0S1UA,Y,97.5,N'
'Flextronics Industrial FLV-IA-10.0S1UA,Y,97.5,N'
'Friem RECon 30L-100-US,Y,98,N'
'Friem RECon 30H-150-US [300V],Y,98,N'
'Fronius International GmbH Fronius Primo 3.8-1 208-240 [208V],Y,96,N'
'Fronius International GmbH Fronius Primo 3.8-1 208-240 [240V],Y,95.5,N'
'Fronius International GmbH Fronius Primo 5.0-1 208-240 [208V],Y,96.5,N'
'Fronius International GmbH Fronius Primo 5.0-1 208-240 [240V],Y,96.5,N'
'Fronius International GmbH Fronius Primo 6.0-1 208-240 [208V],Y,96.5,N'
'Fronius International GmbH Fronius Primo 6.0-1 208-240 [240V],Y,96.5,N'
#REF!
'Fronius International GmbH Fronius Primo 7.6-1 208-240 [208V],Y,97,N'
#REF!
'Fronius International GmbH Fronius Primo 7.6-1 208-240 [240V],Y,97,N'
#REF!
'Fronius International GmbH Fronius Primo 8.2-1 208-240 [208V],Y,97,N'
'Fronius International GmbH Fronius Primo 8.2-1 208-240 [240V],Y,97,N'
'Fronius International GmbH Fronius Primo 10.0-1 [208V],Y,96.5,N'
'Fronius International GmbH Fronius Primo 10.0-1 [240V],Y,96.5,N'
'Fronius International GmbH Fronius Symo 10.0-3 208-240 [208V],Y,96.5,N'
'Fronius International GmbH Fronius Symo 10.0-3 208-240 [240V],Y,96.5,N'
'Fronius International GmbH Fronius Symo 10.0-3 480 [480V],Y,96.5,N'
'Fronius International GmbH Fronius Primo 11.4-1 [208V],Y,96.5,N'
'Fronius International GmbH Fronius Primo 11.4-1 [240V],Y,96.5,N'
'Fronius International GmbH Fronius Symo 12.0-3 208-240 [208V],Y,96.5,N'
'Fronius International GmbH Fronius Symo 12.0-3 208-240 [240V],Y,96.5,N'
'Fronius International GmbH Fronius Primo 12.5-1 [208V],Y,96.5,N'
'Fronius International GmbH Fronius Primo 12.5-1 [240V],Y,96.5,N'
'Fronius International GmbH Fronius Symo 12.5-3 480 [480V],Y,97,N'
'Fronius International GmbH Fronius Primo 15.0-1 [208V],Y,97,N'
'Fronius International GmbH Fronius Primo 15.0-1 [240V],Y,97,N'
'Fronius International GmbH Fronius Symo 15.0-3 [208V],Y,96.5,N'
'Fronius International GmbH Fronius Symo 15.0-3 480 [480V],Y,97,N'
'Fronius International GmbH Fronius Symo 17.5-3 480 [480V],Y,97.5,N'
'Fronius International GmbH Fronius Symo 20.0-3 480 [480V],Y,97.5,N'
'Fronius International GmbH Fronius Symo 22.7-3 480 [480V],Y,97.5,N'
'Fronius International GmbH Fronius Symo 24.0-3 480 [480V],Y,97.5,N'
'Fronius USA Galvo 1.5-1 208-240 [208V],Y,94,N'
'Fronius USA Galvo 1.5-1 208-240 [240V],Y,94.5,N'
'Fronius USA Galvo 2.0-1 208-240 [208V],Y,94.5,N'
'Fronius USA Galvo 2.0-1 208-240 [240V],Y,94.5,N'
'Fronius USA IG 2000 NEG,Y,93.5,N'
'Fronius USA IG 2000 POS,Y,93.5,N'
'Fronius USA IG 2500-LV NEG,Y,93,N'
'Fronius USA IG 2500-LV POS,Y,93,N'
'Fronius USA Galvo 2.5-1 208-240 [208V],Y,95,N'
'Fronius USA Galvo 2.5-1 208-240 [240V],Y,95,N'
'Fronius USA IG 3000 NEG,Y,94,N'
'Fronius USA IG 3000 POS,Y,94,N'
'Fronius USA Galvo 3.1-1 208-240 [208V],Y,95,N'
'Fronius USA IG Plus 3.0-1 UNI [208V],Y,95,N'
'Fronius USA IG Plus 3.0-1 UNI [240V],Y,95.5,N'
'Fronius USA IG Plus 3.0-1 UNI [277V],Y,95.5,N'
'Fronius USA IG Plus A 3.0 [208V],Y,95,N'
'Fronius USA IG Plus A 3.0 [240V],Y,95.5,N'
'Fronius USA IG Plus A 3.0 [277V],Y,96,N'
'Fronius USA IG Plus V 3.0 [208V],Y,95,N'
'Fronius USA IG Plus V 3.0 [240V],Y,95.5,N'
'Fronius USA IG Plus V 3.0 [277V],Y,96,N'
'Fronius USA Galvo 3.1-1 208-240 [240V],Y,95.5,N'
'Fronius USA Fronius Primo 3.8-1 208-240 [208V],Y,96,N'
'Fronius USA Fronius Primo 3.8-1 208-240 [240V],Y,95.5,N'
'Fronius USA IG Plus 3.8-1 UNI [208V],Y,95,N'
'Fronius USA IG Plus 3.8-1 UNI [240V],Y,95.5,N'
'Fronius USA IG Plus 3.8-1 UNI [277V],Y,95.5,N'
'Fronius USA IG Plus A 3.8 [208V],Y,95,N'
'Fronius USA IG Plus A 3.8 [240V],Y,95.5,N'
'Fronius USA IG Plus A 3.8 [277V],Y,96,N'
'Fronius USA IG Plus V 3.8 [208V],Y,95,N'
'Fronius USA IG Plus V 3.8 [240V],Y,95.5,N'
'Fronius USA IG Plus V 3.8 [277V],Y,96,N'
'Fronius USA IG 4000 NEG,Y,94,N'
'Fronius USA IG 4000 POS,Y,94,N'
'Fronius USA IG 4500-LV NEG,Y,93.5,N'
'Fronius USA IG 4500-LV POS,Y,93.5,N'
'Fronius USA Fronius Primo 5.0-1 208-240 [208V],Y,96.5,N'
'Fronius USA Fronius Primo 5.0-1 208-240 [240V],Y,96.5,N'
'Fronius USA IG Plus 5.0-1 UNI [208V],Y,95.5,N'
'Fronius USA IG Plus 5.0-1 UNI [240V],Y,95.5,N'
'Fronius USA IG Plus 5.0-1 UNI [277V],Y,96,N'
'Fronius USA IG Plus A 5.0 [208V],Y,95.5,N'
'Fronius USA IG Plus A 5.0 [240V],Y,95.5,N'
'Fronius USA IG Plus A 5.0 [277V],Y,96,N'
'Fronius USA IG Plus V 5.0 [208V],Y,95.5,N'
'Fronius USA IG Plus V 5.0 [240V],Y,95.5,N'
'Fronius USA IG Plus V 5.0 [277V],Y,96,N'
'Fronius USA IG 5100 NEG,Y,94.5,N'
'Fronius USA IG 5100 POS,Y,94.5,N'
'Fronius USA Fronius Primo 6.0-1 208-240 [208V],Y,96.5,N'
'Fronius USA Fronius Primo 6.0-1 208-240 [240V],Y,96.5,N'
'Fronius USA IG Plus 6.0-1 UNI [208V],Y,95.5,N'
'Fronius USA IG Plus 6.0-1 UNI [240V],Y,96,N'
'Fronius USA IG Plus 6.0-1 UNI [277V],Y,96,N'
'Fronius USA IG Plus A 6.0 [208V],Y,95.5,N'
'Fronius USA IG Plus A 6.0 [240V],Y,96,N'
'Fronius USA IG Plus A 6.0 [277V],Y,96,N'
'Fronius USA IG Plus V 6.0 [208V],Y,95.5,N'
'Fronius USA IG Plus V 6.0 [240V],Y,96,N'
'Fronius USA IG Plus V 6.0 [277V],Y,96,N'
'Fronius USA IG Plus 7.5-1 UNI [208V],Y,95,N'
'Fronius USA IG Plus 7.5-1 UNI [240V],Y,95.5,N'
'Fronius USA IG Plus 7.5-1 UNI [277V],Y,96,N'
'Fronius USA IG Plus A 7.5 [208V],Y,95,N'
'Fronius USA IG Plus A 7.5 [240V],Y,95.5,N'
'Fronius USA IG Plus A 7.5 [277V],Y,96,N'
'Fronius USA IG Plus V 7.5 [208V],Y,95,N'
'Fronius USA IG Plus V 7.5 [240V],Y,95.5,N'
'Fronius USA IG Plus V 7.5 [277V],Y,96,N'
'Fronius USA Fronius Primo 7.6-1 208-240 [208V],Y,97,N'
'Fronius USA Fronius Primo 7.6-1 208-240 [240V],Y,97,N'
'Fronius USA Fronius Primo 8.2-1 208-240 [208V],Y,97,N'
'Fronius USA Fronius Primo 8.2-1 208-240 [240V],Y,97,N'
'Fronius USA Fronius Primo 10.0-1 [208V],Y,96.5,N'
'Fronius USA Fronius Primo 10.0-1 [240V],Y,96.5,N'
'Fronius USA Fronius Symo 10.0-3 208-240 [208V],Y,96.5,N'
'Fronius USA Fronius Symo 10.0-3 208-240 [240V],Y,96.5,N'
'Fronius USA Fronius Symo 10.0-3 480 [480V],Y,96.5,N'
'Fronius USA IG Plus 10.0-1 UNI [208V],Y,95,N'
'Fronius USA IG Plus 10.0-1 UNI [240V],Y,95.5,N'
'Fronius USA IG Plus 10.0-1 UNI [277V],Y,96,N'
'Fronius USA IG Plus V 10.0-3 Delta [208V],Y,95.5,N'
'Fronius USA IG Plus V 10.0-3 Delta [240V],Y,95.5,N'
'Fronius USA IG Plus A 10.0 [208V],Y,95,N'
'Fronius USA IG Plus A 10.0 [240V],Y,95.5,N'
'Fronius USA IG Plus A 10.0 [277V],Y,96,N'
'Fronius USA IG Plus A 10.0-3 Delta [208V],Y,95.5,N'
'Fronius USA IG Plus A 10.0-3 Delta [240V],Y,95.5,N'
'Fronius USA IG Plus V 10.0 [208V],Y,95,N'
'Fronius USA IG Plus V 10.0 [240V],Y,95.5,N'
'Fronius USA IG Plus V 10.0 [277V],Y,96,N'
'Fronius USA Fronius Primo 11.4-1 [208V],Y,96.5,N'
'Fronius USA Fronius Primo 11.4-1 [240V],Y,96.5,N'
'Fronius USA IG Plus 11.4-1 UNI [208V],Y,95.5,N'
'Fronius USA IG Plus 11.4-1 UNI [240V],Y,96,N'
'Fronius USA IG Plus 11.4-1 UNI [277V],Y,96,N'
'Fronius USA IG Plus 11.4-3 Delta [208V],Y,95,N'
'Fronius USA IG Plus 11.4-3 Delta [240V],Y,95.5,N'
'Fronius USA IG Plus A 11.4 [208V],Y,95,N'
'Fronius USA IG Plus A 11.4 [240V],Y,95.5,N'
'Fronius USA IG Plus A 11.4 [277V],Y,96,N'
'Fronius USA IG Plus A 11.4-3 Delta [208V],Y,95,N'
'Fronius USA IG Plus A 11.4-3 Delta [240V],Y,96,N'
'Fronius USA IG Plus V 11.4 [208V],Y,95,N'
'Fronius USA IG Plus V 11.4 [240V],Y,95.5,N'
'Fronius USA IG Plus V 11.4 [277V],Y,96,N'
'Fronius USA IG Plus V 11.4-3 Delta [208V],Y,95,N'
'Fronius USA IG Plus V 11.4-3 Delta [240V],Y,96,N'
'Fronius USA Fronius Symo 12.0-3 208-240 [208V],Y,96.5,N'
'Fronius USA Fronius Symo 12.0-3 208-240 [240V],Y,96.5,N'
'Fronius USA IG Plus 12.0-3 WYE [277V],Y,96,N'
'Fronius USA IG Plus A 12.0-3 WYE [277V],Y,96,N'
'Fronius USA IG Plus V 12.0-3 WYE [277V],Y,96,N'
'Fronius USA Fronius Primo 12.5-1 [208V],Y,96.5,N'
'Fronius USA Fronius Primo 12.5-1 [240V],Y,96.5,N'
'Fronius USA Fronius Symo 12.5-3 480 [480V],Y,97,N'
'Fronius USA Fronius Primo 15.0-1 [208V],Y,97,N'
'Fronius USA Fronius Primo 15.0-1 [240V],Y,97,N'
'Fronius USA Fronius Symo 15.0-3 [208V],Y,96.5,N'
'Fronius USA Fronius Symo 15.0-3 480 [480V],Y,97,N'
'Fronius USA Fronius Symo 17.5-3 480 [480V],Y,97.5,N'
'Fronius USA Fronius Symo 20.0-3 480 [480V],Y,97,N'
'Fronius USA Fronius Symo 22.7-3 480 [480V],Y,97.5,N'
'Fronius USA Fronius Symo 24.0-3 480 [480V],Y,97.5,N'
'Fronius USA CL 33.3 Delta [208V],Y,94.5,N'
'Fronius USA CL 33.3 Delta [240V],Y,95,N'
'Fronius USA CL 36.0 Wye [277V],Y,95.5,N'
'Fronius USA CL 44.4 Delta [208V],Y,94.5,N'
'Fronius USA CL 44.4 Delta [240V],Y,95,N'
'Fronius USA CL 48.0 Wye [277V],Y,95.5,N'
'Fronius USA CL 55.5 Delta [208V],Y,94.5,N'
'Fronius USA CL 55.5 Delta [240V],Y,95,N'
'Fronius USA CL 60.0 Wye [277V],Y,95.5,N'
'FSP Group FSP600PV-NA-208 [208V],N,95,Y'
'FSP Group FSP600PV-NA-240 [240V],N,95,Y'
'FSP Group FSP600PV-NA-277 [277V],N,95,Y'
'GAF RIAC 1000 [208V],N,96,Y'
'GAF RIAC 1000 [240V],N,96,Y'
'GE Energy GEPVe-1100-NA-120 [120V],Y,90.5,N'
'GE Energy GEPVe-2000-NA-240 [240V],Y,92,N'
'GE Energy GEPVb-2500-NA-240 [240V],Y,94,N'
'GE Energy GEPVe-2500-NA-240 [240V],Y,94.5,N'
'GE Energy GEPVb-2800-NA-240/208-02 [208V],Y,93.5,N'
'GE Energy GEPVb-2800-NA-240/208-02 [240V],Y,94,N'
'GE Energy GEPVe-2800-NA-208 [208V],Y,92,N'
'GE Energy GEPVb-3000-NA-240 [240V],Y,94.5,N'
'GE Energy GEPVe-3000-NA-240 [240V],Y,93.5,N'
'GE Energy GEPVb-3300-NA-240/208-02 [208V],Y,95,N'
'GE Energy GEPVb-3300-NA-208 [208V],Y,94,N'
'GE Energy GEPVb-3300-NA-240 [240V],Y,94.5,N'
'GE Energy GEPVb-3300-NA-240/208-02 [240V],Y,95.5,N'
'GE Energy GEPVe-3500-NA-240 [240V],Y,95.5,N'
'GE Energy GEPVb-3800-NA-240 [240V],Y,95,N'
'GE Energy GEPVb-4000-NA-240/208-02 [208V],Y,95,N'
'GE Energy GEPVb-4000-NA-240/208-02 [240V],Y,95.5,N'
'GE Energy GEPVb-5000-NA-240/208-02 [208V],Y,95,N'
'GE Energy GEPVe-4600-NA-208 [208V],Y,95.5,N'
'GE Energy GEPVe-4800-NA-240 [240V],Y,96,N'
'GE Energy GEPVb-5000-NA-240/208-02 [240V],Y,95.5,N'
'GE Energy GEPVb-5000-NA-240-01 [240V],Y,95.5,N'
'GE Energy GEPVe-5200-NA-240 [240V],Y,96,N'
'Gefran APV 1700-2M-TL-US [208V],Y,96,N'
'Gefran APV 1700-2M-TL-US [240V],Y,96,N'
'Gefran APV 1700-2M-TL-US [277V],Y,96,N'
'Gefran APV 2300-2M-TL-US [208V],Y,96.5,N'
'Gefran APV 2300-2M-TL-US [240V],Y,96.5,N'
'Gefran APV 3100-2M-TL-US [208V],Y,96.5,N'
'Gefran APV 3100-2M-TL-US [277V],Y,96.5,N'
'Gefran APV 3800-2M-TL-US [240V],Y,97,N'
'Gefran APV 4400-2M-TL-US [208V],Y,97,N'
'Gefran APV 4400-2M-TL-US [277V],Y,97,N'
'Gefran APV 5200-2M-TL-US [240V],Y,97,N'
'General Electric PVIA2000NA1240 [240V],Y,94.5,N'
'General Electric PVIA4000NA1240 [240V],Y,95.5,N'
'Geoprotek Technology GS-1000 [208V],Y,94.5,N'
'Geoprotek Technology GS-1500 [208V],Y,94.5,N'
'Geoprotek Technology GS-2000 [208V],Y,95.5,N'
'Geoprotek Technology GS-3000 [208V],Y,95.5,N'
'Green Power Technologies PV500U + MVT,Y,96,N'
'Green Power Technologies PV630WD,N,96.5,N'
'Green Power Technologies 940WD3-LV400 [400V],N,97,N'
'Green Power Technologies PV900WD,N,97,N'
'Green Power Technologies 1170WD3-LV500 [500V],N,97.5,N'
'Green Power Technologies 1140WD3-HV560 [560V],N,97.5,N'
'Green Power Technologies 1260WD3-HV620 [620V],N,97.5,N'
'Green Power Technologies 1400WD3-HV690 [690V],N,98,N'
'GreenVolts GV-SCP001 [480V],Y,96,N'
'GridPoint Connect C36,N,91,N'
'Growatt New Energy Technology Co., Ltd. Growatt 1500-US [208V],Y,96,N'
'Growatt New Energy Technology Co., Ltd. Growatt 1500-US [240V],Y,96,N'
'Growatt New Energy Technology Co., Ltd. Growatt 1500-US [277V],Y,96,N'
'Growatt New Energy Technology Co., Ltd. Growatt 2000-US [208V],Y,96.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 2000HF-US [208V],Y,95.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 2000HF-US [240V],Y,95.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 2000-US [240V],Y,96.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 2000-US [277V],Y,96.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 2500HF-US [208V],Y,95.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 2500HF-US [240V],Y,95.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 3000-US [208V],Y,96.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 3000-US [240V],Y,96.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 3000-US [277V],Y,96.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 3000HF-US [208V],Y,95.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 3000HF-US [240V],Y,95.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 3600 MTL-US [208V],Y,97,N'
'Growatt New Energy Technology Co., Ltd. Growatt 3600 MTL-US [240V],Y,97,N'
'Growatt New Energy Technology Co., Ltd. Growatt 3600 MTL-US [277V],Y,97,N'
'Growatt New Energy Technology Co., Ltd. Growatt 4000MTLP-US [208V],Y,95.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 4000MTLP-US [240V],Y,96,N'
'Growatt New Energy Technology Co., Ltd. Growatt 4000MTLP-US [277V],Y,96,N'
'Growatt New Energy Technology Co., Ltd. Growatt 4200 MTL-US [208V],Y,97,N'
'Growatt New Energy Technology Co., Ltd. Growatt 4200 MTL-US [240V],Y,97,N'
'Growatt New Energy Technology Co., Ltd. Growatt 4200 MTL-US [277V],Y,97,N'
'Growatt New Energy Technology Co., Ltd. Growatt 5000MTLP-US [208V],Y,95.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 5000 MTL-US [208V],Y,97,N'
'Growatt New Energy Technology Co., Ltd. Growatt 5000 MTL-US [240V],Y,97,N'
'Growatt New Energy Technology Co., Ltd. Growatt 5000 MTL-US [277V],Y,97,N'
'Growatt New Energy Technology Co., Ltd. Growatt 5000MTLP-US [277V],Y,96.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 5000MTLP-US [240V],Y,96,N'
'Growatt New Energy Technology Co., Ltd. Growatt 6000MTLP-US [208V],Y,96,N'
'Growatt New Energy Technology Co., Ltd. Growatt 6000MTLP-US [240V],Y,96,N'
'Growatt New Energy Technology Co., Ltd. Growatt 6000MTLP-US [277V],Y,96.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 7000MTLP-US [208V],Y,96,N'
'Growatt New Energy Technology Co., Ltd. Growatt 7600MTLP-US [208V],Y,96,N'
'Growatt New Energy Technology Co., Ltd. Growatt 7000MTLP-US [240V],Y,96.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 7000MTLP-US [277V],Y,96.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 7600MTLP-US [240V],Y,96.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 7600MTLP-US [277V],Y,96.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 8000TL-US [208V],Y,96.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 8000TL-US [240V],Y,97,N'
'Growatt New Energy Technology Co., Ltd. Growatt 9000TL-US [208V],Y,96.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 9000TL-US [240V],Y,97,N'
#REF!
#REF!
'Growatt New Energy Technology Co., Ltd. Growatt 10000TL-US [208V],Y,96.5,N'
#REF!
'Growatt New Energy Technology Co., Ltd. Growatt 10000 TL3-US [240V],Y,95.5,N'
#REF!
'Growatt New Energy Technology Co., Ltd. Growatt 12000 TL3-US [277V],Y,95.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 11000TL-US [240V],Y,97,N'
'Growatt New Energy Technology Co., Ltd. Growatt 18000 TL3-US [277V],Y,96,N'
'Growatt New Energy Technology Co., Ltd. Growatt 20000 TL3-US [277V],Y,96.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 33000TL3-US,Y,98.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 36000TL3-US,Y,98.5,N'
'Growatt New Energy Technology Co., Ltd. Growatt 40000TL3-US,Y,98.5,N'
'Hansol Technics HSPV-A250,N,93,N'
'Heart Transverter HT2000,Y,89,N'
'Helios USA 6TA [120V],N,94.5,N'
'HiQ Solar Mini3500-US,N,94.5,N'
'HiQ Solar TS208-5k75 [208V],Y,97,N'
'HiQ Solar TS480-8k [480V],Y,98,N'
'HiQ Solar TSXL480-10k [480V],N,97.5,N'
'HiSEL Power HiSEL-K 1500 [208V],Y,95,N'
'HiSEL Power HiSEL-K 1500 [240V],Y,95,N'
'HiSEL Power HiSEL-K 2000 [208V],Y,95.5,N'
'HiSEL Power HiSEL-K 2000 [240V],Y,96,N'
'HiSEL Power HiSEL-K 3000 [208V],Y,96,N'
'HiSEL Power HiSEL-K 3000 [240V],Y,96,N'
'HiSEL Power HiSEL-K 4000 [208V],Y,97,N'
'HiSEL Power HiSEL-K 4000 [240V],Y,97.5,N'
'HiSEL Power HiSEL-K 5000 [208V],Y,97,N'
'HiSEL Power HiSEL-K 5000 [240V],Y,97.5,N'
'Home Director HD-SUN-INV1100-EVR [120V],Y,90.5,N'
'Home Director HD-SUN-INV2000-EVR [240V],Y,92,N'
'Home Director HD-SUN-INV2500 [240V],Y,94.5,N'
'Home Director HD-SUN-INV3000 [240V],Y,93.5,N'
'Home Director HD-SUN-INV3500 [240V],Y,95.5,N'
'Home Director HD-SUN-INV4600 [208V],Y,95.5,N'
#REF!
'Home Director HD-SUN-INV5200 [240V],Y,96,N'
#REF!
'Hoymiles Converter Technology MI-250 [240V],N,96.5,Y'
#REF!
'Huawei Technologies Co., Ltd. SUN2000-3.8KTL-USL0 [240V],Y,99,N'
#REF!
'Huawei Technologies Co., Ltd. SUN2000-5KTL-USL0 [240V],Y,99,N'
#REF!
'Huawei Technologies Co., Ltd. SUN2000-7.6KTL-USL0 [240V],Y,99,N'
#REF!
'Huawei Technologies Co., Ltd. SUN2000-9KTL-USL0 [240V],Y,99,N'
'Huawei Technologies Co., Ltd. SUN2000-10KTL-USL0 [240V],Y,99,N'
'Huawei Technologies Co., Ltd. SUN2000-11.4KTL-USL0 [240V],Y,99,N'
'Huawei Technologies Co., Ltd. SUN2000-22KTL-US,N,98,N'
'Huawei Technologies Co., Ltd. SUN2000-25KTL-US,Y,98,N'
'Huawei Technologies Co., Ltd. SUN2000-30KTL-US,Y,98,N'
'Huawei Technologies Co., Ltd. SUN2000-33KTL-US,N,98.5,N'
'Huawei Technologies Co., Ltd. SUN2000-33KTL-US [480V],N,98.5,N'
'Huawei Technologies Co., Ltd. SUN2000-36KTL-US,N,98.5,N'
'Huawei Technologies Co., Ltd. SUN2000-36KTL-US [480V],N,98.5,N'
'Huawei Technologies Co., Ltd. SUN2000-40KTL-US,N,98.5,N'
'Huawei Technologies Co., Ltd. SUN2000-40KTL-US [480V],N,98.5,N'
'Huawei Technologies Co., Ltd. SUN2000-45KTL-US-HV-D0,N,98.5,N'
'Huawei Technologies Co., Ltd. SUN2000-45KTL-US-HV-D0 [600V],N,98.5,N'
#REF!
'Huawei Technologies Co., Ltd. SUN2000-100KTL-USH0 [800V],N,98.5,N'
#REF!
'HYOSUNG HS-P1000GLO-U,N,98,N'
'Ideal Power Inc. 30C [480V],N,95,N'
#REF!
'Ideal Power Inc. 30C3 [480V],N,95,N'
'Ideal Power Inc. 30PV,N,95,N'
#REF!
'Ideal Power Inc. 30PV+S [480V],N,95,N'
'Ideal Power Inc. 30PVF,N,95,N'
'Ideal Power Inc. IPV-30 kW-480 [480V],Y,96.5,N'
'i-Energy GT260 [240V],N,92,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 2.8 HF U 240 Vac [240V],Y,95.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 2.8 HF U 277Vac [277V],Y,95.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 2.8 TL U M 208 Vac [208V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 2.8 TL U M 240 Vac [240V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 3.3 HF U 208 Vac [208V],Y,95,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 3.3 HF U 240 Vac [240V],Y,95.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 3.3 HF U 277Vac [277V],Y,95.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 3.3 TL U M 208 Vac [208V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 3.3 TL U M 240 Vac [240V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 3.6TL U 208V [208V],Y,96,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 3.6TL U 240V [240V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 3.6TL U 277 [277V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5 HF U 208 Vac [208V],Y,95,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5 HF U 240 Vac [240V],Y,96,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5 HF U 277Vac [277V],Y,95.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5 TL U M 208 Vac [208V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5 TL U M 240 Vac [240V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5TL U [208V],Y,96,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5TL U [240V],Y,96,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5TL U [277V],Y,96,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5U [208V],Y,95,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5U [240V],Y,95,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 5U [277V],Y,95.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 6 HF U 240 Vac [240V],Y,95.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 6 HF U 277Vac [277V],Y,95,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 6 TL U M 240 Vac [240V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 6TL U 240 [240V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 6TL U 277V [277V],Y,97,N'
#REF!
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 7.5TL U 208 [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 7.5TL U 240 [240V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 7.5TL U 277 [277V],Y,97,N'
#REF!
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 8.6TL U 240 [240V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 8.6TL U 277 [277V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 10TL U [277V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 15U [208V],Y,95,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 15U [480V],Y,95,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 18 TL U M [480V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 24 TL U M [480V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 25U [208V],Y,95.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 25U [480V],Y,95.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 40TL U M [480V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 100U [208V],Y,94.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 100U [240V],Y,94.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 100UP [208V],Y,95,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 100UP [480V],Y,95.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 125 TL U 208 Outdoor [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 125 U 208 Outdoor [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 125 U 480 Outdoor [480V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 165 TL U 275 Outdoor [275V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 200 TL U 330 Outdoor [330V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 220 TL U 360 Outdoor [360V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 375TL X208 Indoor [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 375TL X208 Outdoor [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 500T U X480 Indoor [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 500T U X480 Outdoor [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 500TL U X208 Indoor [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 500TL U X208 Outdoor [208V],Y,96.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 500TL U X275 Indoor [275V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 600TL U X330 Indoor [330V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 600TL U X330 Outdoor [330V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 600TL X330 Outdoor [330V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 610TL U B220 Indoor [220V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 610TL U B220 Outdoor [300V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 660TL U X275 Indoor [275V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 660TL U X275 Outdoor [275V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 660TL X360 Indoor [360V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 660TL X360 Outdoor [360V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 800TL U X330 Indoor [330V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 800TL U X330 Outdoor [330V],Y,97,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 830TL U B300 Indoor [300V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 830TL U B300 Outdoor [300V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 880TL X360 Indoor [360V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. INGECON SUN 880TL X360 Outdoor [360V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 915TL U B330 Indoor [330V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 915TL U B330 Outdoor [330V],N,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1000TL U B360 Indoor [360V],N,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1000TL U B360 Outdoor [360V],N,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1110TL U B400 Indoor [400V],N,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1110TL U B400 Outdoor [400V],N,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1165TL U B420 Indoor [420V],N,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1165TL U B420 Outdoor [420V],N,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1170TL U B450 Indoor [450V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1170TL U B450 Outdoor [450V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1400TL U B540 Indoor [450V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1400TL U B540 Outdoor [450V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1500TL U B578 Indoor [450V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1500TL U B578 Outdoor [450V],Y,97.5,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1560TL U B600 Indoor [450V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1560TL U B600 Outdoor [450V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1600TL U B615 Indoor [450V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1600TL U B615 Outdoor [450V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1640TL U B630 Indoor [450V],Y,98,N'
'INGETEAM POWER TECHNOLOGY S.A. Ingecon Sun 1640TL U B630 Outdoor [450V],Y,98,N'
'Involar MAC250A-240-NA,N,93,N'
'Involar MAC500-XX,N,94.5,Y'
'iPower SHO-1.1 [120V],Y,90.5,N'
'iPower SHO-2.0 [240V],Y,92,N'
'iPower SHO-2.5 [240V],Y,94.5,N'
'iPower SHO-3.0 [240V],Y,93.5,N'
'iPower SHO-3.5 [240V],Y,95.5,N'
'iPower SHO-4.6 [208V],Y,95.5,N'
'iPower SHO-4.8 [240V],Y,96,N'
'iPower SHO-5.2 [240V],Y,96,N'
'Jema Energy JAE7140,N,95.5,N'
'Jema Energy JAE7141,N,95,N'
'Jema Energy IF500TL-UL OUTDOOR,Y,96,N'
'Jema Energy IF600TL-UL OUTDOOR,Y,96,N'
'Jiangsu Zeversolar New Energy Evershine TL3000-US-208,Y,96,N'
'Jiangsu Zeversolar New Energy Evershine TL3000-US-240,Y,96.5,N'
'Jiangsu Zeversolar New Energy Evershine TL4000-US-208,Y,96.5,N'
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
'Jiangsu Zeversolar New Energy Evershine TL4000-US-240,Y,96.5,N'
'Jiangsu Zeversolar New Energy Evershine TL5000-US-208,Y,96,N'
'Jiangsu Zeversolar New Energy Evershine TL5000-US-240,Y,96.5,N'
'Jiangsu Zeversolar New Energy Evershine TL6000-US-208,Y,96,N'
'Jiangsu Zeversolar New Energy Evershine TL6000-US-240,Y,96.5,N'
'Jiangyin Hareon Power HR-240P-AC/Bb [208V],N,95,Y'
'Jiangyin Hareon Power HR-240P-AC/Bb [240V],N,95,Y'
'Jiangyin Hareon Power HR-240P-AC/BbP [208V],N,95,Y'
'Jiangyin Hareon Power HR-240P-AC/BbP [240V],N,95,Y'
'Jiangyin Hareon Power HR-245P-AC/Bb [208V],N,95,Y'
'Jiangyin Hareon Power HR-245P-AC/Bb [240V],N,95,Y'
'Jiangyin Hareon Power HR-245P-AC/BbP [208V],N,95,Y'
'Jiangyin Hareon Power HR-245P-AC/BbP [240V],N,95,Y'
'Jiangyin Hareon Power HR-250-AC/Cb [208V],N,95,Y'
'Jiangyin Hareon Power HR-250-AC/Cb [240V],N,95,Y'
'Jiangyin Hareon Power HR-250P-AC/Bb [208V],N,95,Y'
'Jiangyin Hareon Power HR-250P-AC/Bb [240V],N,95,Y'
'Jiangyin Hareon Power HR-250P-AC/BbP [208V],N,95,Y'
'Jiangyin Hareon Power HR-250P-AC/BbP [240V],N,95,Y'
'Jiangyin Hareon Power HR-255-AC/Cb [208V],N,95,Y'
'Jiangyin Hareon Power HR-255-AC/Cb [240V],N,95,Y'
'Jiangyin Hareon Power HR-255P-AC/Bb [208V],N,95,Y'
'Jiangyin Hareon Power HR-255P-AC/Bb [240V],N,95,Y'
'Jiangyin Hareon Power HR-255P-AC/BbP [208V],N,95,Y'
'Jiangyin Hareon Power HR-255P-AC/BbP [240V],N,95,Y'
'Jiangyin Hareon Power HR-260-AC/Cb [208V],N,95,Y'
'Jiangyin Hareon Power HR-260-AC/Cb [240V],N,95,Y'
'Jiangyin Hareon Power HR-260P-AC/Bb [208V],N,95,Y'
'Jiangyin Hareon Power HR-260P-AC/Bb [240V],N,95,Y'
'Jiangyin Hareon Power HR-260P-AC/BbP [208V],N,95,Y'
'Jiangyin Hareon Power HR-260P-AC/BbP [240V],N,95,Y'
'Jiangyin Hareon Power HR-265-AC/Cb [208V],N,95,Y'
'Jiangyin Hareon Power HR-265-AC/Cb [240V],N,95,Y'
'Jiangyin Hareon Power HR-270-AC/Cb [208V],N,95,Y'
'Jiangyin Hareon Power HR-270-AC/Cb [240V],N,95,Y'
'Jinko Solar Co.,Ltd. JKMS260M-60B-EP [240V],N,97,Y'
'Jinko Solar Co.,Ltd. JKMS265M-60B-EP [240V],N,97,Y'
'Jinko Solar Co.,Ltd. JKMS270M-60B-EP [240V],N,97,Y'
'Jinko Solar Co.,Ltd. JKMS275M-60B-EP [240V],N,97,Y'
'Jinko Solar Co.,Ltd. JKMS275M-60-EP [240V],N,97,Y'
'Jinko Solar Co.,Ltd. JKMS280M-60B-EP [240V],N,97,Y'
'Jinko Solar Co.,Ltd. JKMS280M-60-EP [240V],N,97,Y'
'Jinko Solar Co.,Ltd. JKMS285M-60B-EP [240V],N,97,Y'
'Jinko Solar Co.,Ltd. JKMS285M-60-EP [240V],N,97,Y'
'Jinko Solar Co.,Ltd. JKMS290M-60B-EP [240V],N,97,Y'
'Jinko Solar Co.,Ltd. JKMS290M-60-EP [240V],N,97,Y'
'Jinko Solar Co.,Ltd. JKMS295M-60B-EP [240V],N,97,Y'
'Jinko Solar Co.,Ltd. JKMS295M-60-EP [240V],N,97,Y'
'Jinko Solar Co.,Ltd. JKMS300M-60-EP [240V],N,97,Y'
'KACO blueplanet Ultraverter 250,N,97.5,Y'
'KACO blueplanet 1501xi [240V],Y,95,N'
'KACO blueplanet 1502x [208V],Y,95.5,N'
'KACO blueplanet 1502xi [208V],Y,95.5,N'
'KACO blueplanet 1502x [240V],Y,94,N'
'KACO blueplanet 1502xi [240V],Y,94,N'
'KACO blueplanet 2.0 TL1 M1 WM OD US3x [208V],Y,96,N'
'KACO blueplanet 2.0 TL1 M1 WM OD US3x [240V],Y,96.5,N'
'KACO blueplanet 2502x [208V],Y,95,N'
'KACO blueplanet 2502x [240V],Y,95.5,N'
'KACO blueplanet 2502xi [208V],Y,95,N'
'KACO blueplanet 2502xi [240V],Y,95.5,N'
'KACO blueplanet 2901xi [240V],Y,94,N'
'KACO blueplanet 3.0 TL1 M1 WM OD US3x [208V],Y,96,N'
'KACO blueplanet 3.0 TL1 M1 WM OD US3x [240V],Y,96.5,N'
'KACO blueplanet 3502x [208V],Y,95.5,N'
'KACO blueplanet 3502x [240V],Y,95.5,N'
'KACO blueplanet 3502xi [208V],Y,95.5,N'
'KACO blueplanet 3502xi [240V],Y,95.5,N'
'KACO blueplanet 3601xi [240V],Y,93.5,N'
'KACO blueplanet 4.0 TL1 M1 WM OD US3x [208V],Y,96.5,N'
'KACO blueplanet 4.0 TL1 M1 WM OD US3x [240V],Y,96.5,N'
'KACO blueplanet 5.0 TL1 M1 WM OD US3x [208V],Y,96.5,N'
'KACO blueplanet 5002x [208V],Y,95,N'
'KACO blueplanet 5002x [240V],Y,95.5,N'
'KACO blueplanet 5002xi [208V],Y,95,N'
'KACO blueplanet 5002xi [240V],Y,95.5,N'
'KACO blueplanet 5.0 TL1 M1 WM OD US3x [240V],Y,96.5,N'
'KACO blueplanet 6400M [208V],Y,96.5,N'
'KACO blueplanet 6400M [240V],Y,96.5,N'
'KACO blueplanet 6400x [208V],Y,96.5,N'
'KACO blueplanet 6400x [240V],Y,96.5,N'
'KACO blueplanet 6400xi [208V],Y,96.5,N'
'KACO blueplanet 6400xi [240V],Y,96.5,N'
'KACO blueplanet 7600M [208V],Y,96.5,N'
'KACO blueplanet 7600M [240V],Y,96.5,N'
'KACO blueplanet 7600x [208V],Y,96.5,N'
'KACO blueplanet 7600x [240V],Y,96.5,N'
'KACO blueplanet 7600xi [208V],Y,96.5,N'
'KACO blueplanet 7600xi [240V],Y,96.5,N'
'KACO blueplanet 10.0 TL3 [480V],Y,97,N'
'KACO XP10U-H4 (-PSD) [480V],Y,97,N'
'KACO blueplanet 32.0 TL3 M1 [480V],Y,97,N'
'KACO blueplanet 32.0 TL3 M3 [480V],Y,97,N'
'KACO blueplanet 40.0 TL3 M1 [480V],Y,97.5,N'
'KACO blueplanet 40.0 TL3 M3 [480V],Y,97.5,N'
'KACO XP42U-H2 [208V],Y,95.5,N'
'KACO blueplanet 50.0 TL3 M1 [480V],Y,97.5,N'
'KACO blueplanet 50.0 TL3 M3 [480V],Y,97.5,N'
'KACO XP50U-H4 [480V],Y,96,N'
'KACO XP100U-H2 [480V],Y,95.5,N'
'KACO XP100U-H4 [480V],Y,96,N'
'KACO XP500U-TL,Y,98,N'
'KACO XP550U-TL,Y,98,N'
'KACO KACO blueplanet 750 TL3 750 TL3 M1 GM OD USX0,Y,98,N'
'KACO KACO blueplanet 875 TL3 875 TL3 M1 GM OD USX0,Y,98,N'
'KACO KACO blueplanet 1000 TL3 1000 TL3 M1 GM OD USX0,Y,98,N'
'KACO KACO blueplanet 1500 TL3 M1 GM OD USX0,Y,98,N'
'KACO KACO blueplanet 2200 TL3 M1 GM OD USX0,Y,98,N'
#REF!
'Kostal Solar Electric Piko 5.3 US,Y,94,N'
'LeadSolar Energy Co., Ltd LS560 [240V],N,95.5,Y'
'LeadSolar Energy Co., Ltd LS600 [240V],N,95.5,Y'
'LeadSolar Energy Co., Ltd LS600T [208V],N,95,Y'
'LeadSolar Energy Co., Ltd LS600ES [277V],N,96,Y'
'LeadSolar Energy Co., Ltd LS700TS-208 [208V],N,95.5,Y'
'LeadSolar Energy Co., Ltd LS650S [277V],N,96,Y'
'LeadSolar Energy Co., Ltd LS700S [277V],N,96,Y'
'LeadSolar Energy Co., Ltd LS700TS-240 [240V],N,95.5,Y'
'LeadSolar Energy Co., Ltd LS600X [240V],N,96,Y'
#REF!
'LeadSolar Energy Co.,Ltd LS1400-240V [240V],N,95,Y'
#REF!
'Leatec Fine Ceramics CM21-0113 [240V],N,96,Y'
#REF!
'LG Electronics Inc. LG315E1K-A5 [208V],N,97,Y'
#REF!
'LG Electronics Inc. LG315E1K-A5 [240V],N,97,Y'
#REF!
'LG Electronics Inc. LG320E1K-A5 [208V],N,97,Y'
#REF!
'LG Electronics Inc. LG320E1K-A5 [240V],N,97,Y'
#REF!
'LG Electronics Inc. LG325E1C-A5 [208V],N,97,Y'
#REF!
'LG Electronics Inc. LG325E1C-A5 [240V],N,97,Y'
#REF!
'LG Electronics Inc. LG325E1K-A5 [208V],N,97,Y'
#REF!
'LG Electronics Inc. LG325E1K-A5 [240V],N,97,Y'
#REF!
'LG Electronics Inc. LG330E1C-A5 [208V],N,97,Y'
#REF!
'LG Electronics Inc. LG330E1C-A5 [240V],N,97,Y'
'LG Electronics Inc. LG335E1C-A5 [208V],N,97,Y'
'LG Electronics Inc. LG335E1C-A5 [240V],N,97,Y'
'LG Electronics Inc. LG295A1C-B3 [208V],N,96,Y'
'LG Electronics Inc. LG295A1W-B3 [208V],N,96,Y'
'LG Electronics Inc. LG300A1C-B3 [208V],N,96,Y'
'LG Electronics Inc. LG300A1W-B3 [208V],N,96,Y'
'LG Electronics Inc. LG305A1C-B3 [208V],N,96,Y'
'LG Electronics Inc. LG305A1W-B3 [208V],N,96,Y'
'LG Electronics Inc. LM305UE-G1 [208V],N,96,Y'
'LG Electronics Inc. LG295A1C-B3 [240V],N,96.5,Y'
'LG Electronics Inc. LG295A1W-B3 [240V],N,96.5,Y'
'LG Electronics Inc. LG300A1C-B3 [240V],N,96.5,Y'
'LG Electronics Inc. LG300A1W-B3 [240V],N,96.5,Y'
'LG Electronics Inc. LG305A1C-B3 [240V],N,96.5,Y'
'LG Electronics Inc. LG305A1W-B3 [240V],N,96.5,Y'
'LG Electronics Inc. LM305UE-G1 [240V],N,96.5,Y'
'LG Electronics Inc. LG355A1C-A5 [208V],N,96,Y'
'LG Electronics Inc. LG355A1C-A5 [240V],N,97,Y'
'LG Electronics Inc. LG360A1C-A5 [208V],N,96,Y'
'LG Electronics Inc. LG360A1C-A5 [240V],N,97,Y'
'LG Electronics Inc. LG365A1C-A5 [208V],N,96,Y'
'LG Electronics Inc. LG365A1C-A5 [240V],N,97,Y'
'LG Electronics Inc. LG370A1C-A5 [208V],N,96,Y'
'LG Electronics Inc. LG370A1C-A5 [240V],N,97,Y'
'LG Electronics Inc. LM320UE-A2 [208V],N,96,Y'
'LG Electronics Inc. LM320UE-A2 [240V],N,97,Y'
'LG Electronics Inc. A005KEEN261 [208V],N,98,N'
'LG Electronics Inc. A005KEEN261 [240V],N,98,N'
'LG Electronics Inc. D007KEEN261 [208V],N,97.5,N'
'LG Electronics Inc. D007KEEN261 [240V],N,97.5,N'
'Lixma Tech LSI4000 [240V],Y,95,N'
'Mage Solar POWERTEC Plus 240 / 6 PL-US AC [240V],N,95,Y'
'Mage Solar POWERTEC Plus 245 / 6 PL US AC [240V],N,95,Y'
'Mage Solar USA POWERTEC Plus 250 / 6 PL US AC [208V],N,95,Y'
'Mage Solar USA POWERTEC Plus 250 / 6 PL US AC [240V],N,95,Y'
'Ming Shen Energy Technology EnerBridge Emi_301RD [240V],N,96,Y'
'Mohr Power MPS1100EVR [120V],Y,90.5,N'
'Mohr Power MPS2000EVR [240V],Y,92,N'
'Mohr Power MPS2500 [240V],Y,94.5,N'
'Mohr Power MPS3000 [240V],Y,93.5,N'
'Mohr Power MPS3500 [240V],Y,95.5,N'
'Mohr Power MPS4600 [208V],Y,95.5,N'
'Mohr Power MPS4800 [240V],Y,96,N'
'Mohr Power MPS5200 [240V],Y,96,N'
'Motech Industries PVMate 2900U [208V],Y,95.5,N'
'Motech Industries PVMate 2900U-POS [208V],Y,95.5,N'
'Motech Industries PVMate 3000U [208V],Y,95.5,N'
'Motech Industries PVMate 3000U-PG [208V],Y,95.5,N'
'Motech Industries PVMate 2900U [240V],Y,96,N'
'Motech Industries PVMate 2900U-POS [240V],Y,96,N'
'Motech Industries PVMate 3000U [240V],Y,96,N'
'Motech Industries PVMate 3000U-PG [240V],Y,96,N'
'Motech Industries PVMate 3840U [208V],Y,95.5,N'
'Motech Industries PVMate 3840U-POS [208V],Y,95.5,N'
'Motech Industries PVMate 3900U [208V],Y,95.5,N'
'Motech Industries PVMate 3900U-POS [208V],Y,95.5,N'
'Motech Industries PVMate 4000U [208V],Y,95.5,N'
'Motech Industries PVMate 4000U-PG [208V],Y,95.5,N'
'Motech Industries PVMate 3840U [240V],Y,96,N'
'Motech Industries PVMate 3840U-POS [240V],Y,96,N'
'Motech Industries PVMate 3900U [240V],Y,96,N'
'Motech Industries PVMate 3900U-POS [240V],Y,96,N'
'Motech Industries PVMate 4000U [240V],Y,96,N'
'Motech Industries PVMate 4000U-PG [240V],Y,96,N'
'Motech Industries PVMate 4900U [208V],Y,96,N'
'Motech Industries PVMate 4900U-POS [208V],Y,96,N'
'Motech Industries PVMate 5000U [208V],Y,96,N'
'Motech Industries PVMate 5000U-PG [208V],Y,96,N'
'Motech Industries PVMate 5300U [208V],Y,95.5,N'
'Motech Industries PVMate 5300U-POS [208V],Y,95.5,N'
'Motech Industries PVMate 4900U [240V],Y,96,N'
'Motech Industries PVMate 4900U-POS [240V],Y,96,N'
'Motech Industries PVMate 5000U [240V],Y,96,N'
'Motech Industries PVMate 5000U-PG [240V],Y,96,N'
'Motech Industries PVMate 5300U [240V],Y,96,N'
'Motech Industries PVMate 5300U-POS [240V],Y,96,N'
'Motech Industries PVMate 6500U [208V],Y,95.5,N'
'Motech Industries PVMate 6500U [240V],Y,96,N'
'Motech Industries PVMate 6500U [277V],Y,96,N'
'Motech Industries PVMate 7500U [208V],Y,95.5,N'
'Motech Industries PVMate 7500U [240V],Y,96,N'
'Motech Industries PVMate 7500U [277V],Y,96,N'
'Nextronex Energy Systems Ray-Max 150,N,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-1K-2G-H-US [208V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-1K-2G-H-US [240V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-1K-2G-W-US [208V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-1K-2G-W-US [240V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1K-2G-US [208V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1K-2G-US [240V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-1.5K-2G-H-US [208V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-1.5K-2G-H-US [240V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-1.5K-2G-W-US [208V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-1.5K-2G-W-US [240V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1.5K-2G-US [208V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1.5K-2G-US [240V],Y,96,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2K-2G-H-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2K-2G-H-US [240V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2K-2G-W-US [208V],Y,96.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2K-2G-W-US [240V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-2K-2G-US [208V],Y,96.5,N'
#REF!
#REF!
#REF!
#REF!
#REF!
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-2K-2G-US [240V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2K [240V],Y,94,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2.5K-2G-H-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2.5K-2G-H-US [240V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2.5K-2G-W-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-2.5K-2G-W-US [240V],Y,96.5,N'
#REF!
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-2.5K-2G-US [240V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P2.5K-4G-US [240V],N,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-3K-2G-H-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-3K-2G-H-US [240V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-3K-2G-W-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-3K-2G-W-US [240V],Y,97,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-3K-2G-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-3K-2G-US [240V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P3K-4G-US [240V],N,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-3.6K-2G-H-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-3.6K-2G-H-US [240V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-3.6K-2G-W-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-3.6K-2G-W-US [240V],Y,96.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-3.6K-2G-US [208V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-3.6K-2G-US [240V],Y,96.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P3.6K-4G-US [240V],N,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-4K-2G-H-US [208V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-4K-2G-H-US [240V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-4K-2G-W-US [208V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-4K-2G-W-US [240V],Y,97,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-4K-2G-US [208V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-4K-2G-US [240V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P4K-4G-US [240V],N,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-4.6K-2G-H-US [208V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-4.6K-2G-H-US [240V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-4.6K-2G-W-US [208V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-4.6K-2G-W-US [240V],Y,97,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-4.6K-2G-US [208V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-4.6K-2G-US [240V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P4.6K-4G-US [240V],N,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-5K-2G-H-US [208V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-5K-2G-H-US [240V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-5K-2G-W-US [208V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-5K-2G-W-US [240V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-5K-2G-US [208V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-5K-2G-US [240V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. GCI-5K-DB [240V],Y,95.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. GCI-5K-W [240V],Y,95.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis 5000-DB [240V],Y,95.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P5K-4G-US [240V],N,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P6K2-4G-US [240V],N,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P6K-4G-US,Y,97.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P6K-4G-US [240V],N,97.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-6K-US 480 Vac [480V],Y,97,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P7K-4G-US [240V],Y,97.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P7.6K-4G-US,Y,97.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P7.6K-4G-US [240V],N,97.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P8K-4G-US,Y,97.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P8K-4G-US [240V],N,97.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P9K-4G-US,Y,97.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P9K-4G-US [240V],N,97.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-10K-US [480V],Y,97.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P10K-4G-US,Y,97.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-1P10K-4G-US [240V],N,97.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-15K-US [480V],Y,97.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-20K-US [480V],Y,97.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-25K-US [480V],N,98,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-30K-US [480V],N,98,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-36K-US [480V],N,98,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-40K-US-F [480V],N,98.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-40K-US [480V],N,98.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-40K-US-F [480V],N,98.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-50K-US [480V],N,98.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-50K-US-F [480V],N,98.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-50K-US-F-SW [480V],N,98.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-50K-US-SW [480V],N,98.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-50K-US [480V],N,98.5,N'
#REF!
'Ningbo Ginlong Technologies Co.,Ltd. Solis-60K-US-F [480V],N,98.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-60K-US-F-SW [480V],N,98.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-66K-US-F [480V],N,98.5,N'
'Ningbo Ginlong Technologies Co.,Ltd. Solis-66K-US-F-SW [480V],N,98.5,N'
'Northern Electric BDM-300X2-208A [208V],N,95.5,Y'
'Northern Electric BDM-300X2-240A [240V],N,95.5,Y'
'Northern Electric & Power BDM-250-208A [208V],N,95,Y'
'Northern Electric & Power BDM-250-240A [240V],N,95,Y'
'Northern Electric & Power Co., Ltd BDM-300-208A [208V],N,95.5,Y'
'Northern Electric & Power Co., Ltd BDM-300-240A [240V],N,95.5,Y'
'Open Energy Solar Save 1100 [240V],Y,90.5,N'
'Open Energy Solar Save 2000 [240V],Y,92,N'
'Open Energy Solar Save 2500 [240V],Y,94.5,N'
'Open Energy Solar Save 3500 [240V],Y,95.5,N'
'Open Energy Solar Save 4600 [208V],Y,95.5,N'
'Open Energy Solar Save 4800 [240V],Y,96,N'
'Open Energy Solar Save 5200 [240V],Y,96,N'
'OPTI International GT 1500 [208V],Y,94.5,N'
'OPTI International GT 1500 [240V],Y,94.5,N'
'OPTI International GT 2000 [208V],Y,95.5,N'
'OPTI International GT 2000 [240V],Y,95,N'
'OPTI International GT 3000 [208V],Y,95.5,N'
'OPTI International GT 3000 [240V],Y,95.5,N'
'OPTI-Solar GT-4000 [208V],Y,95.5,N'
'OPTI-Solar GT-4000 [240V],Y,96,N'
'OutBack Power Technologies, Inc. FXR3048A,Y,91,N'
'OutBack Power Technologies, Inc. FXR3048A [120V],Y,91,N'
'OutBack Power Technologies, Inc. GTFX3048,N,91,N'
'OutBack Power Technologies, Inc. GVFX3524,Y,90.5,N'
'OutBack Power Technologies, Inc. VFXR3524A,Y,90.5,N'
'OutBack Power Technologies, Inc. VFXR3524A [120V],Y,90.5,N'
'OutBack Power Technologies, Inc. GVFX3648,N,91,N'
'OutBack Power Technologies, Inc. VFXR3648A,Y,91,N'
'OutBack Power Technologies, Inc. VFXR3648A [120V],Y,91,N'
#REF!
'OutBack Power Technologies, Inc. GS4048A,Y,92.5,N'
'OutBack Power Technologies, Inc. GS4048A [240V],Y,92.5,N'
'OutBack Power Technologies, Inc. SBX5048-120/240 [240V],Y,94,N'
'OutBack Power Technologies, Inc. GS8048A,Y,92.5,N'
'OutBack Power Technologies, Inc. GS8048A [240V],Y,92.5,N'
'OutBack Power Technologies, Inc. GS8048,N,90,N'
'Perfect Galaxy AE-30-60-PV-A [480V],Y,93,N'
'Perfect Galaxy AE-30-60-PV-D [208V],Y,92.5,N'
'Perfect Galaxy AE-30-60-PV-E [240V],Y,93,N'
'Perfect Galaxy AE-30-60-PV-F [240V],Y,94.5,N'
'Perfect Galaxy PVS-30 [208V],Y,95,N'
'Perfect Galaxy PVS-30 [240V],Y,95,N'
'Perfect Galaxy PVS-30 [480V],Y,95,N'
'Perfect Galaxy AE-50-60-PV-D [208V],Y,94.5,N'
'Perfect Galaxy AE-50-60-PV-F [240V],Y,93,N'
'Perfect Galaxy PVS-50 [208V],Y,95.5,N'
'Perfect Galaxy PVS-50 [240V],Y,95.5,N'
'Perfect Galaxy PVS-50 [480V],Y,95.5,N'
'Perfect Galaxy PVS-50-S-MT [208V],Y,95.5,N'
'Perfect Galaxy PVS-50-S-MT [240V],Y,95.5,N'
'Perfect Galaxy PVS-50-S-MT [480V],Y,95.5,N'
'Perfect Galaxy AE-50-60-PV-A [480V],Y,93,N'
'Perfect Galaxy AE-75-60-PV-A [480V],Y,95.5,N'
'Perfect Galaxy AE-75-60-PV-D [208V],Y,95.5,N'
'Perfect Galaxy PVS-75 [208V],Y,96,N'
'Perfect Galaxy PVS-75 [240V],Y,96,N'
'Perfect Galaxy PVS-75 [480V],Y,96,N'
'Perfect Galaxy AE-100-60-PV-A [480V],Y,94.5,N'
'Perfect Galaxy AE-100-60-PV-A-HE [480V],Y,95.5,N'
'Perfect Galaxy AE-100-60-PV-D [208V],Y,94.5,N'
'Perfect Galaxy AE-100-60-PV-F [240V],Y,95,N'
'Perfect Galaxy PVS-100 [208V],Y,96,N'
'Perfect Galaxy PVS-100 [240V],Y,96,N'
'Perfect Galaxy PVS-100 [480V],Y,96,N'
'Perfect Galaxy SDMS0100208LNIU [208V],Y,95,N'
'Perfect Galaxy SDMS0100240LNIU [240V],Y,95,N'
'Perfect Galaxy SDMS0100480LNIU [480V],Y,95,N'
'Perfect Galaxy PVS-110-S-MT [208V],Y,95,N'
'Perfect Galaxy PVS-110-S-MT [240V],Y,95.5,N'
'Perfect Galaxy PVS-110-S-MT [480V],Y,95.5,N'
'Perfect Galaxy AE-135-60-PV-A [480V],Y,95.5,N'
'Perfect Galaxy AE-135-60-PV-D [208V],Y,95,N'
'Perfect Galaxy PVS-135 [208V],Y,96,N'
'Perfect Galaxy PVS-135 [240V],Y,96,N'
'Perfect Galaxy PVS-135 [480V],Y,96,N'
'Perfect Galaxy PVS-210-S [208V],Y,95.5,N'
'Perfect Galaxy PVS-210-S [240V],Y,95.5,N'
'Perfect Galaxy PVS-210-S [480V],Y,95.5,N'
'Perfect Galaxy AE-225-60-PV-A [480V],Y,94.5,N'
'Perfect Galaxy AE-225-60-PV-D [208V],Y,95.5,N'
'Perfect Galaxy EQX0250UV480TN (P),Y,96.5,N'
'Perfect Galaxy PVS-250,Y,95.5,N'
'Perfect Galaxy PVS-250 [208V],Y,96,N'
'Perfect Galaxy PVS-250 [240V],Y,96,N'
'Perfect Galaxy PVS-250 [480V],Y,96,N'
'Perfect Galaxy PVS-375 [480V],Y,95.5,N'
#REF!
'Perfect Galaxy AE-500-60-PV-A [480V],Y,95,N'
'Perfect Galaxy EQX0500US200X-N,Y,96,N'
'Perfect Galaxy EQX0500US200X-P,Y,96,N'
'Perfect Galaxy EQX0500US480T-N,Y,96,N'
'Perfect Galaxy EQX0500US480T-P,Y,96,N'
'Perfect Galaxy EQX0500UV320XP(N),Y,97,N'
'Perfect Galaxy PVS-500,Y,95.5,N'
'Perfect Galaxy PVS-500 [480V],Y,96,N'
'Perfect Galaxy SDMS0500UL320XN,Y,95.5,N'
'Perfect Galaxy SDMS0500UL320XP,Y,95.5,N'
'Perfect Galaxy SDMS0500UL480TN,Y,96,N'
'Perfect Galaxy SDMS0500UL480TP,Y,96,N'
'Perfect Galaxy PV-625-XRLS-VV-RVG,Y,96.5,N'
'Perfect Galaxy PV-625-XRLS-VV-STG,Y,96.5,N'
'Perfect Galaxy EQX0630UV360XP(N),Y,97,N'
'Perfect Galaxy PV-680-XRLS-VV-RVG,Y,96.5,N'
'Perfect Galaxy PV-680-XRLS-VV-STG,Y,96.5,N'
'Perfect Galaxy EQX0750UV320XP(N),Y,97,N'
'Perfect Galaxy EPP-1000-0600-32060-200X-U-N,Y,96.5,N'
'Perfect Galaxy EPP-1000-0600-32060-200X-U-P,Y,96.5,N'
'Perfect Galaxy EQX1000UV400XP(N),Y,97.5,N'
'Perfect Galaxy PVS-1000,Y,96,N'
'Perfect Galaxy EPP-1250-1000-52085-320X-U-N,Y,97,N'
'Perfect Galaxy EPP-1250-1000-52085-320X-U-P,Y,97,N'
'Perfect Galaxy International Ltd EQMX0500UV320XN [320V],N,97.5,N'
'Perfect Galaxy International Ltd EQMX0500UV320XP [320V],N,97.5,N'
'Perfect Galaxy International Ltd EQMX0630UV400XN [400V],N,97.5,N'
'Perfect Galaxy International Ltd EQMX0630UV400XP [400V],N,97.5,N'
'Perfect Galaxy International Ltd. EQX0500UV320XP(N),Y,97,N'
'Petra Solar 103.10866.500x [120V],N,93,Y'
'Petra Systems 103.10400.0002 [240V],N,96,Y'
'Petra Systems 103.10400.0001 [120V],N,96,Y'
'Phoenixtec Power PS240US3R [208V],Y,95.5,N'
#REF!
'Phoenixtec Power PS240US3R [240V],Y,95.5,N'
'Phono Solar Technology PS240M-20/U-AC,N,94.5,Y'
#REF!
'Phono Solar Technology PS240P-20/U-AC,N,94.5,Y'
'Phono Solar Technology PS245M-20/U-AC,N,94.5,Y'
#REF!
'Phono Solar Technology PS245P-20/U-AC,N,94.5,Y'
'Phono Solar Technology PS250M-20/U-AC,N,94.5,Y'
#REF!
'Phono Solar Technology PS250P-20/U-AC,N,94.5,Y'
#REF!
'Phono Solar Technology PS255M-20/U-AC,N,94.5,Y'
'Phono Solar Technology PS255P-20/U-AC,N,94.5,Y'
'Phono Solar Technology PS260M-20/U-AC,N,94.5,Y'
#REF!
'Phono Solar Technology PS260P-20/U-AC,N,94.5,Y'
#REF!
'Pika Energy X3001-NA,Y,96,N'
#REF!
'Pika Energy X7603 [240V],N,96.5,N'
#REF!
'Pika Energy X7601 [240V],Y,96.5,N'
#REF!
'Pika Energy X7602 [240V],Y,96.5,N'
'Pika Energy X11403 [208V],N,97.5,N'
'Pika Energy X11402 [208V],Y,97.5,N'
'Power Electronics FS0300CU,Y,96.5,N'
'Power Electronics FS0300PU,Y,96.5,N'
'Power Electronics FS0450CU,Y,97,N'
'Power Electronics FS0450PU,Y,97,N'
'Power Electronics FS0501CU,Y,96.5,N'
'Power Electronics FS0560CU,Y,96,N'
'Power Electronics FS0560PU,Y,96,N'
'Power Electronics FS0600PU,Y,97,N'
'Power Electronics FS0640CU,Y,96,N'
'Power Electronics FS0640PU,Y,96,N'
'Power Electronics FS0600CU,Y,97,N'
'Power Electronics FS0750CU,Y,96.5,N'
'Power Electronics FS0751PU,Y,97,N'
'Power Electronics FS0701CU [360V],Y,97,N'
'Power Electronics FS0830PU,Y,97,N'
'Power Electronics FS0751CU,N,97,N'
'Power Electronics FS0900PU,Y,97,N'
'Power Electronics FS0830CU,Y,97,N'
'Power Electronics FS0970CU,Y,97,N'
'Power Electronics FS0970PU,Y,97,N'
'Power Electronics FS0901CU,N,97,N'
'Power Electronics FS1001CU,Y,97,N'
'Power Electronics FS1004CU,N,97,N'
'Power Electronics FS0900CU,Y,97.5,N'
'Power Electronics FS0940CU,N,97,N'
'Power Electronics FS1050PU,Y,97,N'
'Power Electronics FS1051CU,N,97,N'
'Power Electronics FS1003CU,Y,97,N'
'Power Electronics FS01110PU,Y,97,N'
#REF!
'Power Electronics FS1000CU [440V],N,97,N'
#REF!
'Power Electronics FS1112CU [440V],N,97,N'
'Power Electronics FS1050CU15 [565V],N,97,N'
'Power Electronics FS1100CU15O3 [600V],N,98,N'
'Power Electronics FS1050CU,Y,97,N'
'Power Electronics FS1080CU [400V],N,97,N'
'Power Electronics FS1200CU,Y,97,N'
#REF!
'Power Electronics FS1200PU,Y,97,N'
'Power Electronics FS1201CU [400V],N,98,N'
'Power Electronics FS1100CU15 [600V],N,97,N'
'Power Electronics FS01110CU,Y,97,N'
'Power Electronics FS1250PU,Y,97,N'
'Power Electronics FS1140CU [420V],N,97,N'
#REF!
'Power Electronics FS1271CU [420V],N,98,N'
'Power Electronics FS1290CU [330V],Y,97,N'
'Power Electronics FS1200CU15 [645V],N,97.5,N'
'Power Electronics FS1190CU [440V],N,97,N'
#REF!
'Power Electronics FS1331CU [440V],N,97,N'
'Power Electronics FS1250CU,Y,97.5,N'
'Power Electronics FS1275CU15 [690V],N,97,N'
'Power Electronics FS1260CU [400V],N,97,N'
'Power Electronics FS1401CU [400V],Y,97,N'
'Power Electronics FS1430CU [330V],Y,97,N'
#REF!
'Power Electronics FS1330CU [420V],N,97,N'
'Power Electronics FS1480CU [420V],N,97,N'
'Power Electronics FS1400CU15 [565V],N,97.5,N'
'Power Electronics FS1530CU [390V],Y,97,N'
#REF!
'Power Electronics FS1390CU [440V],N,97,N'
'Power Electronics FS1550CU [440V],Y,97,N'
'Power Electronics FS1500CU15O3 [600V],N,98,N'
#REF!
'Power Electronics FS1440CU [400V],N,97,N'
'Power Electronics FS1600CU [400V],N,97,N'
'Power Electronics FS1475CU15 [600V],N,97.5,N'
'Power Electronics FS1590CU [440V],N,97,N'
'Power Electronics FS1520CU [420V],N,97,N'
#REF!
'Power Electronics FS1690CU [420V],N,97,N'
'Power Electronics FS1700CU [390V],Y,97,N'
'Power Electronics FS1600CU15 [645V],N,97.5,N'
'Power Electronics FS1770CU [440V],N,97,N'
#REF!
'Power Electronics FS1620CU [400V],N,97,N'
#REF!
'Power Electronics FS1801CU [400V],N,97,N'
'Power Electronics FS1700CU15 [690V],N,98,N'
'Power Electronics FS1750CU15 [565V],N,97.5,N'
#REF!
'Power Electronics FS1710CU [420V],N,97,N'
'Power Electronics FS1901CU [420V],N,97,N'
'Power Electronics FS1850CU15O3 [600V],N,98,N'
'Power Electronics FS1790CU [440V],N,97,N'
'Power Electronics FS1991CU [440V],N,97,N'
#REF!
'Power Electronics FS1800CU [400V],N,97,N'
'Power Electronics FS2000CU [400V],N,97,N'
'Power Electronics FS1850CU15 [600V],N,97.5,N'
#REF!
'Power Electronics FS1900CU [420V],N,97,N'
'Power Electronics FS2110CU [420V],N,97,N'
'Power Electronics FS2000CU15 [645V],N,98,N'
#REF!
'Power Electronics FS1980CU [440V],N,97,N'
#REF!
'Power Electronics FS2200CU [440V],N,97,N'
#REF!
'Power Electronics FS2100CU15 [565V],N,97.5,N'
#REF!
'Power Electronics FS2125CU15 [690V],N,98,N'
#REF!
'Power Electronics FS2225CU15 [600V],N,97.5,N'
#REF!
'Power Electronics FS2250CU15O3 [600V],N,98,N'
#REF!
'Power Electronics FS2150CU15 [645V],N,98,N'
#REF!
'Power Electronics FS2400CU15 [645V],N,98,N'
#REF!
'Power Electronics FS2450CU15 [565V],N,97.5,N'
#REF!
'Power Electronics FS2550CU15 [690V],N,98,N'
#REF!
'Power Electronics FS2300CU15 [690V],N,98,N'
#REF!
'Power Electronics FS2600CU15O3 [600V],N,98,N'
#REF!
'Power Electronics FS2600CU15 [600V],N,98,N'
'Power Electronics FS2800CU15 [645V],N,98,N'
'Power Electronics FS3000CU15 [690V],N,98,N'
'Powercom SLK-1500 [208V],Y,94.5,N'
'Powercom SLK-1500 [240V],Y,94.5,N'
'Powercom SLK-2000 [208V],Y,95.5,N'
'Powercom SLK-2000 [240V],Y,95,N'
'Powercom SLK-3000 [208V],Y,95.5,N'
'Powercom SLK-3000 [240V],Y,95.5,N'
'Powercom SLK-4000 [208V],Y,95.5,N'
'Powercom SLK-4000 [240V],Y,96,N'
'Powercom SLK-4000 [277V],Y,95.5,N'
'Power-One MICRO-0.25-I-OUTD-US-208 [208V],N,96,Y'
'Power-One MICRO-0.25-I-OUTD-US-240 [240V],N,96,Y'
'Power-One MICRO-0.3HV-I-OUTD-US-208 [208V],N,96,Y'
'Power-One MICRO-0.3HV-I-OUTD-US-240 [240V],N,96,Y'
'Power-One MICRO-0.3-I-OUTD-US-208 [208V],N,96,Y'
'Power-One MICRO-0.3-I-OUTD-US-240 [240V],N,96,Y'
'Power-One UNO-2.0-I-OUTD-S-US [208V],Y,95.5,N'
'Power-One UNO-2.0-I-OUTD-S-US [240V],Y,95.5,N'
'Power-One UNO-2.0-I-OUTD-S-US [277V],Y,95.5,N'
'Power-One UNO-2.5-I-OUTD-S-US [208V],Y,95.5,N'
'Power-One UNO-2.5-I-OUTD-S-US [240V],Y,96,N'
'Power-One UNO-2.5-I-OUTD-S-US [277V],Y,96,N'
'Power-One PVI-3000-I-OUTD-US [208V],Y,90.5,N'
'Power-One PVI-3000-I-OUTD-US-F [208V],Y,90.5,N'
'Power-One PVI-3.0-OUTD-S-US [208V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US [240V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US [277V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-A [208V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-A [240V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-A [277V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-Z [208V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-Z [240V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-Z [277V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-Z-A [208V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-Z-A [240V],Y,96,N'
'Power-One PVI-3.0-OUTD-S-US-Z-A [277V],Y,96,N'
'Power-One PVI-3.0-OUTD-US [208V],Y,96,N'
'Power-One PVI-3.0-OUTD-US [240V],Y,96,N'
'Power-One PVI-3.0-OUTD-US [277V],Y,96,N'
'Power-One PVI-3000-I-OUTD-US [240V],Y,92,N'
'Power-One PVI-3000-I-OUTD-US-F [240V],Y,91,N'
'Power-One PVI-3.8-1-OUTD-x-US-y [208V],Y,96,N'
'Power-One PVI-3600-OUTD-US-F [208V],Y,94.5,N'
'Power-One PVI-3600-US [208V],Y,94,N'
'Power-One PVI-3.6-OUTD-S-US [208V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US [240V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US [277V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-A [208V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-A [240V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-A [277V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-Z [208V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-Z [240V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-Z [277V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-Z-A [208V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-Z-A [240V],Y,96,N'
'Power-One PVI-3.6-OUTD-S-US-Z-A [277V],Y,96,N'
'Power-One PVI-3.6-OUTD-US [208V],Y,96,N'
'Power-One PVI-3.6-OUTD-US [240V],Y,96,N'
'Power-One PVI-3.6-OUTD-US [277V],Y,96,N'
'Power-One PVI-3600-OUTD-US-F [240V],Y,95,N'
'Power-One PVI-3600-US [240V],Y,94.5,N'
'Power-One PVI-3.8-1-OUTD-x-US-y [240V],Y,96.5,N'
'Power-One PVI-3.8-1-OUTD-x-US-y [277V],Y,96.5,N'
'Power-One PVI-3.8-OUTD-S-US [208V],Y,95.5,N'
'Power-One PVI-3.8-OUTD-S-US [240V],Y,96,N'
'Power-One PVI-3.8-OUTD-S-US [277V],Y,96,N'
'Power-One PVI-3.8-OUTD-S-US-A [208V],Y,95.5,N'
'Power-One PVI-3.8-OUTD-S-US-A [240V],Y,96,N'
'Power-One PVI-3.8-OUTD-S-US-A [277V],Y,96,N'
'Power-One PVI-3.8-OUTD-S-US-Z [208V],Y,95.5,N'
'Power-One PVI-3.8-OUTD-S-US-Z [240V],Y,96,N'
'Power-One PVI-3.8-OUTD-S-US-Z [277V],Y,96,N'
'Power-One PVI-3.8-OUTD-S-US-Z-A [208V],Y,95.5,N'
'Power-One PVI-3.8-OUTD-S-US-Z-A [240V],Y,96,N'
'Power-One PVI-3.8-OUTD-S-US-Z-A [277V],Y,96,N'
'Power-One PVI-3.8-OUTD-US [208V],Y,95.5,N'
'Power-One PVI-3.8-OUTD-US [240V],Y,96,N'
'Power-One PVI-3.8-OUTD-US [277V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US [208V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US [240V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US [277V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-A [208V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-A [240V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-A [277V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-Z [208V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-Z [240V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-Z [277V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-Z-A [208V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-Z-A [240V],Y,96,N'
'Power-One PVI-4.2-OUTD-S-US-Z-A [277V],Y,96,N'
'Power-One PVI-4.2-OUTD-US [208V],Y,96,N'
'Power-One PVI-4.2-OUTD-US [240V],Y,96,N'
'Power-One PVI-4.2-OUTD-US [277V],Y,96,N'
'Power-One PVI-4.6-1-OUTD-x-US-y [208V],Y,96,N'
'Power-One PVI-4.6-1-OUTD-x-US-y [240V],Y,96.5,N'
'Power-One PVI-4.6-1-OUTD-x-US-y [277V],Y,96.5,N'
'Power-One PVI-5000-OUTD-S-US-Z [208V],Y,96,N'
'Power-One PVI-5000-OUTD-S-US-Z [240V],Y,96.5,N'
'Power-One PVI-5000-OUTD-S-US-Z [277V],Y,96.5,N'
'Power-One PVI-5000-OUTD-S-US-Z-A [208V],Y,96,N'
'Power-One PVI-5000-OUTD-S-US-Z-A [240V],Y,96.5,N'
'Power-One PVI-5000-OUTD-S-US-Z-A [277V],Y,96.5,N'
'Power-One PVI-5000-OUTD-US [208V],Y,96,N'
'Power-One PVI-5000-OUTD-US [240V],Y,96.5,N'
'Power-One PVI-5000-OUTD-US [277V],Y,96.5,N'
'Power-One PVI-5000-OUTD-US-A [208V],Y,96,N'
'Power-One PVI-5000-OUTD-US-A [240V],Y,96.5,N'
'Power-One PVI-5000-OUTD-US-A [277V],Y,96.5,N'
'Power-One PVI-5000-OUTD-US-Z [208V],Y,96,N'
'Power-One PVI-5000-OUTD-US-Z [240V],Y,96.5,N'
'Power-One PVI-5000-OUTD-US-Z [277V],Y,96.5,N'
'Power-One PVI-5000-OUTD-US-Z-A [208V],Y,96,N'
#REF!
#REF!
'Power-One PVI-5000-OUTD-US-Z-A [240V],Y,96.5,N'
'Power-One PVI-5000-OUTD-US-Z-A [277V],Y,96.5,N'
'Power-One PVI-6000-OUTD-S-US-A [208V],Y,96,N'
'Power-One PVI-6000-OUTD-S-US-A [240V],Y,96.5,N'
'Power-One PVI-6000-OUTD-S-US-A [277V],Y,96.5,N'
'Power-One PVI-6000-OUTD-S-US-Z [208V],Y,96,N'
'Power-One PVI-6000-OUTD-S-US-Z [240V],Y,96.5,N'
'Power-One PVI-6000-OUTD-S-US-Z [277V],Y,96.5,N'
'Power-One PVI-6000-OUTD-S-US-Z-A [208V],Y,96,N'
'Power-One PVI-6000-OUTD-S-US-Z-A [240V],Y,96.5,N'
'Power-One PVI-6000-OUTD-S-US-Z-A [277V],Y,96.5,N'
'Power-One PVI-6000-OUTD-US [208V],Y,96,N'
'Power-One PVI-6000-OUTD-US [240V],Y,96.5,N'
'Power-One PVI-6000-OUTD-US [277V],Y,96.5,N'
'Power-One PVI-6000-OUTD-US-A [208V],Y,96,N'
'Power-One PVI-6000-OUTD-US-A [240V],Y,96.5,N'
'Power-One PVI-6000-OUTD-US-A [277V],Y,96.5,N'
'Power-One PVI-6000-OUTD-US-Z [208V],Y,96,N'
'Power-One PVI-6000-OUTD-US-Z [240V],Y,96.5,N'
'Power-One PVI-6000-OUTD-US-Z [277V],Y,96.5,N'
'Power-One PVI-6000-OUTD-US-Z-A [208V],Y,96,N'
'Power-One PVI-6000-OUTD-US-Z-A [240V],Y,96.5,N'
'Power-One PVI-6000-OUTD-US-Z-A [277V],Y,96.5,N'
'Power-One UNO-7.6-TL-OUTD-S-US-A [208V],Y,96.5,N'
'Power-One UNO-7.6-TL-OUTD-S-US-A [240V],Y,96.5,N'
'Power-One UNO-7.6-TL-OUTD-S-US-A [277V],Y,96.5,N'
'Power-One UNO-7.6-TL-OUTD-S-US-Z-A [208V],Y,96.5,N'
'Power-One UNO-7.6-TL-OUTD-S-US-Z-A [240V],Y,96.5,N'
'Power-One UNO-7.6-TL-OUTD-S-US-Z-A [277V],Y,96.5,N'
'Power-One UNO-8.6-TL-OUTD-S-US-A [240V],Y,96.5,N'
'Power-One UNO-8.6-TL-OUTD-S-US-A [277V],Y,96.5,N'
'Power-One UNO-8.6-TL-OUTD-S-US-Z-A [240V],Y,96.5,N'
'Power-One UNO-8.6-TL-OUTD-S-US-Z-A [277V],Y,96.5,N'
'Power-One PVI-10.0-I-OUTD-x-US-208-y [208V],Y,96,N'
'Power-One PVI-10.0-I-OUTD-x-US-480-y-z [480V],Y,97,N'
'Power-One PVI-12.0-I-OUTD-x-US-480-y [480V],Y,97,N'
'Power-One TRIO-20.0-TL-OUTD-S1-480-A [480V],Y,97.5,N'
'Power-One TRIO-20.0-TL-OUTD-S1A-480-A [480V],Y,97.5,N'
'Power-One TRIO-20.0-TL-OUTD-S1A-US-480 [480V],Y,97.5,N'
'Power-One TRIO-20.0-TL-OUTD-S1B-480-A [480V],Y,97.5,N'
'Power-One TRIO-20.0-TL-OUTD-S1B-US-480 [480V],Y,97.5,N'
'Power-One TRIO-20.0-TL-OUTD-S1-US-480 [480V],Y,97.5,N'
'Power-One TRIO-20.0-TL-OUTD-S-480-A [480V],Y,97.5,N'
'Power-One TRIO-20.0-TL-OUTD-S-US-480 [480V],Y,97.5,N'
'Power-One TRIO-27.6-TL-OUTD-S1-480-A [480V],Y,97.5,N'
'Power-One TRIO-27.6-TL-OUTD-S1A-480-A [480V],Y,97.5,N'
'Power-One TRIO-27.6-TL-OUTD-S1A-US-480 [480V],Y,97.5,N'
'Power-One TRIO-27.6-TL-OUTD-S1B-480-A [480V],Y,97.5,N'
'Power-One TRIO-27.6-TL-OUTD-S1B-US-480 [480V],Y,97.5,N'
'Power-One TRIO-27.6-TL-OUTD-S1-US-480 [480V],Y,97.5,N'
'Power-One TRIO-27.6-TL-OUTD-S-480-A [480V],Y,97.5,N'
'Power-One TRIO-27.6-TL-OUTD-S-US-480 [480V],Y,97.5,N'
'Power-One PVI-CENTRAL-50-US [208V],Y,95,N'
'Power-One PVI-CENTRAL-50-US [480V],Y,95,N'
'Power-One PVI-CENTRAL-100-US [208V],Y,95,N'
'Power-One PVI-CENTRAL-100-US [480V],Y,95,N'
'Power-One PVI-CENTRAL-250-US [480V],Y,97,N'
'Power-One PVI-CENTRAL-300-US [480V],Y,97,N'
'Power-One ULTRA-750-TL-OUTD-2-US-690-x-y-z [690V],Y,96.5,N'
'Power-One ULTRA-750-TL-OUTD-4-US-690-x-y-z [690V],Y,96.5,N'
'Power-One ULTRA-750-TL-OUTD-1-US-690-x-y-z [690V],Y,96.5,N'
'Power-One ULTRA-750-TL-OUTD-3-US-690-x-y-z [690V],Y,96.5,N'
'Power-One ULTRA-1100-TL-OUTD-2-US-690-x-y-z [690V],Y,96.5,N'
'Power-One ULTRA-1100-TL-OUTD-4-US-690-x-y-z [690V],Y,97,N'
'Power-One ULTRA-1100-TL-OUTD-1-US-690-x-y-z [690V],Y,96.5,N'
'Power-One ULTRA-1100-TL-OUTD-3-US-690-x-y-z [690V],Y,97,N'
'Power-One ULTRA-1500-TL-OUTD-2-US-690-x-y-z [690V],Y,96.5,N'
'Power-One ULTRA-1500-TL-OUTD-4-US-690-x-y-z [690V],Y,97,N'
'Power-One ULTRA-1500-TL-OUTD-1-US-690-x-y-z [690V],Y,96.5,N'
'Power-One ULTRA-1500-TL-OUTD-3-US-690-x-y-z [690V],Y,97,N'
'Princeton Power Systems GTIB-208-30WYYYYYY [208V],N,93,N'
'Princeton Power Systems GTIB30-480BGNSC [480V],Y,92.5,N'
'Princeton Power Systems GTIB-480-30-WZZZZZZ [480V],N,92.5,N'
'Princeton Power Systems GTIB-480-30-ZZZZZZZ [480V],N,95.5,N'
'Princeton Power Systems GTIB-480-100-xxxx [480V] [480Vdc],N,94.5,N'
'Princeton Power Systems GTIB-480-100-xxxx [480V] [600Vdc],N,95,N'
'Princeton Power Systems GTIB-480-100X-YYYYYYYY-Z-G1.2 [480V],Y,94.5,N'
'Princeton Power Systems GTIB-480-125-XXXXXX-W-G1.3 [480V],N,94,N'
'Princeton Power Systems GTIB-480-125-XXXXXX-Y-G1.3 [480V],N,96,N'
'Princeton Power Systems BIGI-250-X48GNMNR [480V],Y,94.5,N'
'Princeton Power Systems BIGI-250-X48GNNR [480V],N,94.5,N'
'PV Powered PVP1100,Y,91.5,N'
'PV Powered PVP1100EVR [120V],Y,90.5,N'
'PV Powered PVP2000 [120V],Y,92.5,N'
'PV Powered PVP2000EVR [240V],Y,92,N'
'PV Powered PVP2500 [240V],Y,94.5,N'
'PV Powered PVP2800-208 [208V],Y,92,N'
'PV Powered PVP3000 [240V],Y,93.5,N'
'PV Powered PVP3500 [240V],Y,95.5,N'
'PV Powered PVP4600 [240V],Y,95.5,N'
'PV Powered PVP4800 [240V],Y,96,N'
'PV Powered PVP5200 [240V],Y,96,N'
'PV Powered PVP30KW-208 [208V],Y,94,N'
'PV Powered PVP30KW-480 [480V],Y,94,N'
'PV Powered PVP30KW-LV-208 [208V],Y,93,N'
'PV Powered PVP30KW-LV-480 [480V],Y,93.5,N'
'PV Powered PVP35 kW-208 [208V],Y,95.5,N'
'PV Powered PVP35 kW-480 [480V],Y,96,N'
'PV Powered PVP35 kW-600 [600V],Y,95.5,N'
'PV Powered PVP50KW-208 [208V],Y,96,N'
'PV Powered PVP50KW-480 [480V],Y,96,N'
'PV Powered PVP50KW-600 [600V],Y,96,N'
'PV Powered PVP75KW-208 [208V],Y,95.5,N'
'PV Powered PVP75KW-480 [480V],Y,95.5,N'
'PV Powered PVP75KW-600 [600V],Y,96,N'
'PV Powered PVP100 kW-208 [208V],Y,95.5,N'
'PV Powered PVP100 kW-480 [480V],Y,96,N'
'PV Powered PVP100KW-600 [600V],Y,96,N'
'PV Powered PVP250KW-480 [480V],Y,96.5,N'
'PV Powered PVP250KW-600 [600V],Y,96.5,N'
'PV Powered PVP260KW [480V],Y,97,N'
'PV Powered PVP260KW-LV [480V],Y,96.5,N'
'REFU Elektronik REFUsol 24K-UL [480V],N,98,N'
'REFU Elektronik REFUsol 24K-UL-AFCI [480V],N,98,N'
'REFU Elektronik REFUsol 48K-UL [480V],N,98,N'
'REFU Elektronik REFUsol 48K-UL-AFCI [480V],N,98,N'
'Refusol 804R012 [480V],Y,97.5,N'
'Refusol 804R016 [480V],Y,97.5,N'
'Refusol 804R020 [480V],Y,97.5,N'
'Refusol 804R024 [480V],Y,98,N'
'Renergy RS-1500 [208V],Y,94.5,N'
'Renergy RS-1500 [240V],Y,94.5,N'
'Renergy RS-2000 [208V],Y,95.5,N'
'Renergy RS-2000 [240V],Y,95,N'
'Renergy RS-3000 [208V],Y,95.5,N'
'Renergy RS-3000 [240V],Y,95.5,N'
'Renergy RS-4000 [208V],Y,95.5,N'
'Renergy RS-4000 [240V],Y,96,N'
'Renergy RS-5000 [240V],Y,95.5,N'
'Renesola Zhejiang Replus-250A [240V],N,95,Y'
'Renesola Zhejiang Replus-250B [208V],N,95,Y'
'Renesola Zhejiang Replus-300-208A,N,95.5,Y'
'Renesola Zhejiang Replus-300-240A,N,95.5,Y'
'Renesola Zhejiang MU300SAP3 [240V],N,96,Y'
'Renesola Zhejiang Replus 3600MTLB-US [208V],Y,97,N'
'Renesola Zhejiang Replus 3600MTLB-US [240V],Y,97,N'
'Renesola Zhejiang Replus 3600MTLB-US [277V],Y,97,N'
'Renesola Zhejiang Replus 4200MTLB-US [208V],Y,97,N'
'Renesola Zhejiang Replus 4200MTLB-US [240V],Y,97,N'
'Renesola Zhejiang Replus 4200MTLB-US [277V],Y,97,N'
'Renesola Zhejiang Replus 5000MTLB-US [208V],Y,97,N'
'Renesola Zhejiang Replus 5000MTLB-US [240V],Y,97,N'
'Renesola Zhejiang Replus 5000MTLB-US [277V],Y,97,N'
'Renesola Zhejiang Replus 8000TLB-US [208V],Y,96.5,N'
'Renesola Zhejiang Replus 8000TLB-US [240V],Y,97,N'
'Renesola Zhejiang Replus 9000TLB-US [208V],Y,96.5,N'
'Renesola Zhejiang Replus 9000TLB-US [240V],Y,96.5,N'
'Renesola Zhejiang Replus 10000TLB-US [208V],Y,96.5,N'
'Renesola Zhejiang Replus 10000TLB-US [240V],Y,97,N'
'Renesola Zhejiang Replus 10000TL3B-US [277V],Y,95.5,N'
'Renesola Zhejiang Replus 12000TL3B-US [277V],Y,95.5,N'
'Renesola Zhejiang Replus 11000TLB-US [240V],Y,97,N'
'Renesola Zhejiang Replus 18000TL3B-US [277V],Y,96,N'
'Renesola Zhejiang Replus 20000TL3B-US [277V],Y,96.5,N'
'Renovo Power Systems RN3000US,Y,96.5,N'
'Renovo Power Systems RN5000US,Y,94.5,N'
'Resonix EVSK1750WG [208V],Y,94.5,N'
'Resonix EVSK1750WG [240V],Y,94.5,N'
'Resonix EVSK2340WG [208V],Y,95.5,N'
'Resonix EVSK2340WG [240V],Y,95,N'
'Resonix EVSK3510WG [208V],Y,95.5,N'
'Resonix EVSK3510WG [240V],Y,95.5,N'
#REF!
'Resonix EVSK4700WG [208V],Y,95.5,N'
#REF!
'Resonix EVSK4700WG [240V],Y,96,N'
'Rhombus Energy Solutions BESI-50kW-480 [480V],N,94,N'
'Rhombus Energy Solutions BESS-50kW-480 [480V],N,94,N'
'Ritek RTMU300SAP2 [240V],N,96,Y'
'Sainty Solar SSI-2K2U [240V],Y,94.5,N'
'Sainty Solar SSI-3K3U [240V],Y,95,N'
'Sainty Solar SSI-4K4U [240V],Y,95.5,N'
'Sainty Solar SSI-5K5U [240V],Y,95.5,N'
'Samil Power SolarPond 240HF-US [208V],N,95.5,Y'
'Samil Power SolarPond 240HF-US [240V],N,95,Y'
'Samil Power SolarRiver3000TL-US [208V],Y,96.5,N'
'Samil Power SolarRiver3000TL-US [240V],Y,97,N'
'Samil Power SolarRiver4000TL-US [208V],Y,97,N'
'Samil Power SolarRiver4000TL-US [240V],Y,97,N'
'Samil Power SolarRiver5000TL-US [208V],Y,97,N'
'Samil Power SolarRiver5000TL-US [240V],Y,97,N'
'Samil Power SolarRiver6000TL-US [208V],Y,97,N'
'Samil Power SolarRiver6000TL-US [240V],Y,97,N'
'Samil Power SolarRiver6000TL-US [277V],Y,97,N'
'Samil Power SolarRiver7000TL-US [208V],Y,97,N'
'Samil Power SolarRiver7000TL-US [240V],Y,97.5,N'
'Samil Power SolarRiver7000TL-US [277V],Y,97,N'
'Samil Power SolarRiver8000TL-US [208V],Y,97,N'
'Samil Power SolarRiver8000TL-US [240V],Y,97.5,N'
'Samil Power SolarRiver8000TL-US [277V],Y,97,N'
'Samil Power SolarRiver9000TL-US [208V],Y,97,N'
'Samil Power SolarRiver9000TL-US [240V],Y,97.5,N'
'Samil Power SolarRiver9000TL-US [277V],Y,97.5,N'
'Samil Power SolarRiver10000TL-US [208V],Y,97,N'
'Samil Power SolarRiver10000TL-US [240V],Y,97.5,N'
'Samil Power SolarRiver10000TL-US [277V],Y,97.5,N'
'SanRex PV-100K-48T-13,Y,94.5,N'
'SanRex PV-250K-48T-13,Y,95,N'
'SanRex PV-500K-48T-13,N,95.5,N'
'Satcon Technology AE-30-60-PV-A [480V],Y,93,N'
'Satcon Technology AE-30-60-PV-D [208V],Y,92.5,N'
'Satcon Technology AE-30-60-PV-E [240V],Y,93,N'
'Satcon Technology AE-30-60-PV-F [240V],Y,94.5,N'
'Satcon Technology PVS-30 [208V],Y,95,N'
'Satcon Technology PVS-30 [240V],Y,95,N'
'Satcon Technology PVS-30 [480V],Y,95,N'
'Satcon Technology AE-50-60-PV-D [208V],Y,94.5,N'
'Satcon Technology AE-50-60-PV-F [240V],Y,93,N'
'Satcon Technology PVS-50 [208V],Y,95.5,N'
'Satcon Technology PVS-50 [240V],Y,95.5,N'
'Satcon Technology PVS-50 [480V],Y,95.5,N'
'Satcon Technology PVS-50-S-MT [208V],Y,95.5,N'
'Satcon Technology PVS-50-S-MT [240V],Y,95.5,N'
'Satcon Technology PVS-50-S-MT [480V],Y,95.5,N'
'Satcon Technology AE-50-60-PV-A [480V],Y,93,N'
'Satcon Technology AE-75-60-PV-A [480V],Y,95.5,N'
'Satcon Technology AE-75-60-PV-D [208V],Y,95.5,N'
'Satcon Technology PVS-75 [208V],Y,96,N'
'Satcon Technology PVS-75 [240V],Y,96,N'
'Satcon Technology PVS-75 [480V],Y,96,N'
'Satcon Technology AE-100-60-PV-A [480V],Y,94.5,N'
'Satcon Technology AE-100-60-PV-A-HE [480V],Y,95.5,N'
'Satcon Technology AE-100-60-PV-D [208V],Y,94.5,N'
'Satcon Technology AE-100-60-PV-F [240V],Y,95,N'
'Satcon Technology PVS-100 [208V],Y,96,N'
'Satcon Technology PVS-100 [240V],Y,96,N'
'Satcon Technology PVS-100 [480V],Y,96,N'
'Satcon Technology SDMS0100208LNIU [208V],Y,95,N'
'Satcon Technology SDMS0100240LNIU [240V],Y,95,N'
'Satcon Technology SDMS0100480LNIU [480V],Y,95,N'
'Satcon Technology PVS-110-S-MT [208V],Y,95,N'
'Satcon Technology PVS-110-S-MT [240V],Y,95.5,N'
'Satcon Technology PVS-110-S-MT [480V],Y,95.5,N'
'Satcon Technology AE-135-60-PV-A [480V],Y,95.5,N'
'Satcon Technology AE-135-60-PV-D [208V],Y,95,N'
'Satcon Technology PVS-135 [208V],Y,96,N'
'Satcon Technology PVS-135 [240V],Y,96,N'
'Satcon Technology PVS-135 [480V],Y,96,N'
'Satcon Technology PVS-210-S [208V],Y,95.5,N'
'Satcon Technology PVS-210-S [240V],Y,95.5,N'
'Satcon Technology PVS-210-S [480V],Y,95.5,N'
'Satcon Technology AE-225-60-PV-A [480V],Y,94.5,N'
'Satcon Technology AE-225-60-PV-D [208V],Y,95.5,N'
'Satcon Technology PVS-250,Y,95.5,N'
#REF!
#REF!
'Satcon Technology PVS-250 [208V],Y,96,N'
'Satcon Technology PVS-250 [240V],Y,96,N'
'Satcon Technology PVS-250 [480V],Y,96,N'
'Satcon Technology PVS-375 [480V],Y,95.5,N'
'Satcon Technology AE-500-60-PV-A [480V],Y,95,N'
'Satcon Technology EQX0500US200X-N,Y,96,N'
'Satcon Technology EQX0500US200X-P,Y,96,N'
'Satcon Technology EQX0500US480T-N,Y,96,N'
'Satcon Technology EQX0500US480T-P,Y,96,N'
#REF!
'Satcon Technology PVS-500,Y,95.5,N'
'Satcon Technology PVS-500 [480V],Y,96,N'
'Satcon Technology SDMS0500UL320XN [320V],Y,95.5,N'
'Satcon Technology SDMS0500UL320XP [320V],Y,95.5,N'
'Satcon Technology SDMS0500UL480TN [480V],Y,96,N'
'Satcon Technology SDMS0500UL480TP [480V],Y,96,N'
'Satcon Technology EPP-1000-0600-32060-200X-U-N,Y,96.5,N'
'Satcon Technology EPP-1000-0600-32060-200X-U-P,Y,96.5,N'
'Satcon Technology EPP-1250-1000-52085-320X-U-N,Y,97,N'
'Satcon Technology EPP-1250-1000-52085-320X-U-P,Y,97,N'
'Schneider Electric Solar Inverters USA, Inc. Conext TX 2800 NA [208V],Y,94.5,N'
'Schneider Electric Solar Inverters USA, Inc. Conext TX 2800 NA [240V],Y,94.5,N'
'Schneider Electric Solar Inverters USA, Inc. Conext TX 3300 NA [208V],Y,94.5,N'
'Schneider Electric Solar Inverters USA, Inc. Conext TX 3300 NA [240V],Y,95,N'
'Schneider Electric Solar Inverters USA, Inc. Conext TX 3800 NA [208V],Y,95.5,N'
'Schneider Electric Solar Inverters USA, Inc. Conext TX 3800 NA [240V],Y,95.5,N'
'Schneider Electric Solar Inverters USA, Inc. XW4024-120/240-60 [120V],Y,91.5,N'
'Schneider Electric Solar Inverters USA, Inc. XW4024-120/240-60,Y,91,N'
'Schneider Electric Solar Inverters USA, Inc. XW4548-120/240-60,Y,93,N'
'Schneider Electric Solar Inverters USA, Inc. Conext TX 5000 NA [208V],Y,95.5,N'
#REF!
'Schneider Electric Solar Inverters USA, Inc. XW+5548-NA,Y,93.5,N'
'Schneider Electric Solar Inverters USA, Inc. XW+5548-NA [120V],Y,93,N'
'Schneider Electric Solar Inverters USA, Inc. Conext TX 5000 NA [240V],Y,96,N'
'Schneider Electric Solar Inverters USA, Inc. XW6048-120-60 [120V],Y,92.5,N'
'Schneider Electric Solar Inverters USA, Inc. XW+6848-NA,Y,92.5,N'
'Schneider Electric Solar Inverters USA, Inc. XW+6848-NA [120V],Y,92.5,N'
'Schneider Electric Solar Inverters USA, Inc. XW6048-120/240,Y,92.5,N'
'Schneider Electric Solar Inverters USA, Inc. Conext CL 18000NA,Y,97,N'
'Schneider Electric Solar Inverters USA, Inc. Conext CL 25000NA,Y,98,N'
'Schneider Electric Solar Inverters USA, Inc. GT30-208 [208V],Y,96,N'
'Schneider Electric Solar Inverters USA, Inc. Conext CL-60A,Y,98,N'
'Schneider Electric Solar Inverters USA, Inc. GT100-208 [208V],Y,95,N'
'Schneider Electric Solar Inverters USA, Inc. GT100-208-PG [208V],Y,95,N'
'Schneider Electric Solar Inverters USA, Inc. GT100-480 [480V],Y,96,N'
'Schneider Electric Solar Inverters USA, Inc. GT100-480-PG [480V],Y,96,N'
'Schneider Electric Solar Inverters USA, Inc. Conext CL125 [600V],N,98.5,N'
'Schneider Electric Solar Inverters USA, Inc. GT250-480 [480V],Y,96,N'
'Schneider Electric Solar Inverters USA, Inc. GT250-480-PG [480V],Y,96,N'
'Schneider Electric Solar Inverters USA, Inc. GT500-480 [480V],Y,96,N'
'Schneider Electric Solar Inverters USA, Inc. GT500-480-PG [480V],Y,96,N'
'Schneider Electric Solar Inverters USA, Inc. GT500-MVX,Y,95.5,N'
'Schneider Electric Solar Inverters USA, Inc. GT500-MVX-PG,Y,95.5,N'
'Schneider Electric Solar Inverters USA, Inc. Conext Core XC540-NA,N,97,N'
'Schneider Electric Solar Inverters USA, Inc. Conext Core XC630-NA,N,97.5,N'
#REF!
'Schneider Electric Solar Inverters USA, Inc. Conext Core XC680-NA,N,97.5,N'
#REF!
'Schneider Electric Solar Inverters USA, Inc. Conext Core XC733-NA,N,97.5,N'
#REF!
'Schneider Electric Solar Inverters USA, Inc. CS1666-1-NA [575V],N,98,N'
#REF!
'Schneider Electric Solar Inverters USA, Inc. CS1666-2-NA [575V],N,98,N'
#REF!
'Schneider Electric Solar Inverters USA, Inc. CS1666-3-NA [575V],N,98,N'
#REF!
'Schneider Electric Solar Inverters USA, Inc. CS1800-NA [575V],N,98,N'
'Schneider Electric Solar Inverters USA, Inc. CS2000-NA [575V],N,97.5,N'
'Schneider Electric Solar Inverters USA, Inc. CS2200-NA [600V],N,98,N'
'Schneider Electric Solar Inverters USA, Inc. CS2400-NA [600V],N,98,N'
'Schuco USA SB700U [120V],Y,91.5,N'
'Schuco USA SB700U-SBD [120V],Y,91.5,N'
'Schuco USA SWR1800U [120V],Y,91.5,N'
'Schuco USA SWR1800U-SBD [120V],Y,91.5,N'
'Schuco USA SWR2100U [240V],Y,93,N'
'Schuco USA SWR2500U [208V],Y,92.5,N'
'Schuco USA SWR2500U-SBD [208V],Y,92.5,N'
'Schuco USA SWR2500U [240V],Y,93,N'
'Schuco USA SWR2500U-SBD [240V],Y,93,N'
'Schuco USA SB3000US [208V],Y,95,N'
'Schuco USA SB3000US [240V],Y,95.5,N'
'Schuco USA SB3300U [240V],Y,94.5,N'
'Schuco USA SB3800U [208V],Y,94,N'
'Schuco USA SB4000US [208V],Y,95.5,N'
'Schuco USA SB3800U [240V],Y,94.5,N'
'Schuco USA SB4000US [240V],Y,96,N'
'Schuco USA SB5000US [208V],Y,95.5,N'
'Schuco USA SB5000US [240V],Y,95.5,N'
'Schuco USA SB5000US [277V],Y,95.5,N'
'Schuco USA SB6000U [208V],Y,94.5,N'
'Schuco USA SB6000U [240V],Y,94.5,N'
'Schuco USA SB6000U [277V],Y,94.5,N'
'Schuco USA SB6000US [208V],Y,95.5,N'
'Schuco USA SB6000US [240V],Y,95.5,N'
'Schuco USA SB6000US [277V],Y,96,N'
'Schuco USA SB7000US [208V],Y,95.5,N'
' ,,(%),'